## Case Info
Base Case Check List
2030-31 Heavy Winter 2 Case, Pre |  |  |  | A70 Owners
65 = PSC
66 = BHE??
68 = IM (Inter Mountain??)
| Due To WECC | 2025-05-09 | 2025-05-09 | 700 = PSC Non-Util
| Short Name | 31HW2 |  | 73 = TSGT
| From case | 31HW2 |  | 733 = City of Lamar
| Year | 2031 |  | 735 = TSGT Non Util
| Season | Winter | W | 737 = HCE
| Time | 1800-2000 |  | 738 /68= CORE
| Loading | Heavy Winter | 100% | 739 = Yampa Valley
| Ref. Case Used | v05-01z |  | 93 = PRPA (zone 780)
26 = WAPA
95 = CSU (zone 785)
127 = TSGT New Mexico
Operations determination on each season’s duration.
   Spring Season – April 1st through May 31st
   Summer Season – June 1st through October 31st
   Winter Season – November 1st through March 31st

## Process
| Process Check List | 31HW2
Process
Done? | Item | Notes
Extract PSCo Changes
Retrieve Approved Starting Case
Retrieve Comparison case
| Harmonize models | see Pre-Extract checklist/tab
Extract Differences
Apply PSCo Topology changes
| Edit extract EPCL | ⇒See Extract Checks tab
Apply changes file
| Update Title block | File > titl or Ctrl-T 20yyHS/LW_A70 Prerun submittal Includes A70 Updates Month dd, 20yy
Save case as xxXX p_v-01 - START.sav
| Solve and debug until case solves | For any new buses added by the Extract file, manually set voltage/angle to that of the nearest pre-existing bus. May require adjustments to solution settings, but final settings should be: - Full Newton Raphsom - TCUL Adjustments enabled - All SVDs enabled - Phase shifters enables in discrete mode - Area interchange enabled for tie-lines
Apply EXT Util changes
| TSGT A70 (search 70 and 78) | Solve and debug until case solves
| TSGT A10 (SPS, New Mexico System) (search 70 and 78) | Solve and debug until case solves
| TSGT A73 (WAPA) | Solve and debug until case solves
| BHE | Must Extract from PSSe; Import PTI .raw file in PSLF; Solve and debug until case solves
| CSU Transit to A73 | Change has likely been applied to all starting cases at this point. Make a note if CSU-owned facilities exist in A70
| PRPA A70 | Must Extract from PSSe; Import PTI .raw file in PSLF; Solve and debug until case solves
| PRPA A73 (might not have) | Must Extract from PSSe; Import PTI .raw file in PSLF; Solve and debug until case solves
Apply PSCo load changes
Placeholder - new process in development
PSCo Generation
Apply interchange (get from WECC) in PSLF
Balance the system (rough dispatch)
Swing gen Pgen < Pmax
Run a report: rept --> loss
GEN + IMPORT + DER = LOAD + EXPORT + LOSS
Adjust generation until load and gen are about equal.
| THEN SOLVE | solving before this point, will result in a error mismatch - divergence - if the two values are significantly off; Be within +- 200MW to 300MW
| Use "YYHS/HW#_LR_PSCo-v-08.xls" spreadsheet and "WECC Case Build Dispatch Priority v1.0.docx" to adjust A70 generation according to case needs (full dispatch) | WECC Dispatch Priority Doc: WECC Case Build Dispatch Priority draft v0.1.docx
| Copy case Load, Loss, and Import information into LnR tab | Generation Dispatch Tool Template: YYHS-HW#_LR_PSCo-v-08.xls
Copy A70 generator data into V23 Gens tab
Adjust dispatch and renewable resource capacity in Generation tab according to case requirements and WECC Dispatch Priority document
Run PSLF Python created by dispatch spreadsheet into case, solve
Repeat as needed until swing gen is within Pmax/Pmin limits
Fix overloads
Fix voltages
| Update .dyd file | Combine any valid MOD-026/027 updates received for existing generators and .dyd files for generator projects added during the build process into a single .dyd document
Update/Create Sig changes document
Check Replog
Specify PSCo Case specific tie-line added/deleted
| Submit!!!!!!! | Check lists below
| yyyyHW-LS#_A70_PRERUN_SUBMISSON.zip | Title of Zip File to be submitted | Submission schedule for PRERUN OP Base Cases
| yyyy-mm-dd PSCo Dynamix data UPDates.dyd | dynamic update file to the MDF
| yyyyHW-LS#_A70_PRERUN_SUBMISSION.sav | case file (Prerun)
| yyyyHW/LS#_LnR_BHE | Black Hills L&R
| yyyyHW/LS#_LnR_PRPA | Platte River
| yyyyHW/LS#_LnR_PSCo | Public Service
| yyyyHW/LS#_LnR_TSGT | Tri-State, also called "Reduced PSCC" L&R sheet
| yyyyHW/LS#_Significant Changes_PSCo | significant changes, follow template ecpl_xtractv21d--PSCo_SIGads-v-01d.p and SIG_ADD_v01d.py
| yyyyHW-LS#_A70_Case-Review_SUBMISSION.zip | Title of Zip File to be submitted | Submission schedule for RREVIEW Cases
| 20yyHW/LS# - Exceptions to SADD.docx | list of exceptions to SADD
| yyyyHW-LS#_A70_Case-Review_CHANGES.p | EPCL change file that updates the prerun case. Epcl_xtractv21n.p
| yyyyHW-LS#_Case_Signoff_BHCE.pdf | signed DO & OS documents from Black Hills
| yyyyHW-LS#_Case_Signoff_PRPA.pdf | signed DO & OS documents from Platte River
| yyyyHW-LS#_Case_Signoff_PSCo.pdf | signoff document (blank document included with case DL form WECC)
| yyyyHW-LS#_Case_Signoff_TSGT.pdf | signed DO & OS documents from TriState
| yyyy-mm-dd PSCo Dynamix data UPDates.dyd | optional - updated dynamic data which was not submitted in the prerun case

## Pre-Extract
| EPCL Pre-Extract Checks | [5 empty] | 31HW2
Checks to reduce EPCL extract code - e.g. harmonize models
Done? | Bus/Project NAME | ISD (yyyy) | Season (S/W) | Bus No. 1 | Bus No. 2 | PSLF Ref Table | Notes
| assign A70 Balancing Authority = 65 |  |  |  |  | busd
| Set Voltages VMAX = 1.05 VMIN = 0.95 |  |  |  |  | busd
| Run latest FAC-008 ratings update file | [5 empty] | Need to apply ratings information for existing facilities, should only be overwritten if a Network Upgrade project will be in-service by the case year/season
| Build Pre-Extract Project Adds list | [5 empty] | Modeling Project Tracker_7-8-25.xlsx
Add items from the project tracker that will be in-serviced between timeframe of starting case and timeframe of building case
For projects with automation scripts referenced in Project Tracker, run script into model and solve.
If automation scripts flag real errors (i.e. can't find bus 7XXXX), go back to previous version of working case and do not run script into pre-extract model. Project addition will be captured by extract comparison.

## Pre-Extract Project Adds
Project | Description | Change FIle | Pre-Extract Needed? | Added? | Error/Solution Notes
CCII Topology Update |  | CCII_topo_upd.p | Y | Y
Port Data Center | Add bus 70077 R_2023_05 Add loads I1-I8 to bus 70077 Remove 70048 - 70528 '1' Add 70048 - 70077 '1' Add 70528 - 70077 '1' | Port taps Spruce - Green Valley See 'R_2023_05 Port.py' | Y | Y
Pine Junction Substation | 71507 PINEJCT_CR CR at 71507, LID: HID_RES 70124 CONIFER - 71507 PINEJCT_CR | Radial connection to Conifer (70124) | Y | Y
May Valley - Longhorn |  | Segment 6. double circuit 345 kV | N | N
Goose Creek STATCOM | 420 MVAR Type 2 SVD at 70918 | Add 420 MVAR STATCOM to Goose Creek 70918 See '420 MVAR STATCOM Goose Creek.py' | Y | Y
May Valley Sync Con | 2x166 MVA Synchronous Condensors at 70919 | Add two 166 MVA sync cons to May Valley See '2x166 MVA SyncCond at May Valley.py' | Y | Y
5283 LEET-ELAT UG Line Replacement PHASE 2 |  | Two phases (2024. 2026). Increase facility ratings. Thermocouple for DLR installed 30SEP2022 | Y | Y
CWRL-ROSEDALE SUB | ##### ROSEDALE 230 ##### ROSEDALE 230 - 70368 ROSEDALE 115 70471 WELD_PS 230 - ##### ROSEDALE 230 | Upgrade Rosedale sub to 230 Kv. Not in Tamcast. | N | N
Delbert Substation | 71503 DELBERT_CR CR load at 71503, LID: HID_RES 70518 BAYOU_CR - 71503 DELBERT_CR 71503 DELBERT_CR - 70583 ELIZABTH_CR Delete: 70518 - 70583 | Delbert taps Bayou - Elizabeth line (70518 - 70583) | Y | Y
5295 Barker Lacombe 230kV UG Line | 70152 BARKER Two stages: P1, then P2 at 70152 70152 BARKER - 70324 LACOMBE ck 1 and 2 | Connects to 70324 LACOMBE via double circuit; P1 & P2 loads transferred from Lacombe to Barker. Transformer #1 February 6, 2026; transformer #2 SEPember 15, 2026. | Y | Y
Barker Transmission Substation Sub | TR3 approved. We need a timeline for banks |  | Y | Y
5297 Barker Lacombe 230kV UG Line | 70152 BARKER Two stages: P1, then P2 at 70152 70152 BARKER - 70324 LACOMBE ck 1 and 2 | Connects to 70324 LACOMBE via double circuit; P1 & P2 loads transferred from Lacombe to Barker. Transformer #1 February 6, 2026; transformer #2 SEPember 15, 2026. | Y | Y
Dawson Ridge Substation | 71501 DAWSONRDG_CR CR at 71501 LID - HID_MIX 70091 CASTLRCK - 71501 DAWSONRDG_CR 71501 DAWSONRDG_CR - 71502 CITADEL_CR Delete: 70091 CASTLRCK - 71502 CITADEL_CR | Castle Rock - Wolfensberger (70091 - 70519) develops to Castle Rock - Dawson Ridge - Citadel - Wolfensberger as Dawson Ridge and Citadel are in-serviced | Y | Y
Midway 230/115 kV Transformer Upgrade | Uprate 70286 - 70285 - 71980 T1 to SN and SE 280 MVA |  | Y | Y
WFRZ 9054 Major Line Rebuild 115 kV |  | Ridge - Ralston - Valmont | N | N
Pathway Seg 4-MayVly-Tundra(Sandstone) Tline | 345kV double-circuit 70919 MAY_VALLEY - 70653 TUNDRA DANI - TUND circuit 2 T2 345/230 Added at Harvest _MI T1&T2 70920 MAY_VALLEY 34.5 - 70919 MAYVALLEY 345 |  | Y | Y
Pathway Seg 5-Tundra(Sandstone)-Harvest Mile Tline | 345kV double-circuit 70597 HARVEST_MI - 70653 TUNDRA |  | Y | Y
5283 LEET-ELAT 230KV UG REPL--Phase 2 | 796 MVA Line 5283 70163 ELAT - 70291 MONR Uprate | Scope: Replace the existing oil-filled cable of L5283 Leetsdale-Monroe-Elati 230kV underground line with new XLPE cable to achieve higher facility rating. This will enable higher renewable generation “imports” into Denver metro area resulting from the Company’s 80 percent carbon reduction by 2030 (80x30) goal and accommodate the scheduled generation retirement at Cherokee. | Y | Y
Havana - Chambers Uprate Circuits 9543 & 9544 | Uprate 70216 - 70538 '1' to SN and SE 318.7 MVA Uprate 70217 - 70538 '2' to SN and SE 318.7 MVA | OBSOLETE | N | N
Arapahoe to Air to South to Gray 9332 Uprate | Uprate 70036 - 70531 '1' to SN and SE 159 MVA Uprate 70402 - 70531 '1' to SN and SE 159 MVA Uprate 70208 - 70402 '1' to SN and SE 159 MVA | See '27 ERP ARAP-ARLQ_TP-SOUT-GRAY L9332.py' | Y | Y
Gilman - Avon 115kV Line, Line | NO AVON 79092 - GILMAN 70199 Update cap bank at Vail cap bank at Beaver Creek West | Normally Open (N.O.) secdd. Replace | Y | Y
Gray Street Sub Upgrade | P1 at 70208 70148 DENVTM - 70208 GRAY_ST. 70208 GRAY_ST. - 70173 FEDCTRTP | Install new Distribution bank and loop the nearby Denver Terminal – Federal Center 115 kV line into Gray Street Substation to alleviate loading on the Denver Terminal – Gray Street 115 kV line. | Y | Y
Arapahoe to Greenwood 5709 Uprate | Uprate 70038 - 70189 '1' to SN and SE 956 MVA Update approximate impedance values | See '27 ARAP-GREE L5709 Uprate.py' | Y | Y
Cherokee sub 115kV bus mod | 70110 CHEROKEE_N - 70108 CHEROKEE_S Ck: 2 | new 115kV bus tie between north and south switchyards | N | N
Greenwood Bus tie uprate | Uprate 70189 - 70212 '1' to SN and SE 956 MVA | See '26JAN22 ERP Q1 GREE bus-tie uprate.py' | Y | Y
Cherokee 4 off | Remove SS and Gen | Cherokee 4 taken out of service | Y | Y
WFRZ 9812 PONC-STR 232 Aging Line Rebuild |  |  | N | N
DCP Sandy Creek Sub, LRS, Pre-Con |  |  | N | N
CWRL |  | Add Beebe Draw 230 kV sub to replace La Salle 44. 2027 Add Box Elder 230/115 kV sub to replace Box Elder 44. 2027 Add Beebe Draw - Box Elder 230 Add Box Elder - Ennis 115 | N | N
Pintail New 230/115 Auto at FLUP | 70090 - 70192 New T4 273/319 MVA Auto |  | Y | Y
Outback Substation | 71504 OUTBACK_CR and CR load LID: HID_RES 70546 BRICK CTR_CR - 71504 OUTBACK_CR 71504 OUTBACK_CR - 71505 SPRINGVL_CR Delete: 70546 - 71505 | Brick Center - Kiowa (70546 - 70571) develops to Brick Center - Outback - Spring Valley - Kiowa as Outback and Spring Valley are in-serviced | Y | Y
DCP Wilson #1,Sub |  |  | N | N
Cherokee Remote Tie 'New Sub A' substation addition (Phase I) | Add new bus 115 kV 70103 with connections to: • 70073 - 70103 circuit '1' (137/151 MVA) • 70108 - 70103 circuit '1' (137/151 MVA) • 70126 - 70103 circuit '1' (159/175 MVA) • 70277 - 70103 circuit '1' (159/175 MVA) • 70377 - 70103 circuit '1' (159/175 MVA) • 70377 - 70103 circuit '2' (159/175 MVA) Delete lines: • 70277 - 70377 circuit '1' • 70073 - 70108 circuit '1' • 70126 - 70377 circuit '1' | See 'ERP JY.py' When sub goes into service, the lines it taps will still be at their original ratings and the new 115 kV line from 70110 to 70103 '1' will not be in service yet | Y | Y
Windler Data Center | Add new Winder 7XXXX sub Add line 7XXXX - 70528 '1' Add line 7XXXX - 70497 '1' Add 'IN' load (500 MW 1.0 PF) to 7XXXX | See 'R-2023-07-Windler.py' Assign open bus number to Windler bus in script | Y | Y
Daniels Park to Greenwood 5111 Uprate | Uprate 70139 - 70331 '1' to SN and SE 916 MVA Uprate 70212 - 70331 '2' to SN and SE 916 MVA Update approximate impedance values | See '26OCT21 ERP Q1 DANI-PRAI-GREE L5111.py' | Y | Y
Daniels Park to Greenwood 5707 Uprate | Uprate 70139 - 70323 '2' to SN and SE 916 MVA Uprate 70189 - 70323 '1' to SN and SE 916 MVA Update approximate impedance values | See '26JUN1 ERP Q4 DANI-PRAI-GREE L5707.py' | Y | Y
9257 Climax Robinson Rack Gilman Line |  | proceeds only after Gilman-Avon complete Date on other spreadsheet is DEC 2028. | N | N
Arapahoe to South to Bancroft 9335 Uprate | Uprate 70037 - 70401 '1' to SN and SE 239 MVA Uprate 70045 - 70401 '1' to SN and SE 239 MVA Update approximate impedance values | See '27 ARAP-SOUT_TP-BANC L9335 Uprate.py' | Y | Y
WFRZ 5509 CAME-PARA 230kV Rebuild | 70869 |  | N | N
Smoky Hill 3rd Transformer | Add 70599 - 70396 'T6' | Add third 345/230 xfmr at Smoky Hill See '28SEP27 ERP Q16 SMOK TR6.py' | Y | Y
Daniels Park 4th Transformer | Add 70139-70601 'T6' | Add fourth 345/230 xfmr at Daniels Park See '29SEP13 ERP Q15 DANI TR4.py' | Y | Y
Cherokee to Broomfield_Federal Height_Semper 115kV Circuits 9055/9558/9464 Uprate | Uprate 70110 - 70175 '2' to SN and SE 398 MVA Uprate 70175 - 70382 '1' to SN and SE 398 MVA Uprate 70065 - 70382 '1' to SN and SE 398 MVA Uprate 70065 - 70174 '1' to SN and SE 398 MVA Uprate 70110 - 70174 '1' to SN and SE 398 MVA Update approximate impedance values | See both '29JUN1 ERP Q21 CHER-FEDH-SEMP-BROO L9055.py' and '26NOV18 ERP Q21 CHER-FEDH-BROO.py' | Y | Y
Arapahoe 115 kV Bus Uprate & 2nd 230/115kV Transformer Add | Uprate 70036 - 70037 '1' to SN and SE 397 MVA Add 70037 - 70038 'T6' | See '27FEB10 ERP Q2 ARAP Bus-tie TR6.py' | Y | Y
WFRZ 5205 Parachute - Rilfe Rebuild |  |  | N
DCP Superior Sub, LRS, Pre-Con |  |  | N
DCP Solterra TR1, TAM Sub |  |  | N
South Sub Expansion | Add South 230 kV sub South 230 taps 70038 ARAP - 70141 DAKO '1' Add 230/115 kV xfmr | See '28 ERP SOUTH 230 Substation.py' | Y | Y
Circuits 5167 and 5285: Smoky Hill - Buckley - Tollgate - Jewell - Leetsdale | Uprate 70046 - 70396 '1'to SN and SE 796 MVA Uprate 70067 - 70396 '2' to SN and SE 796 MVA Uprate 70239 - 70491 '1' to SN and SE 796 MVA Uprate 70260 - 70239 '1' to SN and SE 796 MVA Update approximate impedance values | See 'ERP SMOK-BUCK L5285 & L5167 Uprate.py' See 'ERP JEWE-TOLL L5285.py' See 'ERP LEET-JEWE Uprate.py' | Y | Y
Cherokee - New Substation A Line 9542 Uprate | Uprate 70108 - 70103 '1' to SN and SE 318 MVA |  | Y | Y
Cherokee - Mapleton L9546 Uprate | Uprate 70108 - 70277 '1' to SN and SE 318 MVA | See '28 ERP CHER-MAPL Uprate.py' | Y | Y
Greenwood - Monaco Series Reactor | Remove 70189 GREE - 70481 MONA '1' Add bus 70105 'GREE_SR' Add NO branch 70105 GREE SR - 70189 GREE '1' Add NC branch 70105 GREE SR - 70189 GREE '2' Add NC branch 70105 GREE SR - 70481 MONA '1' | Replace line between Greenwood and Monaco with parallel branches, 70105 - 70189 '2' is the reactor See '27 GREE-MONA Series Reactor.py' | Y | Y
Daniels Park to Sante Fe Uprate 5107 | Uprate 70139 - 70527 '1' to SN and SE 637 MVA | See '28 ERP DAN-SANT L5107 Uprate.py' | Y | Y
WFRZ 5207 RIFL-HOPK 230kV Rebuild |  |  | N
Cherokee - Conoco - New Sub A Line 9549 Uprate | Uprate 70126 - 70103 '1' to SN and SE 239 MVA |  | Y | Y
New 115 Line Cherokee - New Sub A | Add new line 70110 - 70103 circuit '1' (318/318 MVA) |  | Y | Y
Comanche 3 Offline | 70777: GEN and SS OFF | Comanche 3 taken offline | Y | Y
PI-2023-2 Comanche 345 kV 10 MW BESS |  |  | Y | Y
REPL-2021-001 |  | Comanche 1 replacement See '25DEC31 GIA REPL_21_1 Rocky Mtn.p' | Y | Y
GI-2020-10 Stagecoach Solar |  | See '26SEP1 GIA GI-2020-10 Stagecoach.p' NOTE: existing model incorporates GI-2014-9 and GI-2020-10 (joint project request) but GI-2014-9 has since withdrawn their LGIA so reduce the Pmax on 700146 by 70 MW manually to represent withdrawal of GI-2014-9 from Queue | Y | Y
GI-2021-6 Aurora Borealis Solar |  | See '24MAY17 GIA GI_2021_6 Aurora Borealis.p' | Y | Y
5RSC-2024-28 Dusty Rose |  | See '25DEC1 EP 5RSC_24_28 Dusty Rose.p' Bid 0295 | Y | Y
PI-2023-3 Southern Star Solar |  | See '3RSC_23_1 Southern Star Solar.p' | Y | Y
PI-2023-4 Southern Star Storage |  | See '3RSC_23_2 Southern Star Storage.p' | Y | Y
PI-2023-5 Towner III Wind |  | See '3RSC_23_3 Towner 3.p' | Y | Y
PI-2024-11 Ft St Vrain BESS |  | See '26OCT15 EP PI_24_11 5RSC_24_14 FSVR storage.p' Bid 0251 | Y | Y
REPL-2024-001 Comanche 2 Replacement |  | See '26AUG17 S4 REPL_2024_1 Arroyo II.p' | Y | Y
PI-2024-5 Alamosa Energy Center |  | See '26MAR31 PI_24_5 5RSC_24_3 ATER.p' Bid 0011 | Y | Y
PI-2024-19 Heartstrong |  | See '26MAY6 PI_24_19 Heartstrong.p' Bid 1016 | Y | Y
PI-2024-10 Spindle BESS |  | See '27JAN15 PI_2024_10 5RSC_24_13 Spindle Storage.p' Bid 0249 | Y | Y
Cherokee 4 Off |  | Cherokee 4 taken offline | Y | Y
5RSC-2024-9 South Park |  | See '27DEC31 5RSC_24_9 South Park.p' Bid 1085 | Y | Y
PI-2024-20 South Park |  | No .p script Bid 1085 | N | N
PI-2024-13 Towner Wind I |  | See '26FEB27 S4 PI_24_13 5RSC_24_15 Towner 1.p' Bid 1029 | Y | Y
PI-2024-12 Cheyenne Ridge II |  | See '24DEC16 S4 PI_24_12 5RSC_24_16 Chey Rdg II.p' Bid 1015 | Y | Y
PI-2024-9 Singing Grass Wind |  | See '26MAY7 S4 E&P PI_2024_9 5RSC_24_17 Singing Grass.p' Bid 1024 | Y | Y
PI-2024-3 Ft Lupton CT |  | See '27MAY31 S4 E&P PI_2024_3 5RSC_2024_01 FLUP CT3.p' Bid 0989 | Y | Y
PI-2024-2 Ft St Vrain 7 & 8 |  | See '27MAY31 S4 E&P PI_2024_2 5RSC_2024_02 FSVR CT 7 and 8.p' Bid 0997 | Y | Y
PI-2024-7 Comanche/Village BESS |  | See '27MAY1 EP PI_24_7 5RSC-2024-12 Comanche Storage.p' Bid 0589 | Y | Y
PI-2024-8 Cornflower |  | See '27JUL31 PI_24_8 5RSC_24_8 Cornflower.p' Bid 0149 | Y | Y
PI-2024-18 Deer Trail II |  | See '2027MAR31 PI_2024_18 5RSC_24_7 Deertrail II.p' Bid 0217 | Y | Y
PI-2024-17 Thunderwolf Expansion |  | See '28JUN1 PI_24_17 5RSC_24_4 Thunderwolf exp.p' Bid 0474 | Y | Y
PI-2024-15 Highland |  | See '28JUN1 EP PI_2-24_15 5RSC_2024_6 Highland.p' Bid 0303 | Y | Y
PI-2024-14 Dryland Prairie |  | See '28MAY1 EP PI_24_14 5RSC_24_10 Dryland Prairie.p' Bid 0282 | Y | Y
PI-2024-16 South Platte |  | See '28JUN1 PI_24_16 5RSC_24_11 South Platte Storage.p' Bid 0467 | Y | Y

## Extract Checks
EPCL Extract Topology Checks
Include Topology and projects ISD
Done? | Step | Notes
| Delete 'extraneous' facility modify chunks | Remove EPCL Modify chunks that update irrelevant information. Examples include: - setting bus vmax1/vmin1 to 0 pu - resetting line/transformer .aloss variable - changing percent ownership (.pown) when the associated owner number (.nown) is 0 - transformer impedance table changes - non-A70 owner table updates - SVD .b and .st dispatch updates
| Delete 'from-to line swap' Addition/Removal chunks | Existing lines, xfmrs, and generators may have different from-to bus assignments or facility IDs between working and reference models. The extract will capture this comparison as removing the existing facility, then re-adding with swapped from and to bus numbers or an updated facility ID. Delete these changes from the model, if the driver is an ID update then change working model facility ID to the facility ID In the reference model.
| Delete changes for non-PSCo facilities | PSCo facilities have Owner Number 65 and 700. Refer to Case Info tab for other owner numbers. EPCL Modify chunks may not include owner info directly, refer to models to confirm ownership.
| Keep ownership modification updates | If facility has ownership changed to/from 65 or 700, and facility ownership change is reflected in reference model, keep change
| Delete facility addition/removals associated with projects not in-service by the case year/season | PSCo-owned facilities being added/removed from the model will almost always be associated with a project in the Project Tracker. If project is not yet in-service for the case timeframe, delete ALL associated changes from the extract file. Season In-Service Cut-offs: - Winter: end of March - Spring: end of May - Summer: end of August - Fall: end of November Important notes: - if project taps existing line, need to delete the associated EPCL Remove chunk which takes the existing line out of the model - projects tapping existing lines may modify circuit IDs to align with new topology, if project not yet in-service then retain working model circuit IDs and validate with One-Lines - project may be partially completed on the case year/season timeframe, so confirm the Extract will not modify projects beyond the portions that will be in-service
| Delete facility modifications associated with projects not in-service by the case year/season | Modifications to existing PSCo-owned facilities may be associated with Network Upgrade projects in the tracker. For EPCL modification of existing facility code chunks, verify the following are not associated with Network Upgrade projects: - Line impedance update - Line rating update - Xfmr impedance update - Xfmr rating update - SVD sizing update If the change is associated with a Network Upgrade project in the tracker, delete from extract file if project will not yet be in-service. Need to make sure FAC-008 ratings update information is not overwritten by Extract update unless an associated uprate project will be in-service
| Delete generator project additions if project has not yet reached the required milestone for WECC model inclusion | - If generator is included in 2023 ERP Approved Portfolio, include in models according to ISD and regardless of project milestone - If generator is only tracked as being in Study Phase 1 or 2, exclude from WECC model - If generator is tracked as having an executed LGIA/PLGIA, only include if building a 5+ year scenario and PSCo is short on resources - If generator project's associated Interconnection Facilities and Network Upgrade projects have reached Stage 4 in ISP PPEP lifecycle process, include according to ISD
| Delete transformer modifications that reset mid-point buses | Existing 3-winding transformers may use different mid-point buses between working case and comparison case. Delete any modifications to 3-wdg xfmr which swap the mid-point bus (tran[@logindx].iint = ) for an arbitrary new mid-point bus. Also delete any associated mid-point bus Addition/Removal EPCL chunks.

## Review Checks
|  |  |  | Review Checks | 31HW2
Specific to the Base Case Reviews
Done? | Check | Bus No. 1 | Bus No. 2 | PSLF Ref Table | Action | Notes

## _archive_Fix Files
| EPCL Files to Run | 31HW2
Files Run In the course of the case
Done? | EPCL File | Notes | ISD | Season
| A70 bus owner fixes.p | assigns bus owners
| A70 MOD-032 UPD.p | Updates the Gen Pmax/min, Qmax/min, GSU tap and nominal settings in accordance with the MOD-032 standard (e.g. the latest data we have)
| A70_gen Fixes.p | assigns gen owners, LID and turbine types
| A70_Loads - LID and OWN.p | populates load long id's and owner for PSCo
| Arapahoe Power Flow 063017.epc | UPDs the power flow model for associated Arapahoe topology
| Checkazao.p | Looks for errors (mis-assigned machines)
| Checks.p | Looks for errors (consistency, duplication)
| FixRate1.p | Input: 70, fixes rates on lines & XFMRS
| Run FAC008.p | Updates the ratings for lines and XFMRs