## Line Ratings (2) (hidden)
|  |  | FAC-008-3 Transmission Lines |  |  |  | OPCO: PSC |  |  | VALIDATION STATUS: VALID | [5 empty] | OWNERSHIP: Jointly Owned,Xcel Owned
[7 empty] | BES: Y |  |  | LIFE CYCLE STATUS: AS BUILT
FACILITY DESIGNATION | LINE NAME | FROM SUB | FROM SUB OWNER | TO SUB | TO SUB OWNER | FROM PSSE | TO PSSE | FACILITY OWNERSHIP | EQUIP NAME | EQUIP TYPE | EQUIP LOCATION | SN (AMPS) | SE (AMPS) | WN (AMPS) | WE (AMPS) | SN (MVA) | SE (MVA) | WN (MVA) | WE (MVA) | COMMENTS
MTHR-HAYD-138.0-1 | 3003 | MT. HARRIS SUBSTATION | XCEL | HAYDEN (WAPA) | FOREIGN | 70525 | 79038 | Xcel Owned | MTHR-HAYD-138.0-1 | FACILITY |  | 301 | 301 | 301 | 301 | 72 | 72 | 72 | 72
MTHR-HAYD-138.0-1 | 3003 | MT. HARRIS SUBSTATION | XCEL | HAYDEN (WAPA) | FOREIGN | 70525 | 79038 | Xcel Owned | Foreign Ratings | Foreign Ratings | HAYD | 301 | 301 | 301 | 301 | 72 | 72 | 72 | 72
UTER-RIFL-230.0-1 | 3007 | RIFLE UTE 230/345KV SUBSTATION | XCEL | RIFLE (WAPA) | FOREIGN | 79057 | 79059 | Jointly Owned | UTER-RIFL-230.0-1 | FACILITY |  | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
UTER-RIFL-230.0-1 | 3007 | RIFLE UTE 230/345KV SUBSTATION | XCEL | RIFLE (WAPA) | FOREIGN | 79057 | 79059 | Jointly Owned | Foreign Ratings | Foreign Ratings | RIFL | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
COLL-UTER-138.0-1 | 3014 | COLLBRAN SUBSTATION | XCEL | RIFLE UTE 230/345KV SUBSTATION | XCEL | 79047 | 79056 | Jointly Owned | COLL-UTER-138.0-1 | FACILITY |  | 300 | 300 | 300 | 300 | 72 | 72 | 72 | 72
COLL-UTER-138.0-1 | 3014 | COLLBRAN SUBSTATION | XCEL | RIFLE UTE 230/345KV SUBSTATION | XCEL | 79047 | 79056 | Jointly Owned | C821 135Y | CURRENT_TRANSFORMER | COLL | 300 | 300 | 300 | 300 | 72 | 72 | 72 | 72
COLL-UTER-138.0-1 | 3014 | COLLBRAN SUBSTATION | XCEL | RIFLE UTE 230/345KV SUBSTATION | XCEL | 79047 | 79056 | Jointly Owned | C821 KWH IN/OUT | SECONDARY_CURRENT_LIMITATION | COLL | 300 | 300 | 300 | 300 | 72 | 72 | 72 | 72
UTEG-COLL-138.0-1 | 3015 | UTE GRAND JUNCTION SUBSTATION | XCEL | COLLBRAN SUBSTATION | XCEL | 79035 | 79047 | Xcel Owned | UTEG-COLL-138.0-1 | FACILITY |  | 400 | 400 | 400 | 400 | 96 | 96 | 96 | 96
UTEG-COLL-138.0-1 | 3015 | UTE GRAND JUNCTION SUBSTATION | XCEL | COLLBRAN SUBSTATION | XCEL | 79035 | 79047 | Xcel Owned | C841 135Y | CURRENT_TRANSFORMER | COLL | 400 | 400 | 400 | 400 | 96 | 96 | 96 | 96
UTEG-COLL-138.0-1 | 3015 | UTE GRAND JUNCTION SUBSTATION | XCEL | COLLBRAN SUBSTATION | XCEL | 79035 | 79047 | Xcel Owned | C841 135X | CURRENT_TRANSFORMER | COLL | 400 | 400 | 400 | 400 | 96 | 96 | 96 | 96
CABI-LOOK-230.0-1 | 5003 | CABIN CREEK HYDRO SUBSTATION | XCEL | LOOKOUT SUBSTATION | XCEL | 70072 | 70266 | Xcel Owned | CABI-LOOK-230.0-1 | FACILITY |  | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
CABI-LOOK-230.0-1 | 5003 | CABIN CREEK HYDRO SUBSTATION | XCEL | LOOKOUT SUBSTATION | XCEL | 70072 | 70266 | Xcel Owned | 5003 METER VAR | SECONDARY_CURRENT_LIMITATION | LOOK | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
CABI-LOOK-230.0-1 | 5003 | CABIN CREEK HYDRO SUBSTATION | XCEL | LOOKOUT SUBSTATION | XCEL | 70072 | 70266 | Xcel Owned | 5003 METER VAR | SECONDARY_CURRENT_LIMITATION | CABI | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
CABI-LOOK-230.0-1 | 5003 | CABIN CREEK HYDRO SUBSTATION | XCEL | LOOKOUT SUBSTATION | XCEL | 70072 | 70266 | Xcel Owned | 5003 METER W | SECONDARY_CURRENT_LIMITATION | CABI | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
CABI-LOOK-230.0-1 | 5003 | CABIN CREEK HYDRO SUBSTATION | XCEL | LOOKOUT SUBSTATION | XCEL | 70072 | 70266 | Xcel Owned |  | LINE_TRAP | LOOK | 1200 | 1200 | 1248 | 1248 | 478 | 478 | 497 | 497
CABI-IDAH-230.0-1 | 5005 | CABIN CREEK HYDRO SUBSTATION | XCEL | IDAHO SPRINGS SUBSTATION | XCEL | 70072 | 70237 | Xcel Owned | CABI-IDAH-230.0-1 | FACILITY |  | 1188 | 1394 | 1422 | 1583 | 473 | 555 | 567 | 631
CABI-IDAH-230.0-1 | 5005 | CABIN CREEK HYDRO SUBSTATION | XCEL | IDAHO SPRINGS SUBSTATION | XCEL | 70072 | 70237 | Xcel Owned | Narcissus | BUSBAR_SECTION | IDAH | 1188 | 1394 | 1422 | 1590 | 473 | 555 | 567 | 633
CABI-IDAH-230.0-1 | 5005 | CABIN CREEK HYDRO SUBSTATION | XCEL | IDAHO SPRINGS SUBSTATION | XCEL | 70072 | 70237 | Xcel Owned | CABI-IDAH-230.0-1 | Transmission Line | 5005 | 1284 | 1413 | 1439 | 1583 | 512 | 563 | 573 | 631
IDAH-LOOK-230.0-1 | 5005 | IDAHO SPRINGS SUBSTATION | XCEL | LOOKOUT SUBSTATION | XCEL | 70237 | 70266 | Xcel Owned | IDAH-LOOK-230.0-1 | FACILITY |  | 1188 | 1200 | 1200 | 1200 | 473 | 478 | 478 | 478
IDAH-LOOK-230.0-1 | 5005 | IDAHO SPRINGS SUBSTATION | XCEL | LOOKOUT SUBSTATION | XCEL | 70237 | 70266 | Xcel Owned | Narcissus | BUSBAR_SECTION | IDAH | 1188 | 1394 | 1422 | 1590 | 473 | 555 | 567 | 633
IDAH-LOOK-230.0-1 | 5005 | IDAHO SPRINGS SUBSTATION | XCEL | LOOKOUT SUBSTATION | XCEL | 70237 | 70266 | Xcel Owned | 5005 METER VAR | SECONDARY_CURRENT_LIMITATION | LOOK | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
IDAH-LOOK-230.0-1 | 5005 | IDAHO SPRINGS SUBSTATION | XCEL | LOOKOUT SUBSTATION | XCEL | 70237 | 70266 | Xcel Owned |  | LINE_TRAP | LOOK | 1200 | 1200 | 1248 | 1248 | 478 | 478 | 497 | 497
CABI-DILL-230.0-1 | 5007 | CABIN CREEK HYDRO SUBSTATION | XCEL | DILLON SUBSTATION | XCEL | 70072 | 70156 | Xcel Owned | CABI-DILL-230.0-1 | FACILITY |  | 1591 | 1591 | 1664 | 1664 | 634 | 634 | 663 | 663
CABI-DILL-230.0-1 | 5007 | CABIN CREEK HYDRO SUBSTATION | XCEL | DILLON SUBSTATION | XCEL | 70072 | 70156 | Xcel Owned | CABI-DILL-230.0-1 | Transmission Line | 5007 | 1591 | 1591 | 1891 | 1891 | 634 | 634 | 753 | 753
CABI-DILL-230.0-1 | 5007 | CABIN CREEK HYDRO SUBSTATION | XCEL | DILLON SUBSTATION | XCEL | 70072 | 70156 | Xcel Owned |  | LINE_TRAP | DILL | 1600 | 1600 | 1664 | 1664 | 637 | 637 | 663 | 663
RUSS-CHER-230.0-1 | 5021 | RUSSELL SUBSTATION | XCEL | CHEROKEE SWITCHYARD SUBSTATION | XCEL | 70369 | 70107 | Xcel Owned | RUSS-CHER-230.0-1 | FACILITY |  | 944 | 1038 | 1152 | 1267 | 376 | 414 | 459 | 505
RUSS-CHER-230.0-1 | 5021 | RUSSELL SUBSTATION | XCEL | CHEROKEE SWITCHYARD SUBSTATION | XCEL | 70369 | 70107 | Xcel Owned | RUSS-CHER-230.0-1 | Transmission Line | 5021 | 944 | 1038 | 1152 | 1267 | 376 | 414 | 459 | 505
RUSS-RIDG-230.0-1 | 5021 | RUSSELL SUBSTATION | XCEL | RIDGE SUBSTATION | XCEL | 70369 | 70355 | Xcel Owned | RUSS-RIDG-230.0-1 | FACILITY |  | 944 | 1038 | 1152 | 1200 | 376 | 414 | 459 | 478
RUSS-RIDG-230.0-1 | 5021 | RUSSELL SUBSTATION | XCEL | RIDGE SUBSTATION | XCEL | 70369 | 70355 | Xcel Owned | RUSS-RIDG-230.0-1 | Transmission Line | 5021 | 944 | 1038 | 1152 | 1267 | 376 | 414 | 459 | 505
RUSS-RIDG-230.0-1 | 5021 | RUSSELL SUBSTATION | XCEL | RIDGE SUBSTATION | XCEL | 70369 | 70355 | Xcel Owned | L5021 METER VAR | SECONDARY_CURRENT_LIMITATION | RIDG | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
CHAT-WATE-230.0-1 | 5023 | CHATFIELD SUBSTATION | XCEL | WATERTON SUBSTATION | XCEL | 70100 | 70464 | Xcel Owned | CHAT-WATE-230.0-1 | FACILITY |  | 1214 | 1397 | 1447 | 1592 | 483 | 557 | 576 | 634
CHAT-WATE-230.0-1 | 5023 | CHATFIELD SUBSTATION | XCEL | WATERTON SUBSTATION | XCEL | 70100 | 70464 | Xcel Owned | Narcissus | BUSBAR_SECTION | CHAT | 1214 | 1420 | 1450 | 1619 | 483 | 566 | 578 | 645
CHAT-WATE-230.0-1 | 5023 | CHATFIELD SUBSTATION | XCEL | WATERTON SUBSTATION | XCEL | 70100 | 70464 | Xcel Owned | CHAT-WATE-230.0-1 | Transmission Line | 5023 | 1270 | 1397 | 1447 | 1592 | 506 | 557 | 576 | 634
SODA-CHAT-230.0-1 | 5023 | SODA LAKES SUBSTATION | XCEL | CHATFIELD SUBSTATION | XCEL | 70018 | 70100 | Xcel Owned | SODA-CHAT-230.0-1 | FACILITY |  | 1214 | 1397 | 1447 | 1592 | 483 | 557 | 576 | 634
SODA-CHAT-230.0-1 | 5023 | SODA LAKES SUBSTATION | XCEL | CHATFIELD SUBSTATION | XCEL | 70018 | 70100 | Xcel Owned | Narcissus | BUSBAR_SECTION | CHAT | 1214 | 1420 | 1450 | 1619 | 483 | 566 | 578 | 645
SODA-CHAT-230.0-1 | 5023 | SODA LAKES SUBSTATION | XCEL | CHATFIELD SUBSTATION | XCEL | 70018 | 70100 | Xcel Owned | SODA-CHAT-230.0-1 | Transmission Line | 5023 | 1270 | 1397 | 1447 | 1592 | 506 | 557 | 576 | 634
LOOK-PLEN-230.0-1 | 5025 | LOOKOUT SUBSTATION | XCEL | PLAINS END SWITCHING STATION | XCEL | 70266 | 70570 | Xcel Owned | LOOK-PLEN-230.0-1 | FACILITY |  | 1166 | 1200 | 1200 | 1200 | 465 | 478 | 478 | 478
LOOK-PLEN-230.0-1 | 5025 | LOOKOUT SUBSTATION | XCEL | PLAINS END SWITCHING STATION | XCEL | 70266 | 70570 | Xcel Owned | LOOK-PLEN-230.0-1 | Transmission Line | 5025 | 1166 | 1282 | 1360 | 1496 | 465 | 511 | 542 | 596
LOOK-PLEN-230.0-1 | 5025 | LOOKOUT SUBSTATION | XCEL | PLAINS END SWITCHING STATION | XCEL | 70266 | 70570 | Xcel Owned | 5025 METER VAR | SECONDARY_CURRENT_LIMITATION | LOOK | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
LOOK-PLEN-230.0-2 | 5027 | LOOKOUT SUBSTATION | XCEL | PLAINS END SWITCHING STATION | XCEL | 70266 | 70570 | Xcel Owned | LOOK-PLEN-230.0-2 | FACILITY |  | 1334 | 1467 | 1500 | 1650 | 531 | 584 | 598 | 657
LOOK-PLEN-230.0-2 | 5027 | LOOKOUT SUBSTATION | XCEL | PLAINS END SWITCHING STATION | XCEL | 70266 | 70570 | Xcel Owned | LOOK-PLEN-230.0-2 | Transmission Line | 5027 | 1334 | 1467 | 1500 | 1650 | 531 | 584 | 598 | 657
LOOK-RIDG-230.0-1 | 5029 | LOOKOUT SUBSTATION | XCEL | RIDGE SUBSTATION | XCEL | 70266 | 70355 | Xcel Owned | LOOK-RIDG-230.0-1 | FACILITY |  | 900 | 990 | 1157 | 1200 | 359 | 394 | 461 | 478
LOOK-RIDG-230.0-1 | 5029 | LOOKOUT SUBSTATION | XCEL | RIDGE SUBSTATION | XCEL | 70266 | 70355 | Xcel Owned | LOOK-RIDG-230.0-1 | Transmission Line | 5029 | 900 | 990 | 1157 | 1273 | 359 | 394 | 461 | 507
LOOK-RIDG-230.0-1 | 5029 | LOOKOUT SUBSTATION | XCEL | RIDGE SUBSTATION | XCEL | 70266 | 70355 | Xcel Owned | L5029 METER VAR | SECONDARY_CURRENT_LIMITATION | RIDG | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
LOOK-RIDG-230.0-1 | 5029 | LOOKOUT SUBSTATION | XCEL | RIDGE SUBSTATION | XCEL | 70266 | 70355 | Xcel Owned | 5029 METER VAR | SECONDARY_CURRENT_LIMITATION | LOOK | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
FLUP-HNLK-230.0-1 | 5047 | FORT LUPTON SUBSTATION | XCEL | HENRY LAKE (Tri State) | FOREIGN | 70192 | 70605 | Xcel Owned | FLUP-HNLK-230.0-1 | FACILITY |  | 1270 | 1397 | 1447 | 1592 | 506 | 557 | 576 | 634
FLUP-HNLK-230.0-1 | 5047 | FORT LUPTON SUBSTATION | XCEL | HENRY LAKE (Tri State) | FOREIGN | 70192 | 70605 | Xcel Owned | FLUP-HNLK-230.0-1 | Transmission Line | 5047 | 1270 | 1397 | 1447 | 1592 | 506 | 557 | 576 | 634
CHER-SISA-230.0-1 | 5055 | CHEROKEE SWITCHYARD SUBSTATION | XCEL | SILVER SADDLE SUBSTATION | XCEL | 70107 | 70609 | Xcel Owned | CHER-SISA-230.0-1 | FACILITY |  | 1271 | 1398 | 1448 | 1593 | 506 | 557 | 577 | 635
CHER-SISA-230.0-1 | 5055 | CHEROKEE SWITCHYARD SUBSTATION | XCEL | SILVER SADDLE SUBSTATION | XCEL | 70107 | 70609 | Xcel Owned | CHER-SISA-230.0-1 | Transmission Line | 5055 | 1271 | 1398 | 1448 | 1593 | 506 | 557 | 577 | 635
CHER-LACO-230.0-1 | 5057 | CHEROKEE SWITCHYARD SUBSTATION | XCEL | LACOMBE SUBSTATION | XCEL | 70107 | 70324 | Xcel Owned | CHER-LACO-230.0-1 | FACILITY |  | 1943 | 2295 | 2200 | 2400 | 774 | 914 | 876 | 956
CHER-LACO-230.0-1 | 5057 | CHEROKEE SWITCHYARD SUBSTATION | XCEL | LACOMBE SUBSTATION | XCEL | 70107 | 70324 | Xcel Owned | 2" (CU 40) | BUSBAR_SECTION | CHER | 1943 | 2295 | 2340 | 2626 | 774 | 914 | 932 | 1046
CHER-LACO-230.0-1 | 5057 | CHEROKEE SWITCHYARD SUBSTATION | XCEL | LACOMBE SUBSTATION | XCEL | 70107 | 70324 | Xcel Owned | CHER-LACO-230.0-1 | Transmission Line | 5057 | 2200 | 2420 | 2200 | 2420 | 876 | 964 | 876 | 964
CHER-LACO-230.0-1 | 5057 | CHEROKEE SWITCHYARD SUBSTATION | XCEL | LACOMBE SUBSTATION | XCEL | 70107 | 70324 | Xcel Owned | 5057 PKG-P | SECONDARY_CURRENT_LIMITATION | CHER | 2400 | 2400 | 2400 | 2400 | 956 | 956 | 956 | 956
CHER-LACO-230.0-1 | 5057 | CHEROKEE SWITCHYARD SUBSTATION | XCEL | LACOMBE SUBSTATION | XCEL | 70107 | 70324 | Xcel Owned | 5057_PKG-P | SECONDARY_CURRENT_LIMITATION | LACO | 2400 | 2400 | 2400 | 2400 | 956 | 956 | 956 | 956
CHER-LACO-230.0-1 | 5057 | CHEROKEE SWITCHYARD SUBSTATION | XCEL | LACOMBE SUBSTATION | XCEL | 70107 | 70324 | Xcel Owned | 5290 PK-2 | SECONDARY_CURRENT_LIMITATION | LACO | 2400 | 2400 | 2400 | 2400 | 956 | 956 | 956 | 956
CHER-LACO-230.0-1 | 5057 | CHEROKEE SWITCHYARD SUBSTATION | XCEL | LACOMBE SUBSTATION | XCEL | 70107 | 70324 | Xcel Owned | 5057 PK-2 | SECONDARY_CURRENT_LIMITATION | LACO | 2400 | 2400 | 2400 | 2400 | 956 | 956 | 956 | 956
CHER-LACO-230.0-1 | 5057 | CHEROKEE SWITCHYARD SUBSTATION | XCEL | LACOMBE SUBSTATION | XCEL | 70107 | 70324 | Xcel Owned | 5290 135Y | CURRENT_TRANSFORMER | LACO | 2400 | 2400 | 2400 | 2400 | 956 | 956 | 956 | 956
ARVA-CHER-230.0-1 | 5067 | ARVADA SUBSTATION | XCEL | CHEROKEE SWITCHYARD SUBSTATION | XCEL | 70041 | 70107 | Xcel Owned | ARVA-CHER-230.0-1 | FACILITY |  | 1270 | 1397 | 1447 | 1592 | 506 | 557 | 576 | 634
ARVA-CHER-230.0-1 | 5067 | ARVADA SUBSTATION | XCEL | CHEROKEE SWITCHYARD SUBSTATION | XCEL | 70041 | 70107 | Xcel Owned | ARVA-CHER-230.0-1 | Transmission Line | 5067 | 1270 | 1397 | 1447 | 1592 | 506 | 557 | 576 | 634
RIDG-ARVA-230.0-1 | 5067 | RIDGE SUBSTATION | XCEL | ARVADA SUBSTATION | XCEL | 70355 | 70041 | Xcel Owned | RIDG-ARVA-230.0-1 | FACILITY |  | 1270 | 1397 | 1447 | 1592 | 506 | 557 | 576 | 634
RIDG-ARVA-230.0-1 | 5067 | RIDGE SUBSTATION | XCEL | ARVADA SUBSTATION | XCEL | 70355 | 70041 | Xcel Owned | RIDG-ARVA-230.0-1 | Transmission Line | 5067 | 1270 | 1397 | 1447 | 1592 | 506 | 557 | 576 | 634
DANI-MARC-230.0-1 | 5085 | DANIELS PARK 115 & 230KV SUBSTATION | XCEL | MARCY SUBSTATION | XCEL | 70139 | 70278 | Xcel Owned | DANI-MARC-230.0-1 | FACILITY |  | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
DANI-MARC-230.0-1 | 5085 | DANIELS PARK 115 & 230KV SUBSTATION | XCEL | MARCY SUBSTATION | XCEL | 70139 | 70278 | Xcel Owned | TL5085 MTR AMP | SECONDARY_CURRENT_LIMITATION | DANI | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
DANI-MARC-230.0-1 | 5085 | DANIELS PARK 115 & 230KV SUBSTATION | XCEL | MARCY SUBSTATION | XCEL | 70139 | 70278 | Xcel Owned | TL5085 MTR WATT | SECONDARY_CURRENT_LIMITATION | DANI | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
DANI-MARC-230.0-1 | 5085 | DANIELS PARK 115 & 230KV SUBSTATION | XCEL | MARCY SUBSTATION | XCEL | 70139 | 70278 | Xcel Owned | TL5085 MTR VAR | SECONDARY_CURRENT_LIMITATION | DANI | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
MARC-WATE-230.0-1 | 5085 | MARCY SUBSTATION | XCEL | WATERTON SUBSTATION | XCEL | 70278 | 70464 | Xcel Owned | MARC-WATE-230.0-1 | FACILITY |  | 1270 | 1397 | 1447 | 1592 | 506 | 557 | 576 | 634
MARC-WATE-230.0-1 | 5085 | MARCY SUBSTATION | XCEL | WATERTON SUBSTATION | XCEL | 70278 | 70464 | Xcel Owned | MARC-WATE-230.0-1 | Transmission Line | 5085 | 1270 | 1397 | 1447 | 1592 | 506 | 557 | 576 | 634
ARAP-SANT_TP-230.0-1 | 5107 | ARAPAHOE SUBSTATION | XCEL | SANTA FE TAP | XCEL | 70038 | 2122 | Xcel Owned | ARAP-SANT_TP-230.0-1 | FACILITY |  | 1270 | 1397 | 1447 | 1592 | 506 | 557 | 576 | 634
ARAP-SANT_TP-230.0-1 | 5107 | ARAPAHOE SUBSTATION | XCEL | SANTA FE TAP | XCEL | 70038 | 2122 | Xcel Owned | ARAP-SANT_TP-230.0-1 | Transmission Line | 5107 | 1270 | 1397 | 1447 | 1592 | 506 | 557 | 576 | 634
DANI-SANT-230.0-1 | 5107 | DANIELS PARK 115 & 230KV SUBSTATION | XCEL | SANTA FE SUBSTATION | XCEL | 70139 | 70527 | Xcel Owned | DANI-SANT-230.0-1 | FACILITY |  | 1270 | 1397 | 1447 | 1592 | 506 | 557 | 576 | 634
DANI-SANT-230.0-1 | 5107 | DANIELS PARK 115 & 230KV SUBSTATION | XCEL | SANTA FE SUBSTATION | XCEL | 70139 | 70527 | Xcel Owned | DANI-SANT-230.0-1 | Transmission Line | 5107 | 1270 | 1397 | 1447 | 1592 | 506 | 557 | 576 | 634
SANT_TP-SANT-230.0-1 | 5107 | SANTA FE TAP | XCEL | SANTA FE SUBSTATION | XCEL | 2122 | 70527 | Xcel Owned | SANT_TP-SANT-230.0-1 | FACILITY |  | 1270 | 1397 | 1447 | 1592 | 506 | 557 | 576 | 634
SANT_TP-SANT-230.0-1 | 5107 | SANTA FE TAP | XCEL | SANTA FE SUBSTATION | XCEL | 2122 | 70527 | Xcel Owned | SANT_TP-SANT-230.0-1 | Transmission Line | 5107 | 1270 | 1397 | 1447 | 1592 | 506 | 557 | 576 | 634
DANI-WATE-230.0-1 | 5109 | DANIELS PARK 115 & 230KV SUBSTATION | XCEL | WATERTON SUBSTATION | XCEL | 70139 | 70464 | Xcel Owned | DANI-WATE-230.0-1 | FACILITY |  | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
DANI-WATE-230.0-1 | 5109 | DANIELS PARK 115 & 230KV SUBSTATION | XCEL | WATERTON SUBSTATION | XCEL | 70139 | 70464 | Xcel Owned | TL5109 MTR AMP | SECONDARY_CURRENT_LIMITATION | DANI | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
DANI-WATE-230.0-1 | 5109 | DANIELS PARK 115 & 230KV SUBSTATION | XCEL | WATERTON SUBSTATION | XCEL | 70139 | 70464 | Xcel Owned | TL5109 MTR WATT | SECONDARY_CURRENT_LIMITATION | DANI | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
DANI-WATE-230.0-1 | 5109 | DANIELS PARK 115 & 230KV SUBSTATION | XCEL | WATERTON SUBSTATION | XCEL | 70139 | 70464 | Xcel Owned | TL5109 MTR VAR | SECONDARY_CURRENT_LIMITATION | DANI | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
DANI-PRAI-230.0-1 | 5111 | DANIELS PARK 115 & 230KV SUBSTATION | XCEL | PRAIRIE SUBSTATION | XCEL | 70139 | 70323 | Xcel Owned | DANI-PRAI-230.0-1 | FACILITY |  | 1200 | 1200 | 1325 | 1325 | 478 | 478 | 528 | 528
DANI-PRAI-230.0-1 | 5111 | DANIELS PARK 115 & 230KV SUBSTATION | XCEL | PRAIRIE SUBSTATION | XCEL | 70139 | 70323 | Xcel Owned |  | LINE_TRAP | DANI | 1200 | 1200 | 1325 | 1325 | 478 | 478 | 528 | 528
GREE-PRAI-230.0-2 | 5111 | GREENWOOD SUBSTATION | XCEL | PRAIRIE SUBSTATION | XCEL | 70481 | 70331 | Xcel Owned | GREE-PRAI-230.0-2 | FACILITY |  | 1200 | 1200 | 1248 | 1248 | 478 | 478 | 497 | 497
GREE-PRAI-230.0-2 | 5111 | GREENWOOD SUBSTATION | XCEL | PRAIRIE SUBSTATION | XCEL | 70481 | 70331 | Xcel Owned |  | LINE_TRAP | GREE | 1200 | 1200 | 1248 | 1248 | 478 | 478 | 497 | 497
DANI-MSST-230.0-1 | 5113 | DANIELS PARK 115 & 230KV SUBSTATION | XCEL | MISSILE SITE | XCEL | 70139 | 70623 | Xcel Owned | DANI-MSST-230.0-1 | FACILITY |  | 1860 | 2000 | 2000 | 2000 | 741 | 797 | 797 | 797
DANI-MSST-230.0-1 | 5113 | DANIELS PARK 115 & 230KV SUBSTATION | XCEL | MISSILE SITE | XCEL | 70139 | 70623 | Xcel Owned | DANI-MSST-230.0-1 | Transmission Line | 5113 | 1860 | 2046 | 2112 | 2324 | 741 | 815 | 841 | 926
DANI-MSST-230.0-1 | 5113 | DANIELS PARK 115 & 230KV SUBSTATION | XCEL | MISSILE SITE | XCEL | 70139 | 70623 | Xcel Owned | TL5113 MTR AMP | SECONDARY_CURRENT_LIMITATION | DANI | 2000 | 2000 | 2000 | 2000 | 797 | 797 | 797 | 797
DANI-MSST-230.0-1 | 5113 | DANIELS PARK 115 & 230KV SUBSTATION | XCEL | MISSILE SITE | XCEL | 70139 | 70623 | Xcel Owned | TL5113 MTR WATT | SECONDARY_CURRENT_LIMITATION | DANI | 2000 | 2000 | 2000 | 2000 | 797 | 797 | 797 | 797
DANI-MSST-230.0-1 | 5113 | DANIELS PARK 115 & 230KV SUBSTATION | XCEL | MISSILE SITE | XCEL | 70139 | 70623 | Xcel Owned | TL5113 MTR VAR | SECONDARY_CURRENT_LIMITATION | DANI | 2000 | 2000 | 2000 | 2000 | 797 | 797 | 797 | 797
DANI-MSST-230.0-1 | 5113 | DANIELS PARK 115 & 230KV SUBSTATION | XCEL | MISSILE SITE | XCEL | 70139 | 70623 | Xcel Owned |  | LINE_TRAP | DANI | 2000 | 2000 | 2208 | 2208 | 797 | 797 | 880 | 880
DANI-MSST-230.0-1 | 5113 | DANIELS PARK 115 & 230KV SUBSTATION | XCEL | MISSILE SITE | XCEL | 70139 | 70623 | Xcel Owned |  | LINE_TRAP | MSST | 2000 | 2000 | 2208 | 2208 | 797 | 797 | 880 | 880
DANI-SRDG-230.0-1 | 5115 | DANIELS PARK 115 & 230KV SUBSTATION | XCEL | SURREY RIDGE | XCEL | 70139 | 70284 | Xcel Owned | DANI-SRDG-230.0-1 | FACILITY |  | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
DANI-SRDG-230.0-1 | 5115 | DANIELS PARK 115 & 230KV SUBSTATION | XCEL | SURREY RIDGE | XCEL | 70139 | 70284 | Xcel Owned | TL5115 MTR WATT | SECONDARY_CURRENT_LIMITATION | DANI | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
DANI-SRDG-230.0-1 | 5115 | DANIELS PARK 115 & 230KV SUBSTATION | XCEL | SURREY RIDGE | XCEL | 70139 | 70284 | Xcel Owned | TL5115 MTR VAR | SECONDARY_CURRENT_LIMITATION | DANI | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
DANI-SRDG-230.0-1 | 5115 | DANIELS PARK 115 & 230KV SUBSTATION | XCEL | SURREY RIDGE | XCEL | 70139 | 70284 | Xcel Owned | TL5115 MTR AMP | SECONDARY_CURRENT_LIMITATION | DANI | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
SRDG-LEMO-230.0-1 | 5115 | SURREY RIDGE | XCEL | LEMON GULCH | XCEL | 70284 | 70533 | Xcel Owned | SRDG-LEMO-230.0-1 | FACILITY |  | 1847 | 2000 | 2000 | 2000 | 736 | 797 | 797 | 797
SRDG-LEMO-230.0-1 | 5115 | SURREY RIDGE | XCEL | LEMON GULCH | XCEL | 70284 | 70533 | Xcel Owned | Swift | BUSBAR_SECTION | LEMO | 1847 | 2032 | 2102 | 2312 | 736 | 809 | 837 | 921
SRDG-LEMO-230.0-1 | 5115 | SURREY RIDGE | XCEL | LEMON GULCH | XCEL | 70284 | 70533 | Xcel Owned | 5115-1 | CIRCUIT_SWITCHER | LEMO | 2000 | 2000 | 2000 | 2000 | 797 | 797 | 797 | 797
SRDG-LEMO-230.0-1 | 5115 | SURREY RIDGE | XCEL | LEMON GULCH | XCEL | 70284 | 70533 | Xcel Owned | 5115-5 | CIRCUIT_SWITCHER | SRDG | 2000 | 2000 | 2000 | 2000 | 797 | 797 | 797 | 797
SULP-LEMO-230.0-1 | 5115 | SULPHUR SUBSTATION | XCEL | LEMON GULCH | XCEL | 70524 | 70533 | Xcel Owned | SULP-LEMO-230.0-1 | FACILITY |  | 1807 | 1988 | 2000 | 2000 | 720 | 792 | 797 | 797
SULP-LEMO-230.0-1 | 5115 | SULPHUR SUBSTATION | XCEL | LEMON GULCH | XCEL | 70524 | 70533 | Xcel Owned | Swift | BUSBAR_SECTION | SULP | 1807 | 1988 | 2056 | 2262 | 720 | 792 | 819 | 901
SULP-LEMO-230.0-1 | 5115 | SULPHUR SUBSTATION | XCEL | LEMON GULCH | XCEL | 70524 | 70533 | Xcel Owned | 5115-3 | CIRCUIT_SWITCHER | LEMO | 2000 | 2000 | 2000 | 2000 | 797 | 797 | 797 | 797
DANI-JFUL-230.0-1 | 5119 | DANIELS PARK 115 & 230KV SUBSTATION | XCEL | JACKSON FULLER SUBSTATION | XCEL | 70139 | 73477 | Xcel Owned | DANI-JFUL-230.0-1 | FACILITY |  | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
DANI-JFUL-230.0-1 | 5119 | DANIELS PARK 115 & 230KV SUBSTATION | XCEL | JACKSON FULLER SUBSTATION | XCEL | 70139 | 73477 | Xcel Owned | TL5119 MTR AMP | SECONDARY_CURRENT_LIMITATION | DANI | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
DANI-JFUL-230.0-1 | 5119 | DANIELS PARK 115 & 230KV SUBSTATION | XCEL | JACKSON FULLER SUBSTATION | XCEL | 70139 | 73477 | Xcel Owned | TL5119 MTR VAR | SECONDARY_CURRENT_LIMITATION | DANI | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
DANI-JFUL-230.0-1 | 5119 | DANIELS PARK 115 & 230KV SUBSTATION | XCEL | JACKSON FULLER SUBSTATION | XCEL | 70139 | 73477 | Xcel Owned | TL5119 MTR WATT | SECONDARY_CURRENT_LIMITATION | DANI | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
FVNG-MIDW-230.0-1 | 5123 | FOUNTAIN VALLEY NUG SWITCHYARD | XCEL | MIDWAY SUBSTATION | XCEL | 70193 | 70286 | Xcel Owned | FVNG-MIDW-230.0-1 | FACILITY |  | 1267 | 1394 | 1443 | 1500 | 505 | 555 | 575 | 598
FVNG-MIDW-230.0-1 | 5123 | FOUNTAIN VALLEY NUG SWITCHYARD | XCEL | MIDWAY SUBSTATION | XCEL | 70193 | 70286 | Xcel Owned | FVNG-MIDW-230.0-1 | Transmission Line | 5123 | 1267 | 1394 | 1443 | 1587 | 505 | 555 | 575 | 632
FVNG-MIDW-230.0-1 | 5123 | FOUNTAIN VALLEY NUG SWITCHYARD | XCEL | MIDWAY SUBSTATION | XCEL | 70193 | 70286 | Xcel Owned | 230 BUSN MU C | CURRENT_TRANSFORMER | FVNG | 1500 | 1500 | 1500 | 1500 | 598 | 598 | 598 | 598
FVNG-MIDW-230.0-1 | 5123 | FOUNTAIN VALLEY NUG SWITCHYARD | XCEL | MIDWAY SUBSTATION | XCEL | 70193 | 70286 | Xcel Owned | 230 BUSN MU A | CURRENT_TRANSFORMER | FVNG | 1500 | 1500 | 1500 | 1500 | 598 | 598 | 598 | 598
FVNG-MIDW-230.0-1 | 5123 | FOUNTAIN VALLEY NUG SWITCHYARD | XCEL | MIDWAY SUBSTATION | XCEL | 70193 | 70286 | Xcel Owned | 230 BUSN MU B | CURRENT_TRANSFORMER | FVNG | 1500 | 1500 | 1500 | 1500 | 598 | 598 | 598 | 598
MIDW-JFUL-230.0-1 | 5129 | MIDWAY SUBSTATION | XCEL | JACKSON FULLER SUBSTATION | XCEL | 70286 | 73477 | Xcel Owned | MIDW-JFUL-230.0-1 | FACILITY |  | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
MIDW-JFUL-230.0-1 | 5129 | MIDWAY SUBSTATION | XCEL | JACKSON FULLER SUBSTATION | XCEL | 70286 | 73477 | Xcel Owned | 5129_VAR_230KV | SECONDARY_CURRENT_LIMITATION | MIDW | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
MALT-HARS-230.0-1 | 5145 | MALTA SUBSTATION | XCEL | HARTSEL (IREA) | XCEL | 70274 | 70927 | Xcel Owned | MALT-HARS-230.0-1 | FACILITY |  | 1200 | 1200 | 1248 | 1248 | 478 | 478 | 497 | 497
MALT-HARS-230.0-1 | 5145 | MALTA SUBSTATION | XCEL | HARTSEL (IREA) | XCEL | 70274 | 70927 | Xcel Owned |  | LINE_TRAP | MALT | 1200 | 1200 | 1248 | 1248 | 478 | 478 | 497 | 497
MALT-BASA-230.0-1 | 5149 | MALTA SUBSTATION | XCEL | BASALT SUBSTATION | XCEL | 70274 | 79004 | Xcel Owned | MALT-BASA-230.0-1 | FACILITY |  | 900 | 900 | 900 | 900 | 359 | 359 | 359 | 359
MALT-BASA-230.0-1 | 5149 | MALTA SUBSTATION | XCEL | BASALT SUBSTATION | XCEL | 70274 | 79004 | Xcel Owned | 230 L5149 C | CURRENT_TRANSFORMER | BASA | 900 | 900 | 900 | 900 | 359 | 359 | 359 | 359
MALT-BASA-230.0-1 | 5149 | MALTA SUBSTATION | XCEL | BASALT SUBSTATION | XCEL | 70274 | 79004 | Xcel Owned | 230 L5149 B | CURRENT_TRANSFORMER | BASA | 900 | 900 | 900 | 900 | 359 | 359 | 359 | 359
MALT-BASA-230.0-1 | 5149 | MALTA SUBSTATION | XCEL | BASALT SUBSTATION | XCEL | 70274 | 79004 | Xcel Owned | 230 L5149 A | CURRENT_TRANSFORMER | BASA | 900 | 900 | 900 | 900 | 359 | 359 | 359 | 359
HOST-MURP-230.0-1 | 5163 | HOMESTEAD SUBSTATION | XCEL | MURPHY CREEK SUBSTATION | XCEL | 70513 | 70551 | Xcel Owned | HOST-MURP-230.0-1 | FACILITY |  | 1849 | 1918 | 1918 | 1918 | 736 | 764 | 764 | 764
HOST-MURP-230.0-1 | 5163 | HOMESTEAD SUBSTATION | XCEL | MURPHY CREEK SUBSTATION | XCEL | 70513 | 70551 | Xcel Owned | Swift | BUSBAR_SECTION | HOST | 1849 | 2034 | 2104 | 2314 | 736 | 810 | 838 | 922
HOST-MURP-230.0-1 | 5163 | HOMESTEAD SUBSTATION | XCEL | MURPHY CREEK SUBSTATION | XCEL | 70513 | 70551 | Xcel Owned | HOST-MURP-230.0-1 | Transmission Line | 5163 | 1860 | 1918 | 1918 | 1918 | 741 | 764 | 764 | 764
HOST-SULP-230.0-1 | 5163 | HOMESTEAD SUBSTATION | XCEL | SULPHUR SUBSTATION | XCEL | 70513 | 70524 | Xcel Owned | HOST-SULP-230.0-1 | FACILITY |  | 1849 | 2000 | 2000 | 2000 | 736 | 797 | 797 | 797
HOST-SULP-230.0-1 | 5163 | HOMESTEAD SUBSTATION | XCEL | SULPHUR SUBSTATION | XCEL | 70513 | 70524 | Xcel Owned | Swift | BUSBAR_SECTION | HOST | 1849 | 2034 | 2104 | 2314 | 736 | 810 | 838 | 922
HOST-SULP-230.0-1 | 5163 | HOMESTEAD SUBSTATION | XCEL | SULPHUR SUBSTATION | XCEL | 70513 | 70524 | Xcel Owned | 5163-6 | CIRCUIT_SWITCHER | HOST | 2000 | 2000 | 2000 | 2000 | 797 | 797 | 797 | 797
SMOK-MURP-230.0-1 | 5163 | SMOKY HILL SUBSTATION | XCEL | MURPHY CREEK SUBSTATION | XCEL | 70396 | 70551 | Xcel Owned | SMOK-MURP-230.0-1 | FACILITY |  | 1860 | 2000 | 2000 | 2000 | 741 | 797 | 797 | 797
SMOK-MURP-230.0-1 | 5163 | SMOKY HILL SUBSTATION | XCEL | MURPHY CREEK SUBSTATION | XCEL | 70396 | 70551 | Xcel Owned | SMOK-MURP-230.0-1 | Transmission Line | 5163 | 1860 | 2046 | 2112 | 2323 | 741 | 815 | 841 | 925
SMOK-MURP-230.0-1 | 5163 | SMOKY HILL SUBSTATION | XCEL | MURPHY CREEK SUBSTATION | XCEL | 70396 | 70551 | Xcel Owned | 5163-2 | CIRCUIT_SWITCHER | MURP | 2000 | 2000 | 2000 | 2000 | 797 | 797 | 797 | 797
QUIN-BRIC-230.0-1 | 5165 | QUINCY SUBSTATION | XCEL | BRICK CENTER | XCEL | 70343 | 70545 | Xcel Owned | QUIN-BRIC-230.0-1 | FACILITY |  | 2000 | 2000 | 2080 | 2080 | 797 | 797 | 829 | 829
QUIN-BRIC-230.0-1 | 5165 | QUINCY SUBSTATION | XCEL | BRICK CENTER | XCEL | 70343 | 70545 | Xcel Owned |  | LINE_TRAP | BRIC | 2000 | 2000 | 2080 | 2080 | 797 | 797 | 829 | 829
QUIN-SMOK-230.0-1 | 5165 | QUINCY SUBSTATION | XCEL | SMOKY HILL SUBSTATION | XCEL | 70343 | 70396 | Xcel Owned | QUIN-SMOK-230.0-1 | FACILITY |  | 1904 | 2000 | 2167 | 2208 | 758 | 797 | 863 | 880
QUIN-SMOK-230.0-1 | 5165 | QUINCY SUBSTATION | XCEL | SMOKY HILL SUBSTATION | XCEL | 70343 | 70396 | Xcel Owned | QUIN-SMOK-230.0-1 | Transmission Line | 5165 | 1904 | 2094 | 2167 | 2384 | 758 | 834 | 863 | 950
QUIN-SMOK-230.0-1 | 5165 | QUINCY SUBSTATION | XCEL | SMOKY HILL SUBSTATION | XCEL | 70343 | 70396 | Xcel Owned |  | LINE_TRAP | SMOK | 2000 | 2000 | 2208 | 2208 | 797 | 797 | 880 | 880
BUCK-JEWE-230.0-1 | 5167 | BUCKLEY SUBSTATION | XCEL | JEWELL SUBSTATION | XCEL | 70067 | 70512 | Xcel Owned | BUCK-JEWE-230.0-1 | FACILITY |  | 1263 | 1389 | 1416 | 1558 | 503 | 553 | 564 | 621
BUCK-JEWE-230.0-1 | 5167 | BUCKLEY SUBSTATION | XCEL | JEWELL SUBSTATION | XCEL | 70067 | 70512 | Xcel Owned | BUCK-JEWE-230.0-1 | Transmission Line | 5167 | 1263 | 1389 | 1416 | 1558 | 503 | 553 | 564 | 621
BUCK-SMOK-230.0-2 | 5167 | BUCKLEY SUBSTATION | XCEL | SMOKY HILL SUBSTATION | XCEL | 70046 | 70396 | Xcel Owned | BUCK-SMOK-230.0-2 | FACILITY |  | 1270 | 1397 | 1447 | 1592 | 506 | 557 | 576 | 634
BUCK-SMOK-230.0-2 | 5167 | BUCKLEY SUBSTATION | XCEL | SMOKY HILL SUBSTATION | XCEL | 70046 | 70396 | Xcel Owned | BUCK-SMOK-230.0-2 | Transmission Line | 5167 | 1270 | 1397 | 1447 | 1592 | 506 | 557 | 576 | 634
SULL-JEWE-230.0-1 | 5167 | SULLIVAN SUBSTATION | XCEL | JEWELL SUBSTATION | XCEL | 70417 | 70512 | Xcel Owned | SULL-JEWE-230.0-1 | FACILITY |  | 1266 | 1393 | 1443 | 1587 | 504 | 555 | 575 | 632
SULL-JEWE-230.0-1 | 5167 | SULLIVAN SUBSTATION | XCEL | JEWELL SUBSTATION | XCEL | 70417 | 70512 | Xcel Owned | SULL-JEWE-230.0-1 | Transmission Line | 5167 | 1266 | 1393 | 1443 | 1587 | 504 | 555 | 575 | 632
JORD-ORCH-230.0-1 | 5169 | JORDAN ROAD SUBSTATION | XCEL | ORCHARD SUBSTATION | XCEL | 70241 | 70313 | Xcel Owned | JORD-ORCH-230.0-1 | FACILITY |  | 1420 | 1562 | 1600 | 1600 | 566 | 622 | 637 | 637
JORD-ORCH-230.0-1 | 5169 | JORDAN ROAD SUBSTATION | XCEL | ORCHARD SUBSTATION | XCEL | 70241 | 70313 | Xcel Owned | Narcissus | BUSBAR_SECTION | JORD | 1420 | 1562 | 1618 | 1780 | 566 | 622 | 645 | 709
JORD-ORCH-230.0-1 | 5169 | JORDAN ROAD SUBSTATION | XCEL | ORCHARD SUBSTATION | XCEL | 70241 | 70313 | Xcel Owned | 5169-7S | CIRCUIT_SWITCHER | ORCH | 1600 | 1600 | 1600 | 1600 | 637 | 637 | 637 | 637
MEAD-ORCH-230.0-1 | 5169 | MEADOW HILLS SUBSTATION | XCEL | ORCHARD SUBSTATION | XCEL | 70283 | 70313 | Xcel Owned | MEAD-ORCH-230.0-1 | FACILITY |  | 1600 | 1600 | 1600 | 1600 | 637 | 637 | 637 | 637
MEAD-ORCH-230.0-1 | 5169 | MEADOW HILLS SUBSTATION | XCEL | ORCHARD SUBSTATION | XCEL | 70283 | 70313 | Xcel Owned | 5169-2 | CIRCUIT_SWITCHER | MEAD | 1600 | 1600 | 1600 | 1600 | 637 | 637 | 637 | 637
MEAD-ORCH-230.0-1 | 5169 | MEADOW HILLS SUBSTATION | XCEL | ORCHARD SUBSTATION | XCEL | 70283 | 70313 | Xcel Owned | 5169-5N | CIRCUIT_SWITCHER | ORCH | 1600 | 1600 | 1600 | 1600 | 637 | 637 | 637 | 637
MEAD-SMOK-230.0-1 | 5169 | MEADOW HILLS SUBSTATION | XCEL | SMOKY HILL SUBSTATION | XCEL | 70283 | 70396 | Xcel Owned | MEAD-SMOK-230.0-1 | FACILITY |  | 1417 | 1558 | 1600 | 1600 | 564 | 621 | 637 | 637
MEAD-SMOK-230.0-1 | 5169 | MEADOW HILLS SUBSTATION | XCEL | SMOKY HILL SUBSTATION | XCEL | 70283 | 70396 | Xcel Owned | Narcissus | BUSBAR_SECTION | SMOK | 1417 | 1558 | 1615 | 1776 | 564 | 621 | 643 | 708
MEAD-SMOK-230.0-1 | 5169 | MEADOW HILLS SUBSTATION | XCEL | SMOKY HILL SUBSTATION | XCEL | 70283 | 70396 | Xcel Owned | 5169-1 | CIRCUIT_SWITCHER | MEAD | 1600 | 1600 | 1600 | 1600 | 637 | 637 | 637 | 637
SMOK-POWH-230.0-1 | 5171 | SMOKY HILL SUBSTATION | XCEL | POWHATON SUBSTATION | XCEL | 70396 | 70532 | Xcel Owned | SMOK-POWH-230.0-1 | FACILITY |  | 2000 | 2000 | 2000 | 2000 | 797 | 797 | 797 | 797
SMOK-POWH-230.0-1 | 5171 | SMOKY HILL SUBSTATION | XCEL | POWHATON SUBSTATION | XCEL | 70396 | 70532 | Xcel Owned | 5171-1 | CIRCUIT_SWITCHER | POWH | 2000 | 2000 | 2000 | 2000 | 797 | 797 | 797 | 797
SPRU-POWH-230.0-1 | 5171 | SPRUCE SUBSTATION | XCEL | POWHATON SUBSTATION | XCEL | 70528 | 70532 | Xcel Owned | SPRU-POWH-230.0-1 | FACILITY |  | 1800 | 1800 | 1800 | 1800 | 717 | 717 | 717 | 717
SPRU-POWH-230.0-1 | 5171 | SPRUCE SUBSTATION | XCEL | POWHATON SUBSTATION | XCEL | 70528 | 70532 | Xcel Owned | 5171 AMP XDCR | SECONDARY_CURRENT_LIMITATION | SPRU | 1800 | 1800 | 1800 | 1800 | 717 | 717 | 717 | 717
SMOK-SPRU-230.0-1 | 5177 | SMOKY HILL SUBSTATION | XCEL | SPRUCE SUBSTATION | XCEL | 70396 | 70528 | Xcel Owned | SMOK-SPRU-230.0-1 | FACILITY |  | 1800 | 1800 | 1800 | 1800 | 717 | 717 | 717 | 717
SMOK-SPRU-230.0-1 | 5177 | SMOKY HILL SUBSTATION | XCEL | SPRUCE SUBSTATION | XCEL | 70396 | 70528 | Xcel Owned | 5177 AMP XDCR | SECONDARY_CURRENT_LIMITATION | SPRU | 1800 | 1800 | 1800 | 1800 | 717 | 717 | 717 | 717
HMIL-SMOK-230.0-1 | 5179 | HARVEST MILE | XCEL | SMOKY HILL SUBSTATION | XCEL | 70596 | 70396 | Xcel Owned | HMIL-SMOK-230.0-1 | FACILITY |  | 2856 | 2880 | 2880 | 2880 | 1138 | 1147 | 1147 | 1147
HMIL-SMOK-230.0-1 | 5179 | HARVEST MILE | XCEL | SMOKY HILL SUBSTATION | XCEL | 70596 | 70396 | Xcel Owned | Bittern | BUSBAR_SECTION | HMIL | 2856 | 3142 | 3256 | 3582 | 1138 | 1252 | 1297 | 1427
HMIL-SMOK-230.0-1 | 5179 | HARVEST MILE | XCEL | SMOKY HILL SUBSTATION | XCEL | 70596 | 70396 | Xcel Owned | TL5179 DFR | SECONDARY_CURRENT_LIMITATION | SMOK | 2880 | 2880 | 2880 | 2880 | 1147 | 1147 | 1147 | 1147
FLUP-JLGR-230.0-1 | 5183 | FORT LUPTON SUBSTATION | XCEL | J. L. Green | FOREIGN | 70192 | 70529 | Xcel Owned | FLUP-JLGR-230.0-1 | FACILITY |  | 1446 | 1591 | 1599 | 1627 | 576 | 634 | 637 | 648
FLUP-JLGR-230.0-1 | 5183 | FORT LUPTON SUBSTATION | XCEL | J. L. Green | FOREIGN | 70192 | 70529 | Xcel Owned | FLUP-JLGR-230.0-1 | Transmission Line | 5183 | 1446 | 1591 | 1648 | 1813 | 576 | 634 | 657 | 722
FLUP-JLGR-230.0-1 | 5183 | FORT LUPTON SUBSTATION | XCEL | J. L. Green | FOREIGN | 70192 | 70529 | Xcel Owned | Foreign Ratings | Foreign Ratings | JLGR | 1599 | 1627 | 1599 | 1627 | 637 | 648 | 637 | 648
SPRU-CHAM-230.0-1 | 5185 | SPRUCE SUBSTATION | XCEL | CHAMBERS SUBSTATION | XCEL | 70528 | 70539 | Xcel Owned | SPRU-CHAM-230.0-1 | FACILITY |  | 1800 | 1800 | 1800 | 1800 | 717 | 717 | 717 | 717
SPRU-CHAM-230.0-1 | 5185 | SPRUCE SUBSTATION | XCEL | CHAMBERS SUBSTATION | XCEL | 70528 | 70539 | Xcel Owned | 5185 AMP XDCR | SECONDARY_CURRENT_LIMITATION | SPRU | 1800 | 1800 | 1800 | 1800 | 717 | 717 | 717 | 717
SPRU-PICA-230.0-1 | 5187 | SPRUCE SUBSTATION | XCEL | PICADILLY | XCEL | 70528 | 70530 | Xcel Owned | SPRU-PICA-230.0-1 | FACILITY |  | 1422 | 1565 | 1600 | 1600 | 567 | 623 | 637 | 637
SPRU-PICA-230.0-1 | 5187 | SPRUCE SUBSTATION | XCEL | PICADILLY | XCEL | 70528 | 70530 | Xcel Owned | Narcissus | BUSBAR_SECTION | PICA | 1422 | 1565 | 1621 | 1783 | 567 | 623 | 646 | 710
SPRU-PICA-230.0-1 | 5187 | SPRUCE SUBSTATION | XCEL | PICADILLY | XCEL | 70528 | 70530 | Xcel Owned | 5187-4 | CIRCUIT_SWITCHER | PICA | 1600 | 1600 | 1600 | 1600 | 637 | 637 | 637 | 637
TOWE-CHAM-230.0-1 | 5187 | TOWER SUBSTATION | XCEL | CHAMBERS SUBSTATION | XCEL | 70432 | 70539 | Xcel Owned | TOWE-CHAM-230.0-1 | FACILITY |  | 1423 | 1566 | 1600 | 1600 | 567 | 624 | 637 | 637
TOWE-CHAM-230.0-1 | 5187 | TOWER SUBSTATION | XCEL | CHAMBERS SUBSTATION | XCEL | 70432 | 70539 | Xcel Owned | Narcissus | BUSBAR_SECTION | TOWE | 1423 | 1566 | 1622 | 1784 | 567 | 624 | 646 | 711
TOWE-CHAM-230.0-1 | 5187 | TOWER SUBSTATION | XCEL | CHAMBERS SUBSTATION | XCEL | 70432 | 70539 | Xcel Owned | 5187-1 | CIRCUIT_SWITCHER | TOWE | 1600 | 1600 | 1600 | 1600 | 637 | 637 | 637 | 637
TOWE-PICA-230.0-1 | 5187 | TOWER SUBSTATION | XCEL | PICADILLY | XCEL | 70432 | 70530 | Xcel Owned | TOWE-PICA-230.0-1 | FACILITY |  | 1422 | 1565 | 1600 | 1600 | 567 | 623 | 637 | 637
TOWE-PICA-230.0-1 | 5187 | TOWER SUBSTATION | XCEL | PICADILLY | XCEL | 70432 | 70530 | Xcel Owned | Narcissus | BUSBAR_SECTION | PICA | 1422 | 1565 | 1621 | 1783 | 567 | 623 | 646 | 710
TOWE-PICA-230.0-1 | 5187 | TOWER SUBSTATION | XCEL | PICADILLY | XCEL | 70432 | 70530 | Xcel Owned | 5187-2 | CIRCUIT_SWITCHER | TOWE | 1600 | 1600 | 1600 | 1600 | 637 | 637 | 637 | 637
TOWE-PICA-230.0-1 | 5187 | TOWER SUBSTATION | XCEL | PICADILLY | XCEL | 70432 | 70530 | Xcel Owned | 5187-3 | CIRCUIT_SWITCHER | PICA | 1600 | 1600 | 1600 | 1600 | 637 | 637 | 637 | 637
IMBO-SPRU-230.0-1 | 5188, 5277 | IMBODEN SUBSTATION | XCEL | SPRUCE SUBSTATION | XCEL | 70526 | 70528 | Xcel Owned | IMBO-SPRU-230.0-1 | FACILITY |  | 1423 | 1565 | 1622 | 1784 | 567 | 624 | 646 | 711
IMBO-SPRU-230.0-1 | 5188, 5277 | IMBODEN SUBSTATION | XCEL | SPRUCE SUBSTATION | XCEL | 70526 | 70528 | Xcel Owned | Narcissus | BUSBAR_SECTION | IMBO | 1423 | 1565 | 1622 | 1784 | 567 | 624 | 646 | 711
ATLR-RIFL-230.0-1 | 5203 | RIFLE GENERATION (TSGT) | FOREIGN | RIFLE 230KV SUBSTATION (PSCO) | XCEL | 79250 | 70358 | Jointly Owned | ATLR-RIFL-230.0-1 | FACILITY |  | 399 | 400 | 399 | 442 | 159 | 159 | 159 | 176
ATLR-RIFL-230.0-1 | 5203 | RIFLE GENERATION (TSGT) | FOREIGN | RIFLE 230KV SUBSTATION (PSCO) | XCEL | 79250 | 70358 | Jointly Owned | Foreign Ratings | Foreign Ratings | ATLR | 399 | 515 | 399 | 515 | 159 | 205 | 159 | 205
ATLR-RIFL-230.0-1 | 5203 | RIFLE GENERATION (TSGT) | FOREIGN | RIFLE 230KV SUBSTATION (PSCO) | XCEL | 79250 | 70358 | Jointly Owned |  | LINE_TRAP | RIFL | 400 | 400 | 442 | 442 | 159 | 159 | 176 | 176
PARA-RIFL-230.0-1 | 5205 | PARACHUTE SUBSTATION | XCEL | RIFLE 230KV SUBSTATION (PSCO) | XCEL | 70309 | 70358 | Xcel Owned | PARA-RIFL-230.0-1 | FACILITY |  | 1085 | 1200 | 1200 | 1200 | 432 | 478 | 478 | 478
PARA-RIFL-230.0-1 | 5205 | PARACHUTE SUBSTATION | XCEL | RIFLE 230KV SUBSTATION (PSCO) | XCEL | 70309 | 70358 | Xcel Owned | Curlew | BUSBAR_SECTION | RIFL | 1085 | 1265 | 1296 | 1441 | 432 | 504 | 516 | 574
PARA-RIFL-230.0-1 | 5205 | PARACHUTE SUBSTATION | XCEL | RIFLE 230KV SUBSTATION (PSCO) | XCEL | 70309 | 70358 | Xcel Owned | 5205 246X | CURRENT_TRANSFORMER | RIFL | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
PARA-RIFL-230.0-1 | 5205 | PARACHUTE SUBSTATION | XCEL | RIFLE 230KV SUBSTATION (PSCO) | XCEL | 70309 | 70358 | Xcel Owned | 5205 246Y | CURRENT_TRANSFORMER | RIFL | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
PARA-RIFL-230.0-1 | 5205 | PARACHUTE SUBSTATION | XCEL | RIFLE 230KV SUBSTATION (PSCO) | XCEL | 70309 | 70358 | Xcel Owned | 5205 135Y | CURRENT_TRANSFORMER | RIFL | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
PARA-RIFL-230.0-1 | 5205 | PARACHUTE SUBSTATION | XCEL | RIFLE 230KV SUBSTATION (PSCO) | XCEL | 70309 | 70358 | Xcel Owned | 5205 135X | CURRENT_TRANSFORMER | RIFL | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
PARA-RIFL-230.0-1 | 5205 | PARACHUTE SUBSTATION | XCEL | RIFLE 230KV SUBSTATION (PSCO) | XCEL | 70309 | 70358 | Xcel Owned |  | LINE_TRAP | PARA | 1200 | 1200 | 1248 | 1248 | 478 | 478 | 497 | 497
PARA-RIFL-230.0-1 | 5205 | PARACHUTE SUBSTATION | XCEL | RIFLE 230KV SUBSTATION (PSCO) | XCEL | 70309 | 70358 | Xcel Owned |  | LINE_TRAP | RIFL | 1200 | 1200 | 1248 | 1248 | 478 | 478 | 497 | 497
HOPK-RIFL-230.0-1 | 5207 | HOPKINS SUBSTATION | XCEL | RIFLE 230KV SUBSTATION (PSCO) | XCEL | 70232 | 70358 | Xcel Owned | HOPK-RIFL-230.0-1 | FACILITY |  | 1085 | 1200 | 1200 | 1200 | 432 | 478 | 478 | 478
HOPK-RIFL-230.0-1 | 5207 | HOPKINS SUBSTATION | XCEL | RIFLE 230KV SUBSTATION (PSCO) | XCEL | 70232 | 70358 | Xcel Owned | Curlew | BUSBAR_SECTION | RIFL | 1085 | 1265 | 1296 | 1441 | 432 | 504 | 516 | 574
HOPK-RIFL-230.0-1 | 5207 | HOPKINS SUBSTATION | XCEL | RIFLE 230KV SUBSTATION (PSCO) | XCEL | 70232 | 70358 | Xcel Owned | Relay Settings | SECONDARY_CURRENT_LIMITATION | RIFL | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
HAGE_TP-MALT-230.0-1 | 5245 | HAGERMAN PASS TAP | XCEL | MALTA SUBSTATION | XCEL | 2053 | 70274 | Xcel Owned | HAGE_TP-MALT-230.0-1 | FACILITY |  | 1104 | 1214 | 1258 | 1384 | 440 | 484 | 501 | 551
HAGE_TP-MALT-230.0-1 | 5245 | HAGERMAN PASS TAP | XCEL | MALTA SUBSTATION | XCEL | 2053 | 70274 | Xcel Owned | HAGE_TP-MALT-230.0-1 | Transmission Line | 5245 | 1104 | 1214 | 1258 | 1384 | 440 | 484 | 501 | 551
HOPK-HAGE_TP-230.0-1 | 5245 | HOPKINS SUBSTATION | XCEL | HAGERMAN PASS TAP | XCEL | 70232 | 2053 | Xcel Owned | HOPK-HAGE_TP-230.0-1 | FACILITY |  | 1104 | 1214 | 1258 | 1384 | 440 | 484 | 501 | 551
HOPK-HAGE_TP-230.0-1 | 5245 | HOPKINS SUBSTATION | XCEL | HAGERMAN PASS TAP | XCEL | 70232 | 2053 | Xcel Owned | HOPK-HAGE_TP-230.0-1 | Transmission Line | 5245 | 1104 | 1214 | 1258 | 1384 | 440 | 484 | 501 | 551
PLEN-PENG-230.0-1 | 5261 | PLAINS END SWITCHING STATION | XCEL | PLAINS END NUG (PG&E) | XCEL | 70570 | 2100 | Xcel Owned | PLEN-PENG-230.0-1 | FACILITY |  | 800 | 800 | 800 | 800 | 319 | 319 | 319 | 319
PLEN-PENG-230.0-1 | 5261 | PLAINS END SWITCHING STATION | XCEL | PLAINS END NUG (PG&E) | XCEL | 70570 | 2100 | Xcel Owned | 5261 METER, JEM 10 | SECONDARY_CURRENT_LIMITATION | PENG | 800 | 800 | 800 | 800 | 319 | 319 | 319 | 319
PLEN-PENG-230.0-1 | 5261 | PLAINS END SWITCHING STATION | XCEL | PLAINS END NUG (PG&E) | XCEL | 70570 | 2100 | Xcel Owned | 230 BUS MU C | CURRENT_TRANSFORMER | PENG | 800 | 800 | 800 | 800 | 319 | 319 | 319 | 319
PLEN-PENG-230.0-1 | 5261 | PLAINS END SWITCHING STATION | XCEL | PLAINS END NUG (PG&E) | XCEL | 70570 | 2100 | Xcel Owned | 5261 PK2 | SECONDARY_CURRENT_LIMITATION | PENG | 800 | 800 | 800 | 800 | 319 | 319 | 319 | 319
PLEN-PENG-230.0-1 | 5261 | PLAINS END SWITCHING STATION | XCEL | PLAINS END NUG (PG&E) | XCEL | 70570 | 2100 | Xcel Owned | 230 BUS MU B | CURRENT_TRANSFORMER | PENG | 800 | 800 | 800 | 800 | 319 | 319 | 319 | 319
PLEN-PENG-230.0-1 | 5261 | PLAINS END SWITCHING STATION | XCEL | PLAINS END NUG (PG&E) | XCEL | 70570 | 2100 | Xcel Owned | 230 BUS MU A | CURRENT_TRANSFORMER | PENG | 800 | 800 | 800 | 800 | 319 | 319 | 319 | 319
PLEN-PENG-230.0-1 | 5261 | PLAINS END SWITCHING STATION | XCEL | PLAINS END NUG (PG&E) | XCEL | 70570 | 2100 | Xcel Owned | 5261 W/VAR XDCR | SECONDARY_CURRENT_LIMITATION | PENG | 800 | 800 | 800 | 800 | 319 | 319 | 319 | 319
BEAV-STOR-230.0-1 | 5265 | BEAVER CREEK EAST SUBSTATION | XCEL | STORY SUBSTATION | XCEL | 70399 | 73192 | Xcel Owned | BEAV-STOR-230.0-1 | FACILITY |  | 693 | 693 | 693 | 693 | 276 | 276 | 276 | 276
BEAV-STOR-230.0-1 | 5265 | BEAVER CREEK EAST SUBSTATION | XCEL | STORY SUBSTATION | XCEL | 70399 | 73192 | Xcel Owned | Foreign Ratings | Foreign Ratings | STOR | 693 | 693 | 693 | 693 | 276 | 276 | 276 | 276
PLEN-PCOG-230.0-1 | 5267 | PLAINS END SWITCHING STATION | XCEL | PLAINS END COGENTRIX NUG | XCEL | 70570 | 2099 | Xcel Owned | PLEN-PCOG-230.0-1 | FACILITY |  | 400 | 400 | 400 | 400 | 159 | 159 | 159 | 159
PLEN-PCOG-230.0-1 | 5267 | PLAINS END SWITCHING STATION | XCEL | PLAINS END COGENTRIX NUG | XCEL | 70570 | 2099 | Xcel Owned | Foreign Ratings | Foreign Ratings | PCOG | 400 | 400 | 400 | 400 | 159 | 159 | 159 | 159
GRVL-SPRU-230.0-1 | 5270 | GREEN VALLEY SUBSTATION | XCEL | SPRUCE SUBSTATION | XCEL | 70048 | 70528 | Xcel Owned | GRVL-SPRU-230.0-1 | FACILITY |  | 1800 | 1800 | 1800 | 1800 | 717 | 717 | 717 | 717
GRVL-SPRU-230.0-1 | 5270 | GREEN VALLEY SUBSTATION | XCEL | SPRUCE SUBSTATION | XCEL | 70048 | 70528 | Xcel Owned | TL5270 AMP XDCR | SECONDARY_CURRENT_LIMITATION | GRVL | 1800 | 1800 | 1800 | 1800 | 717 | 717 | 717 | 717
GRVL-SPRU-230.0-1 | 5270 | GREEN VALLEY SUBSTATION | XCEL | SPRUCE SUBSTATION | XCEL | 70048 | 70528 | Xcel Owned | 5270 AMP XDCR | SECONDARY_CURRENT_LIMITATION | SPRU | 1800 | 1800 | 1800 | 1800 | 717 | 717 | 717 | 717
GRVL-RMEC-230.0-1 | 5271 | GREEN VALLEY SUBSTATION | XCEL | ROCKY MOUNTAIN ENERGY CENTER | XCEL | 70048 | 70590 | Xcel Owned | GRVL-RMEC-230.0-1 | FACILITY |  | 1800 | 1800 | 1800 | 1800 | 717 | 717 | 717 | 717
GRVL-RMEC-230.0-1 | 5271 | GREEN VALLEY SUBSTATION | XCEL | ROCKY MOUNTAIN ENERGY CENTER | XCEL | 70048 | 70590 | Xcel Owned | TL5271 AMP XDCR | SECONDARY_CURRENT_LIMITATION | GRVL | 1800 | 1800 | 1800 | 1800 | 717 | 717 | 717 | 717
GRVL-SKYR-230.0-1 | 5275 | GREEN VALLEY SUBSTATION | XCEL | SKY RANCH SUBSTATION | XCEL | 70048 | 70392 | Xcel Owned | GRVL-SKYR-230.0-1 | FACILITY |  | 1215 | 1393 | 1442 | 1587 | 484 | 555 | 574 | 632
GRVL-SKYR-230.0-1 | 5275 | GREEN VALLEY SUBSTATION | XCEL | SKY RANCH SUBSTATION | XCEL | 70048 | 70392 | Xcel Owned | Narcissus | BUSBAR_SECTION | SKYR | 1215 | 1422 | 1452 | 1621 | 484 | 566 | 578 | 646
GRVL-SKYR-230.0-1 | 5275 | GREEN VALLEY SUBSTATION | XCEL | SKY RANCH SUBSTATION | XCEL | 70048 | 70392 | Xcel Owned | GRVL-SKYR-230.0-1 | Transmission Line | 5275 | 1266 | 1393 | 1442 | 1587 | 504 | 555 | 574 | 632
GRVL-IMBO-230.0-1 | 5277 | GREEN VALLEY SUBSTATION | XCEL | IMBODEN SUBSTATION | XCEL | 70048 | 70526 | Xcel Owned | GRVL-IMBO-230.0-1 | FACILITY |  | 1423 | 1565 | 1622 | 1784 | 567 | 624 | 646 | 711
GRVL-IMBO-230.0-1 | 5277 | GREEN VALLEY SUBSTATION | XCEL | IMBODEN SUBSTATION | XCEL | 70048 | 70526 | Xcel Owned | Narcissus | BUSBAR_SECTION | IMBO | 1423 | 1565 | 1622 | 1784 | 567 | 624 | 646 | 711
GRVL-KEEN-230.0-1 | 5279 | GREEN VALLEY SUBSTATION | XCEL | KEENESBURG SUBSTATION | XCEL | 70048 | 70820 | Xcel Owned | GRVL-KEEN-230.0-1 | FACILITY |  | 1800 | 1800 | 1800 | 1800 | 717 | 717 | 717 | 717
GRVL-KEEN-230.0-1 | 5279 | GREEN VALLEY SUBSTATION | XCEL | KEENESBURG SUBSTATION | XCEL | 70048 | 70820 | Xcel Owned | TL5279 AMP XDCR | SECONDARY_CURRENT_LIMITATION | GRVL | 1800 | 1800 | 1800 | 1800 | 717 | 717 | 717 | 717
LEET-SULL-230.0-1 | 5281 | LEETSDALE SUBSTATION | XCEL | SULLIVAN SUBSTATION | XCEL | 70260 | 70417 | Xcel Owned | LEET-SULL-230.0-1 | FACILITY |  | 995 | 1095 | 1180 | 1298 | 396 | 436 | 470 | 517
LEET-SULL-230.0-1 | 5281 | LEETSDALE SUBSTATION | XCEL | SULLIVAN SUBSTATION | XCEL | 70260 | 70417 | Xcel Owned | LEET-SULL-230.0-1 | Transmission Line | 5281 | 995 | 1095 | 1180 | 1298 | 396 | 436 | 470 | 517
ELAT-MONR-230.0-1 | 5283 | ELATI SUBSTATION | XCEL | MONROE SUBSTATION | XCEL | 70163 | 70291 | Xcel Owned | ELAT-MONR-230.0-1 | FACILITY |  | 1000 | 1100 | 1000 | 1100 | 398 | 438 | 398 | 438
ELAT-MONR-230.0-1 | 5283 | ELATI SUBSTATION | XCEL | MONROE SUBSTATION | XCEL | 70163 | 70291 | Xcel Owned | ELAT-MONR-230.0-1 | Transmission Line | 5283 | 1000 | 1100 | 1000 | 1100 | 398 | 438 | 398 | 438
LEET-MONR-230.0-1 | 5283 | LEETSDALE SUBSTATION | XCEL | MONROE SUBSTATION | XCEL | 70260 | 70291 | Xcel Owned | LEET-MONR-230.0-1 | FACILITY |  | 1000 | 1100 | 1000 | 1100 | 398 | 438 | 398 | 438
LEET-MONR-230.0-1 | 5283 | LEETSDALE SUBSTATION | XCEL | MONROE SUBSTATION | XCEL | 70260 | 70291 | Xcel Owned | LEET-MONR-230.0-1 | Transmission Line | 5283 | 1000 | 1100 | 1000 | 1100 | 398 | 438 | 398 | 438
BUCK-SMOK-230.0-1 | 5285 | BUCKLEY SUBSTATION | XCEL | SMOKY HILL SUBSTATION | XCEL | 70067 | 70396 | Xcel Owned | BUCK-SMOK-230.0-1 | FACILITY |  | 1270 | 1397 | 1440 | 1440 | 506 | 557 | 574 | 574
BUCK-SMOK-230.0-1 | 5285 | BUCKLEY SUBSTATION | XCEL | SMOKY HILL SUBSTATION | XCEL | 70067 | 70396 | Xcel Owned | BUCK-SMOK-230.0-1 | Transmission Line | 5285 | 1270 | 1397 | 1447 | 1592 | 506 | 557 | 576 | 634
BUCK-SMOK-230.0-1 | 5285 | BUCKLEY SUBSTATION | XCEL | SMOKY HILL SUBSTATION | XCEL | 70067 | 70396 | Xcel Owned | TL5285 CNP11A 67GP | SECONDARY_CURRENT_LIMITATION | SMOK | 1440 | 1440 | 1440 | 1440 | 574 | 574 | 574 | 574
BUCK-TOLL-230.0-1 | 5285 | BUCKLEY SUBSTATION | XCEL | TOLLGATE SUBSTATION | XCEL | 70046 | 70491 | Xcel Owned | BUCK-TOLL-230.0-1 | FACILITY |  | 1214 | 1397 | 1447 | 1592 | 484 | 557 | 576 | 634
BUCK-TOLL-230.0-1 | 5285 | BUCKLEY SUBSTATION | XCEL | TOLLGATE SUBSTATION | XCEL | 70046 | 70491 | Xcel Owned | Narcissus | BUSBAR_SECTION | TOLL | 1214 | 1421 | 1450 | 1619 | 484 | 566 | 578 | 645
BUCK-TOLL-230.0-1 | 5285 | BUCKLEY SUBSTATION | XCEL | TOLLGATE SUBSTATION | XCEL | 70046 | 70491 | Xcel Owned | BUCK-TOLL-230.0-1 | Transmission Line | 5285 | 1270 | 1397 | 1447 | 1592 | 506 | 557 | 576 | 634
JEWE-LEET-230.0-1 | 5285 | JEWELL SUBSTATION | XCEL | LEETSDALE SUBSTATION | XCEL | 70239 | 70260 | Xcel Owned | JEWE-LEET-230.0-1 | FACILITY |  | 1266 | 1393 | 1440 | 1440 | 504 | 555 | 574 | 574
JEWE-LEET-230.0-1 | 5285 | JEWELL SUBSTATION | XCEL | LEETSDALE SUBSTATION | XCEL | 70239 | 70260 | Xcel Owned | JEWE-LEET-230.0-1 | Transmission Line | 5285 | 1266 | 1393 | 1443 | 1587 | 504 | 555 | 575 | 632
JEWE-LEET-230.0-1 | 5285 | JEWELL SUBSTATION | XCEL | LEETSDALE SUBSTATION | XCEL | 70239 | 70260 | Xcel Owned | 5285_67GP | SECONDARY_CURRENT_LIMITATION | LEET | 1440 | 1440 | 1440 | 1440 | 574 | 574 | 574 | 574
JEWE-TOLL-230.0-1 | 5285 | JEWELL SUBSTATION | XCEL | TOLLGATE SUBSTATION | XCEL | 70239 | 70491 | Xcel Owned | JEWE-TOLL-230.0-1 | FACILITY |  | 1214 | 1389 | 1416 | 1558 | 484 | 553 | 564 | 621
JEWE-TOLL-230.0-1 | 5285 | JEWELL SUBSTATION | XCEL | TOLLGATE SUBSTATION | XCEL | 70239 | 70491 | Xcel Owned | Narcissus | BUSBAR_SECTION | TOLL | 1214 | 1421 | 1450 | 1619 | 484 | 566 | 578 | 645
JEWE-TOLL-230.0-1 | 5285 | JEWELL SUBSTATION | XCEL | TOLLGATE SUBSTATION | XCEL | 70239 | 70491 | Xcel Owned | JEWE-TOLL-230.0-1 | Transmission Line | 5285 | 1263 | 1389 | 1416 | 1558 | 503 | 553 | 564 | 621
FSVR-ISAB-230.0-1 | 5307 | FORT SAINT VRAIN SWITCHYARD | XCEL | ISABELLE SUBSTATION | XCEL | 70410 | 70544 | Xcel Owned | FSVR-ISAB-230.0-1 | FACILITY |  | 1318 | 1450 | 1486 | 1635 | 525 | 578 | 592 | 651
FSVR-ISAB-230.0-1 | 5307 | FORT SAINT VRAIN SWITCHYARD | XCEL | ISABELLE SUBSTATION | XCEL | 70410 | 70544 | Xcel Owned | FSVR-ISAB-230.0-1 | Transmission Line | 5307 | 1318 | 1450 | 1486 | 1635 | 525 | 578 | 592 | 651
CHER-RIVE-230.0-1 | 5309 | CHEROKEE SWITCHYARD SUBSTATION | XCEL | RIVERDALE SUBSTATION | XCEL | 70107 | 70362 | Xcel Owned | CHER-RIVE-230.0-1 | FACILITY |  | 1271 | 1398 | 1448 | 1593 | 506 | 557 | 577 | 635
CHER-RIVE-230.0-1 | 5309 | CHEROKEE SWITCHYARD SUBSTATION | XCEL | RIVERDALE SUBSTATION | XCEL | 70107 | 70362 | Xcel Owned | CHER-RIVE-230.0-1 | Transmission Line | 5309 | 1271 | 1398 | 1448 | 1593 | 506 | 557 | 577 | 635
RIVE-HNLK-230.0-1 | 5309 | RIVERDALE SUBSTATION | XCEL | HENRY LAKE (Tri State) | FOREIGN | 70362 | 70605 | Xcel Owned | RIVE-HNLK-230.0-1 | FACILITY |  | 1270 | 1397 | 1447 | 1592 | 506 | 557 | 576 | 634
RIVE-HNLK-230.0-1 | 5309 | RIVERDALE SUBSTATION | XCEL | HENRY LAKE (Tri State) | FOREIGN | 70362 | 70605 | Xcel Owned | RIVE-HNLK-230.0-1 | Transmission Line | 5309 | 1270 | 1397 | 1447 | 1592 | 506 | 557 | 576 | 634
FLUP-FSVR-230.0-1 | 5311 | FORT LUPTON SUBSTATION | XCEL | FORT SAINT VRAIN SWITCHYARD | XCEL | 70192 | 70410 | Xcel Owned | FLUP-FSVR-230.0-1 | FACILITY |  | 1276 | 1404 | 1440 | 1440 | 509 | 559 | 574 | 574
FLUP-FSVR-230.0-1 | 5311 | FORT LUPTON SUBSTATION | XCEL | FORT SAINT VRAIN SWITCHYARD | XCEL | 70192 | 70410 | Xcel Owned | Ortolan | BUSBAR_SECTION | FSVR | 1276 | 1404 | 1454 | 1599 | 509 | 559 | 579 | 637
FLUP-FSVR-230.0-1 | 5311 | FORT LUPTON SUBSTATION | XCEL | FORT SAINT VRAIN SWITCHYARD | XCEL | 70192 | 70410 | Xcel Owned | 5311_67GP | SECONDARY_CURRENT_LIMITATION | FLUP | 1440 | 1440 | 1440 | 1440 | 574 | 574 | 574 | 574
FSVR-WIND-230.0-1 | 5313 | FORT SAINT VRAIN SWITCHYARD | XCEL | WINDSOR SUBSTATION | XCEL | 70410 | 70474 | Jointly Owned | FSVR-WIND-230.0-1 | FACILITY |  | 1433 | 1576 | 1632 | 1796 | 571 | 628 | 650 | 715
FSVR-WIND-230.0-1 | 5313 | FORT SAINT VRAIN SWITCHYARD | XCEL | WINDSOR SUBSTATION | XCEL | 70410 | 70474 | Jointly Owned | Narcissus | BUSBAR_SECTION | FSVR | 1433 | 1576 | 1632 | 1796 | 571 | 628 | 650 | 715
WIND-WALT-230.0-1 | 5313 | WINDSOR SUBSTATION | XCEL | Ault WAPA | FOREIGN | 70474 | 73011 | Xcel Owned | WIND-WALT-230.0-1 | FACILITY |  | 1445 | 1590 | 1592 | 1592 | 576 | 633 | 634 | 634
WIND-WALT-230.0-1 | 5313 | WINDSOR SUBSTATION | XCEL | Ault WAPA | FOREIGN | 70474 | 73011 | Xcel Owned | WIND-WALT-230.0-1 | Transmission Line | 5313 | 1445 | 1590 | 1648 | 1813 | 576 | 633 | 657 | 722
WIND-WALT-230.0-1 | 5313 | WINDSOR SUBSTATION | XCEL | Ault WAPA | FOREIGN | 70474 | 73011 | Xcel Owned | Foreign Ratings | Foreign Ratings | 5313 | 1592 | 1592 | 1592 | 1592 | 634 | 634 | 634 | 634
FSVR-WELD-230.0-1 | 5315 | FORT SAINT VRAIN SWITCHYARD | XCEL | WELD SUBSTATION | XCEL | 70410 | 70471 | Xcel Owned | FSVR-WELD-230.0-1 | FACILITY |  | 1433 | 1440 | 1440 | 1440 | 571 | 574 | 574 | 574
FSVR-WELD-230.0-1 | 5315 | FORT SAINT VRAIN SWITCHYARD | XCEL | WELD SUBSTATION | XCEL | 70410 | 70471 | Xcel Owned | Narcissus | BUSBAR_SECTION | FSVR | 1433 | 1576 | 1632 | 1796 | 571 | 628 | 650 | 715
FSVR-WELD-230.0-1 | 5315 | FORT SAINT VRAIN SWITCHYARD | XCEL | WELD SUBSTATION | XCEL | 70410 | 70471 | Xcel Owned | 5315_67GS_230KV | SECONDARY_CURRENT_LIMITATION | WELD | 1440 | 1440 | 1440 | 1440 | 574 | 574 | 574 | 574
FSVR-WELD-230.0-1 | 5315 | FORT SAINT VRAIN SWITCHYARD | XCEL | WELD SUBSTATION | XCEL | 70410 | 70471 | Xcel Owned | 5315_67GP_230KV | SECONDARY_CURRENT_LIMITATION | WELD | 1440 | 1440 | 1440 | 1440 | 574 | 574 | 574 | 574
FSVR-KEEN-230.0-1 | 5327 | FORT SAINT VRAIN SWITCHYARD | XCEL | KEENESBURG SUBSTATION | XCEL | 70410 | 70820 | Xcel Owned | FSVR-KEEN-230.0-1 | FACILITY |  | 1915 | 2273 | 2312 | 2400 | 763 | 906 | 921 | 956
FSVR-KEEN-230.0-1 | 5327 | FORT SAINT VRAIN SWITCHYARD | XCEL | KEENESBURG SUBSTATION | XCEL | 70410 | 70820 | Xcel Owned | 2½" (AL 40) | BUSBAR_SECTION | FSVR | 1915 | 2273 | 2312 | 2603 | 763 | 906 | 921 | 1037
FSVR-KEEN-230.0-1 | 5327 | FORT SAINT VRAIN SWITCHYARD | XCEL | KEENESBURG SUBSTATION | XCEL | 70410 | 70820 | Xcel Owned | TL5327 PK-2-1 | SECONDARY_CURRENT_LIMITATION | FSVR | 2400 | 2400 | 2400 | 2400 | 956 | 956 | 956 | 956
FSVR-KEEN-230.0-1 | 5327 | FORT SAINT VRAIN SWITCHYARD | XCEL | KEENESBURG SUBSTATION | XCEL | 70410 | 70820 | Xcel Owned | TL5327 PK-2-2 | SECONDARY_CURRENT_LIMITATION | FSVR | 2400 | 2400 | 2400 | 2400 | 956 | 956 | 956 | 956
FLUP-FSVR-230.0-2 | 5329 | FORT LUPTON SUBSTATION | XCEL | FORT SAINT VRAIN SWITCHYARD | XCEL | 70192 | 70410 | Xcel Owned | FLUP-FSVR-230.0-2 | FACILITY |  | 1276 | 1404 | 1454 | 1599 | 509 | 559 | 579 | 637
FLUP-FSVR-230.0-2 | 5329 | FORT LUPTON SUBSTATION | XCEL | FORT SAINT VRAIN SWITCHYARD | XCEL | 70192 | 70410 | Xcel Owned | Ortolan | BUSBAR_SECTION | FSVR | 1276 | 1404 | 1454 | 1599 | 509 | 559 | 579 | 637
BOON-MIDW-230.0-1 | 5335 | BOONE SUBSTATION | XCEL | MIDWAY SUBSTATION | XCEL | 70061 | 70286 | Xcel Owned | BOON-MIDW-230.0-1 | FACILITY |  | 1062 | 1062 | 1200 | 1200 | 423 | 423 | 478 | 478
BOON-MIDW-230.0-1 | 5335 | BOONE SUBSTATION | XCEL | MIDWAY SUBSTATION | XCEL | 70061 | 70286 | Xcel Owned | BOON-MIDW-230.0-1 | Transmission Line | 5335 | 1062 | 1062 | 1348 | 1348 | 423 | 423 | 537 | 537
BOON-MIDW-230.0-1 | 5335 | BOONE SUBSTATION | XCEL | MIDWAY SUBSTATION | XCEL | 70061 | 70286 | Xcel Owned | 5335_W_230KV | SECONDARY_CURRENT_LIMITATION | MIDW | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
BOON-MIDW-230.0-1 | 5335 | BOONE SUBSTATION | XCEL | MIDWAY SUBSTATION | XCEL | 70061 | 70286 | Xcel Owned | TL5335METERVAR | SECONDARY_CURRENT_LIMITATION | BOON | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
BOON-MIDW-230.0-1 | 5335 | BOONE SUBSTATION | XCEL | MIDWAY SUBSTATION | XCEL | 70061 | 70286 | Xcel Owned | 5335_VAR_230KV | SECONDARY_CURRENT_LIMITATION | MIDW | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
BOON-LASS-230.0-1 | 5337 | BOONE SUBSTATION | XCEL | LAMAR 345KV SWITCHING STATION | XCEL | 70061 | 70254 | Jointly Owned | BOON-LASS-230.0-1 | FACILITY |  | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
BOON-LASS-230.0-1 | 5337 | BOONE SUBSTATION | XCEL | LAMAR 345KV SWITCHING STATION | XCEL | 70061 | 70254 | Jointly Owned | 230 5337 M A | CURRENT_TRANSFORMER | BOON | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
BOON-LASS-230.0-1 | 5337 | BOONE SUBSTATION | XCEL | LAMAR 345KV SWITCHING STATION | XCEL | 70061 | 70254 | Jointly Owned | 230 5337 M C | CURRENT_TRANSFORMER | BOON | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
BOON-LASS-230.0-1 | 5337 | BOONE SUBSTATION | XCEL | LAMAR 345KV SWITCHING STATION | XCEL | 70061 | 70254 | Jointly Owned | 230 5337 M B | CURRENT_TRANSFORMER | BOON | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
BOON-LASS-230.0-1 | 5337 | BOONE SUBSTATION | XCEL | LAMAR 345KV SWITCHING STATION | XCEL | 70061 | 70254 | Jointly Owned | TL5337METERVAR | SECONDARY_CURRENT_LIMITATION | BOON | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
BREC-DILL-230.0-1 | 5355 | BRECKENRIDGE SUBSTATION | XCEL | DILLON SUBSTATION | XCEL | 70064 | 70156 | Xcel Owned | BREC-DILL-230.0-1 | FACILITY |  | 1964 | 2000 | 2143 | 2208 | 782 | 797 | 854 | 880
BREC-DILL-230.0-1 | 5355 | BRECKENRIDGE SUBSTATION | XCEL | DILLON SUBSTATION | XCEL | 70064 | 70156 | Xcel Owned | BREC-DILL-230.0-1 | Transmission Line | 5355 | 1964 | 2161 | 2143 | 2358 | 782 | 861 | 854 | 939
BREC-DILL-230.0-1 | 5355 | BRECKENRIDGE SUBSTATION | XCEL | DILLON SUBSTATION | XCEL | 70064 | 70156 | Xcel Owned |  | LINE_TRAP | DILL | 2000 | 2000 | 2208 | 2208 | 797 | 797 | 880 | 880
DILL-PTAR-230.0-1 | 5359 | DILLON SUBSTATION | XCEL | PTARMIGAN | XCEL | 70156 | 2102 | Xcel Owned | DILL-PTAR-230.0-1 | FACILITY |  | 1270 | 1397 | 1447 | 1592 | 506 | 557 | 576 | 634
DILL-PTAR-230.0-1 | 5359 | DILLON SUBSTATION | XCEL | PTARMIGAN | XCEL | 70156 | 2102 | Xcel Owned | DILL-PTAR-230.0-1 | Transmission Line | 5359 | 1270 | 1397 | 1447 | 1592 | 506 | 557 | 576 | 634
PTAR-BLUE-230.0-1 | 5367 | PTARMIGAN | XCEL | BLUE RIVER SUBSTATION | XCEL | 2102 | 70053 | Jointly Owned | PTAR-BLUE-230.0-1 | FACILITY |  | 1270 | 1397 | 1447 | 1592 | 506 | 557 | 576 | 634
PTAR-BLUE-230.0-1 | 5367 | PTARMIGAN | XCEL | BLUE RIVER SUBSTATION | XCEL | 2102 | 70053 | Jointly Owned | PTAR-BLUE-230.0-1 | Transmission Line | 5367 | 1270 | 1397 | 1447 | 1592 | 506 | 557 | 576 | 634
VALM-SPIN-230.0-1 | 5385 | VALMONT SWITCHYARD SUBSTATION | XCEL | SPINDLE SUBSTATION | XCEL | 70447 | 70592 | Xcel Owned | VALM-SPIN-230.0-1 | FACILITY |  | 1318 | 1450 | 1486 | 1635 | 525 | 578 | 592 | 651
VALM-SPIN-230.0-1 | 5385 | VALMONT SWITCHYARD SUBSTATION | XCEL | SPINDLE SUBSTATION | XCEL | 70447 | 70592 | Xcel Owned | VALM-SPIN-230.0-1 | Transmission Line | 5385 | 1318 | 1450 | 1486 | 1635 | 525 | 578 | 592 | 651
MNGL-PLEN-230.0-1 | 5389 | MOON GULCH SUBSTATION | XCEL | PLAINS END SWITCHING STATION | XCEL | 70574 | 70570 | Xcel Owned | MNGL-PLEN-230.0-1 | FACILITY |  | 1271 | 1398 | 1435 | 1579 | 506 | 557 | 572 | 629
MNGL-PLEN-230.0-1 | 5389 | MOON GULCH SUBSTATION | XCEL | PLAINS END SWITCHING STATION | XCEL | 70574 | 70570 | Xcel Owned | MNGL-PLEN-230.0-1 | Transmission Line | 5389 | 1271 | 1398 | 1435 | 1579 | 506 | 557 | 572 | 629
MNGL-SIMM-230.0-1 | 5389 | MOON GULCH SUBSTATION | XCEL | SIMMS SUBSTATION | XCEL | 70574 | 70543 | Xcel Owned | MNGL-SIMM-230.0-1 | FACILITY |  | 1261 | 1387 | 1435 | 1579 | 502 | 553 | 572 | 629
MNGL-SIMM-230.0-1 | 5389 | MOON GULCH SUBSTATION | XCEL | SIMMS SUBSTATION | XCEL | 70574 | 70543 | Xcel Owned | MNGL-SIMM-230.0-1 | Transmission Line | 5389 | 1261 | 1387 | 1435 | 1579 | 502 | 553 | 572 | 629
VALM-SIMM-230.0-1 | 5389 | VALMONT SWITCHYARD SUBSTATION | XCEL | SIMMS SUBSTATION | XCEL | 70447 | 70543 | Xcel Owned | VALM-SIMM-230.0-1 | FACILITY |  | 1207 | 1328 | 1395 | 1535 | 481 | 529 | 556 | 612
VALM-SIMM-230.0-1 | 5389 | VALMONT SWITCHYARD SUBSTATION | XCEL | SIMMS SUBSTATION | XCEL | 70447 | 70543 | Xcel Owned | VALM-SIMM-230.0-1 | Transmission Line | 5389 | 1207 | 1328 | 1395 | 1535 | 481 | 529 | 556 | 612
COMA-CALU-230.0-1 | 5408 | COMANCHE SUBSTATION | XCEL | Walsenburg | FOREIGN | 70122 | 70961 | Jointly Owned | COMA-CALU-230.0-1 | FACILITY |  | 900 | 900 | 900 | 900 | 359 | 359 | 359 | 359
COMA-CALU-230.0-1 | 5408 | COMANCHE SUBSTATION | XCEL | Walsenburg | FOREIGN | 70122 | 70961 | Jointly Owned | TL5408XDCRAMP | SECONDARY_CURRENT_LIMITATION | COMA | 900 | 900 | 900 | 900 | 359 | 359 | 359 | 359
COMA-MIDW-230.0-1 | 5411 | COMANCHE SUBSTATION | XCEL | MIDWAY SUBSTATION | XCEL | 70122 | 70286 | Xcel Owned | COMA-MIDW-230.0-1 | FACILITY |  | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
COMA-MIDW-230.0-1 | 5411 | COMANCHE SUBSTATION | XCEL | MIDWAY SUBSTATION | XCEL | 70122 | 70286 | Xcel Owned | 5411_VAR_230KV | SECONDARY_CURRENT_LIMITATION | MIDW | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
COMA-MIDW-230.0-2 | 5413 | COMANCHE SUBSTATION | XCEL | MIDWAY SUBSTATION | XCEL | 70122 | 70286 | Xcel Owned | COMA-MIDW-230.0-2 | FACILITY |  | 1200 | 1366 | 1200 | 1400 | 478 | 544 | 478 | 558
COMA-MIDW-230.0-2 | 5413 | COMANCHE SUBSTATION | XCEL | MIDWAY SUBSTATION | XCEL | 70122 | 70286 | Xcel Owned | COMA-MIDW-230.0-2 | Transmission Line | 5413 | 1242 | 1366 | 1412 | 1546 | 495 | 544 | 563 | 616
COMA-MIDW-230.0-2 | 5413 | COMANCHE SUBSTATION | XCEL | MIDWAY SUBSTATION | XCEL | 70122 | 70286 | Xcel Owned | Foreign Ratings | Foreign Ratings | COMA | 1200 | 1546 | 1200 | 1546 | 478 | 616 | 478 | 616
COMA-MIDW-230.0-2 | 5413 | COMANCHE SUBSTATION | XCEL | MIDWAY SUBSTATION | XCEL | 70122 | 70286 | Xcel Owned | 5413 PKG-S | SECONDARY_CURRENT_LIMITATION | MIDW | 1400 | 1400 | 1400 | 1400 | 558 | 558 | 558 | 558
BOON-COMA-230.0-1 | 5415 | BOONE SUBSTATION | XCEL | COMANCHE SUBSTATION | XCEL | 70061 | 70122 | Xcel Owned | BOON-COMA-230.0-1 | FACILITY |  | 1270 | 1397 | 1447 | 1592 | 506 | 557 | 576 | 634
BOON-COMA-230.0-1 | 5415 | BOONE SUBSTATION | XCEL | COMANCHE SUBSTATION | XCEL | 70061 | 70122 | Xcel Owned | BOON-COMA-230.0-1 | Transmission Line | 5415 | 1270 | 1397 | 1447 | 1592 | 506 | 557 | 576 | 634
CLAR-GREE-230.0-1 | 5435 | CLARK SUBSTATION | XCEL | GREENWOOD SUBSTATION | XCEL | 70112 | 70481 | Xcel Owned | CLAR-GREE-230.0-1 | FACILITY |  | 920 | 1012 | 920 | 1012 | 367 | 403 | 367 | 403
CLAR-GREE-230.0-1 | 5435 | CLARK SUBSTATION | XCEL | GREENWOOD SUBSTATION | XCEL | 70112 | 70481 | Xcel Owned | CLAR-GREE-230.0-1 | Transmission Line | 5435 | 920 | 1012 | 920 | 1012 | 367 | 403 | 367 | 403
CLAR-JORD-230.0-1 | 5435 | CLARK SUBSTATION | XCEL | JORDAN ROAD SUBSTATION | XCEL | 70112 | 70241 | Xcel Owned | CLAR-JORD-230.0-1 | FACILITY |  | 830 | 913 | 830 | 913 | 331 | 364 | 331 | 364
CLAR-JORD-230.0-1 | 5435 | CLARK SUBSTATION | XCEL | JORDAN ROAD SUBSTATION | XCEL | 70112 | 70241 | Xcel Owned | CLAR-JORD-230.0-1 | Transmission Line | 5435 | 830 | 913 | 830 | 913 | 331 | 364 | 331 | 364
PAWN-STOR-230.0-1 | 5455 | PAWNEE 345KV | XCEL | STORY SUBSTATION | XCEL | 70311 | 73192 | Xcel Owned | PAWN-STOR-230.0-1 | FACILITY |  | 1459 | 1478 | 1627 | 1627 | 581 | 589 | 648 | 648
PAWN-STOR-230.0-1 | 5455 | PAWNEE 345KV | XCEL | STORY SUBSTATION | XCEL | 70311 | 73192 | Xcel Owned | PAWN-STOR-230.0-1 | Transmission Line | 5455 | 1459 | 1478 | 1664 | 1812 | 581 | 589 | 663 | 722
PAWN-STOR-230.0-1 | 5455 | PAWNEE 345KV | XCEL | STORY SUBSTATION | XCEL | 70311 | 73192 | Xcel Owned | Foreign Ratings | Foreign Ratings | STOR | 1627 | 1627 | 1627 | 1627 | 648 | 648 | 648 | 648
PAWN-MSST-230.0-1 | 5457 | PAWNEE 345KV | XCEL | MISSILE SITE | XCEL | 70311 | 70623 | Xcel Owned | PAWN-MSST-230.0-1 | FACILITY |  | 1855 | 2000 | 2110 | 2208 | 739 | 797 | 841 | 880
PAWN-MSST-230.0-1 | 5457 | PAWNEE 345KV | XCEL | MISSILE SITE | XCEL | 70311 | 70623 | Xcel Owned | PAWN-MSST-230.0-1 | Transmission Line | 5457 | 1855 | 2041 | 2110 | 2321 | 739 | 813 | 841 | 925
PAWN-MSST-230.0-1 | 5457 | PAWNEE 345KV | XCEL | MISSILE SITE | XCEL | 70311 | 70623 | Xcel Owned |  | LINE_TRAP | PAWN | 2000 | 2000 | 2208 | 2208 | 797 | 797 | 880 | 880
PAWN-MSST-230.0-1 | 5457 | PAWNEE 345KV | XCEL | MISSILE SITE | XCEL | 70311 | 70623 | Xcel Owned |  | LINE_TRAP | MSST | 2000 | 2000 | 2208 | 2208 | 797 | 797 | 880 | 880
PAWN-MANC-230.0-1 | 5461 | PAWNEE 345KV | XCEL | MANCHIEF | XCEL | 70311 | 2021 | Xcel Owned | PAWN-MANC-230.0-1 | FACILITY |  | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
PAWN-MANC-230.0-1 | 5461 | PAWNEE 345KV | XCEL | MANCHIEF | XCEL | 70311 | 2021 | Xcel Owned | L5461 FT-1 | SECONDARY_CURRENT_LIMITATION | MANC | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
PAWN-MANC-230.0-1 | 5461 | PAWNEE 345KV | XCEL | MANCHIEF | XCEL | 70311 | 2021 | Xcel Owned | 230 TL5461 MU A | CURRENT_TRANSFORMER | MANC | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
PAWN-MANC-230.0-1 | 5461 | PAWNEE 345KV | XCEL | MANCHIEF | XCEL | 70311 | 2021 | Xcel Owned | 230 TL5461 MU C | CURRENT_TRANSFORMER | MANC | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
PAWN-MANC-230.0-1 | 5461 | PAWNEE 345KV | XCEL | MANCHIEF | XCEL | 70311 | 2021 | Xcel Owned | 230 TL5461 MU B | CURRENT_TRANSFORMER | MANC | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
PAWN-MANC-230.0-1 | 5461 | PAWNEE 345KV | XCEL | MANCHIEF | XCEL | 70311 | 2021 | Xcel Owned | L5461 W/VAR XDCR | SECONDARY_CURRENT_LIMITATION | MANC | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
PAWN-MANC-230.0-1 | 5461 | PAWNEE 345KV | XCEL | MANCHIEF | XCEL | 70311 | 2021 | Xcel Owned | L5461 PK-2 | SECONDARY_CURRENT_LIMITATION | MANC | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
FLUP-PAWN-230.0-1 | 5463 | FORT LUPTON SUBSTATION | XCEL | PAWNEE 345KV | XCEL | 70192 | 70311 | Xcel Owned | FLUP-PAWN-230.0-1 | FACILITY |  | 1208 | 1329 | 1377 | 1440 | 481 | 529 | 549 | 574
FLUP-PAWN-230.0-1 | 5463 | FORT LUPTON SUBSTATION | XCEL | PAWNEE 345KV | XCEL | 70192 | 70311 | Xcel Owned | FLUP-PAWN-230.0-1 | Transmission Line | 5463 | 1208 | 1329 | 1377 | 1515 | 481 | 529 | 549 | 604
FLUP-PAWN-230.0-1 | 5463 | FORT LUPTON SUBSTATION | XCEL | PAWNEE 345KV | XCEL | 70192 | 70311 | Xcel Owned | TL5463_67GB | SECONDARY_CURRENT_LIMITATION | PAWN | 1440 | 1440 | 1440 | 1440 | 574 | 574 | 574 | 574
FLUP-PAWN-230.0-1 | 5463 | FORT LUPTON SUBSTATION | XCEL | PAWNEE 345KV | XCEL | 70192 | 70311 | Xcel Owned | TL5463_67GP | SECONDARY_CURRENT_LIMITATION | PAWN | 1440 | 1440 | 1440 | 1440 | 574 | 574 | 574 | 574
FLUP-PAWN-230.0-1 | 5463 | FORT LUPTON SUBSTATION | XCEL | PAWNEE 345KV | XCEL | 70192 | 70311 | Xcel Owned | 5463_67GP | SECONDARY_CURRENT_LIMITATION | FLUP | 1440 | 1440 | 1440 | 1440 | 574 | 574 | 574 | 574
PAWN-BRIC-230.0-1 | 5467 | PAWNEE 345KV | XCEL | BRICK CENTER | XCEL | 70311 | 70545 | Xcel Owned | PAWN-BRIC-230.0-1 | FACILITY |  | 1813 | 1813 | 1920 | 1920 | 722 | 722 | 765 | 765
PAWN-BRIC-230.0-1 | 5467 | PAWNEE 345KV | XCEL | BRICK CENTER | XCEL | 70311 | 70545 | Xcel Owned | PAWN-BRIC-230.0-1 | Transmission Line | 5467 | 1813 | 1813 | 2094 | 2094 | 722 | 722 | 834 | 834
PAWN-BRIC-230.0-1 | 5467 | PAWNEE 345KV | XCEL | BRICK CENTER | XCEL | 70311 | 70545 | Xcel Owned | TL5467_50/69S | SECONDARY_CURRENT_LIMITATION | PAWN | 1920 | 1920 | 1920 | 1920 | 765 | 765 | 765 | 765
ALMA-BREC-230.0-1 | 5487 | ALMA SUBSTATION | XCEL | BRECKENRIDGE SUBSTATION | XCEL | 70032 | 70064 | Xcel Owned | ALMA-BREC-230.0-1 | FACILITY |  | 1783 | 2140 | 2101 | 2312 | 710 | 853 | 837 | 921
ALMA-BREC-230.0-1 | 5487 | ALMA SUBSTATION | XCEL | BRECKENRIDGE SUBSTATION | XCEL | 70032 | 70064 | Xcel Owned | 2½" (AL 40) | BUSBAR_SECTION | ALMA | 1783 | 2140 | 2174 | 2462 | 710 | 853 | 866 | 981
ALMA-BREC-230.0-1 | 5487 | ALMA SUBSTATION | XCEL | BRECKENRIDGE SUBSTATION | XCEL | 70032 | 70064 | Xcel Owned | ALMA-BREC-230.0-1 | Transmission Line | 5487 | 1952 | 2147 | 2101 | 2312 | 778 | 855 | 837 | 921
ALMA-MALT-230.0-1 | 5487 | ALMA SUBSTATION | XCEL | MALTA SUBSTATION | XCEL | 70032 | 70274 | Xcel Owned | ALMA-MALT-230.0-1 | FACILITY |  | 1215 | 1336 | 1387 | 1526 | 484 | 532 | 553 | 608
ALMA-MALT-230.0-1 | 5487 | ALMA SUBSTATION | XCEL | MALTA SUBSTATION | XCEL | 70032 | 70274 | Xcel Owned | Curlew | BUSBAR_SECTION | MALT | 1215 | 1336 | 1387 | 1526 | 484 | 532 | 553 | 608
PARA_TP-PARA-230.0-1 | 5503 | PARACHUTE TAP | XCEL | PARACHUTE SUBSTATION | XCEL | 2143 | 70309 | Xcel Owned | PARA_TP-PARA-230.0-1 | FACILITY |  | 1447 | 1591 | 1649 | 1814 | 576 | 634 | 657 | 723
PARA_TP-PARA-230.0-1 | 5503 | PARACHUTE TAP | XCEL | PARACHUTE SUBSTATION | XCEL | 2143 | 70309 | Xcel Owned | PARA_TP-PARA-230.0-1 | Transmission Line | 5503 | 1447 | 1591 | 1649 | 1814 | 576 | 634 | 657 | 723
PARA_TP-PARA-230.0-1 | 5503 | PARACHUTE TAP | XCEL | PARACHUTE SUBSTATION | XCEL | 2143 | 70309 | Xcel Owned | Bittern | BUSBAR_SECTION | PARA | 1447 | 1592 | 1649 | 1814 | 576 | 634 | 657 | 723
PARA_TP-UTER-230.0-1 | 5503 | PARACHUTE TAP | XCEL | RIFLE UTE 230/345KV SUBSTATION | XCEL | 2143 | 79057 | Xcel Owned | PARA_TP-UTER-230.0-1 | FACILITY |  | 1434 | 1578 | 1611 | 1772 | 571 | 629 | 642 | 706
PARA_TP-UTER-230.0-1 | 5503 | PARACHUTE TAP | XCEL | RIFLE UTE 230/345KV SUBSTATION | XCEL | 2143 | 79057 | Xcel Owned | PARA_TP-UTER-230.0-1 | Transmission Line | 5503 | 1434 | 1578 | 1611 | 1772 | 571 | 629 | 642 | 706
CAME-PARA-230.0-1 | 5509 | CAMEO SUBSTATION | XCEL | PARACHUTE SUBSTATION | XCEL | 70078 | 70309 | Xcel Owned | CAME-PARA-230.0-1 | FACILITY | [9 empty] | See Ambient Adjusted Ratings Section
LASS-LAMA-230.0-1 | 5513 | LAMAR 345KV SWITCHING STATION | XCEL | LAMAR (TRI-STATE) | FOREIGN | 70254 | 70560 | Jointly Owned | LASS-LAMA-230.0-1 | FACILITY |  | 600 | 600 | 600 | 600 | 239 | 239 | 239 | 239
LASS-LAMA-230.0-1 | 5513 | LAMAR 345KV SWITCHING STATION | XCEL | LAMAR (TRI-STATE) | FOREIGN | 70254 | 70560 | Jointly Owned | 230 5513 MU C | CURRENT_TRANSFORMER | LASS | 600 | 600 | 600 | 600 | 239 | 239 | 239 | 239
LASS-LAMA-230.0-1 | 5513 | LAMAR 345KV SWITCHING STATION | XCEL | LAMAR (TRI-STATE) | FOREIGN | 70254 | 70560 | Jointly Owned | 230 5513 MU B | CURRENT_TRANSFORMER | LASS | 600 | 600 | 600 | 600 | 239 | 239 | 239 | 239
LASS-LAMA-230.0-1 | 5513 | LAMAR 345KV SWITCHING STATION | XCEL | LAMAR (TRI-STATE) | FOREIGN | 70254 | 70560 | Jointly Owned | 230 5513 MU A | CURRENT_TRANSFORMER | LASS | 600 | 600 | 600 | 600 | 239 | 239 | 239 | 239
GRVL-FLUP-230.0-1 | 5525 | GREEN VALLEY SUBSTATION | XCEL | FORT LUPTON SUBSTATION | XCEL | 70048 | 70192 | Xcel Owned | GRVL-FLUP-230.0-1 | FACILITY |  | 1430 | 1573 | 1629 | 1792 | 570 | 627 | 649 | 714
GRVL-FLUP-230.0-1 | 5525 | GREEN VALLEY SUBSTATION | XCEL | FORT LUPTON SUBSTATION | XCEL | 70048 | 70192 | Xcel Owned | Narcissus | BUSBAR_SECTION | FLUP | 1430 | 1573 | 1629 | 1792 | 570 | 627 | 649 | 714
CHER-GLEN-230.0-1 | 5527 | CHEROKEE SWITCHYARD SUBSTATION | XCEL | GLENN SUBSTATION | XCEL | 70107 | 70200 | Xcel Owned | CHER-GLEN-230.0-1 | FACILITY |  | 1294 | 1520 | 1483 | 1600 | 515 | 605 | 591 | 637
CHER-GLEN-230.0-1 | 5527 | CHEROKEE SWITCHYARD SUBSTATION | XCEL | GLENN SUBSTATION | XCEL | 70107 | 70200 | Xcel Owned | 5770S | SWITCH | GLEN | 1294 | 1520 | 1483 | 1657 | 515 | 605 | 591 | 660
CHER-GLEN-230.0-1 | 5527 | CHEROKEE SWITCHYARD SUBSTATION | XCEL | GLENN SUBSTATION | XCEL | 70107 | 70200 | Xcel Owned | 5770N | SWITCH | GLEN | 1294 | 1520 | 1483 | 1657 | 515 | 605 | 591 | 660
CHER-GLEN-230.0-1 | 5527 | CHEROKEE SWITCHYARD SUBSTATION | XCEL | GLENN SUBSTATION | XCEL | 70107 | 70200 | Xcel Owned | 5527-2 | CIRCUIT_SWITCHER | GLEN | 1600 | 1600 | 1600 | 1600 | 637 | 637 | 637 | 637
GLEN-WASH-230.0-1 | 5527 | GLENN SUBSTATION | XCEL | WASHINGTON SUBSTATION | XCEL | 70200 | 70461 | Xcel Owned | GLEN-WASH-230.0-1 | FACILITY |  | 1218 | 1424 | 1454 | 1600 | 485 | 567 | 579 | 637
GLEN-WASH-230.0-1 | 5527 | GLENN SUBSTATION | XCEL | WASHINGTON SUBSTATION | XCEL | 70200 | 70461 | Xcel Owned | Narcissus | BUSBAR_SECTION | GLEN | 1218 | 1424 | 1454 | 1623 | 485 | 567 | 579 | 647
GLEN-WASH-230.0-1 | 5527 | GLENN SUBSTATION | XCEL | WASHINGTON SUBSTATION | XCEL | 70200 | 70461 | Xcel Owned | 5527-1 | CIRCUIT_SWITCHER | GLEN | 1600 | 1600 | 1600 | 1600 | 637 | 637 | 637 | 637
GLEN-WASH-230.0-1 | 5527 | GLENN SUBSTATION | XCEL | WASHINGTON SUBSTATION | XCEL | 70200 | 70461 | Xcel Owned | 5527-4 | CIRCUIT_SWITCHER | WASH | 1600 | 1600 | 1600 | 1600 | 637 | 637 | 637 | 637
WASH-JLGR-230.0-1 | 5527 | WASHINGTON SUBSTATION | XCEL | J. L. Green | FOREIGN | 70461 | 70529 | Xcel Owned | WASH-JLGR-230.0-1 | FACILITY |  | 1427 | 1570 | 1599 | 1600 | 569 | 625 | 637 | 637
WASH-JLGR-230.0-1 | 5527 | WASHINGTON SUBSTATION | XCEL | J. L. Green | FOREIGN | 70461 | 70529 | Xcel Owned | Narcissus | BUSBAR_SECTION | WASH | 1427 | 1570 | 1626 | 1789 | 569 | 625 | 648 | 713
WASH-JLGR-230.0-1 | 5527 | WASHINGTON SUBSTATION | XCEL | J. L. Green | FOREIGN | 70461 | 70529 | Xcel Owned | Foreign Ratings | Foreign Ratings | JLGR | 1599 | 1627 | 1599 | 1627 | 637 | 648 | 637 | 648
WASH-JLGR-230.0-1 | 5527 | WASHINGTON SUBSTATION | XCEL | J. L. Green | FOREIGN | 70461 | 70529 | Xcel Owned | 5527-3 | CIRCUIT_SWITCHER | WASH | 1600 | 1600 | 1600 | 1600 | 637 | 637 | 637 | 637
FLUP-TCTI-230.0-1 | 5529 | FORT LUPTON SUBSTATION | XCEL | J.M. SHAFER GENERATING STATION | XCEL | 70192 | 2012 | Xcel Owned | FLUP-TCTI-230.0-1 | FACILITY |  | 1185 | 1185 | 1185 | 1185 | 472 | 472 | 472 | 472
FLUP-TCTI-230.0-1 | 5529 | FORT LUPTON SUBSTATION | XCEL | J.M. SHAFER GENERATING STATION | XCEL | 70192 | 2012 | Xcel Owned | Foreign Ratings | Foreign Ratings | TCTI | 1185 | 1185 | 1185 | 1185 | 472 | 472 | 472 | 472
ADOB-UINT-230.0-1 | 5555 | ADOBE SUBSTATION | XCEL | UINTAH SUBSTATION | XCEL | 70268 | 70438 | Xcel Owned | ADOB-UINT-230.0-1 | FACILITY |  | 800 | 800 | 800 | 800 | 319 | 319 | 319 | 319
ADOB-UINT-230.0-1 | 5555 | ADOBE SUBSTATION | XCEL | UINTAH SUBSTATION | XCEL | 70268 | 70438 | Xcel Owned | ADOB-UINT-230.0-1 | Transmission Line | 5555 | 800 | 800 | 800 | 800 | 319 | 319 | 319 | 319 | Railroad Documentation
GJCT-HORI-230.0-1 | 5555 | GRAND JUNCTION SUBSTATION (PSCO) | XCEL | HORIZON SUBSTATION | XCEL | 70206 | 70233 | Xcel Owned | GJCT-HORI-230.0-1 | FACILITY |  | 1229 | 1436 | 1468 | 1600 | 489 | 572 | 585 | 637
GJCT-HORI-230.0-1 | 5555 | GRAND JUNCTION SUBSTATION (PSCO) | XCEL | HORIZON SUBSTATION | XCEL | 70206 | 70233 | Xcel Owned | Narcissus | BUSBAR_SECTION | GJCT | 1229 | 1436 | 1468 | 1635 | 489 | 572 | 585 | 651
GJCT-HORI-230.0-1 | 5555 | GRAND JUNCTION SUBSTATION (PSCO) | XCEL | HORIZON SUBSTATION | XCEL | 70206 | 70233 | Xcel Owned | Narcissus | BUSBAR_SECTION | HORI | 1229 | 1436 | 1468 | 1635 | 489 | 572 | 585 | 651
GJCT-HORI-230.0-1 | 5555 | GRAND JUNCTION SUBSTATION (PSCO) | XCEL | HORIZON SUBSTATION | XCEL | 70206 | 70233 | Xcel Owned | 5555-1 | CIRCUIT_SWITCHER | HORI | 1600 | 1600 | 1600 | 1600 | 637 | 637 | 637 | 637
HORI-ADOB-230.0-1 | 5555 | HORIZON SUBSTATION | XCEL | ADOBE SUBSTATION | XCEL | 70233 | 70268 | Xcel Owned | HORI-ADOB-230.0-1 | FACILITY |  | 800 | 800 | 800 | 800 | 319 | 319 | 319 | 319
HORI-ADOB-230.0-1 | 5555 | HORIZON SUBSTATION | XCEL | ADOBE SUBSTATION | XCEL | 70233 | 70268 | Xcel Owned | HORI-ADOB-230.0-1 | Transmission Line | 5555 | 800 | 800 | 800 | 800 | 319 | 319 | 319 | 319
CLIF-GJCT-230.0-1 | 5557 | CLIFTON SUBSTATION | XCEL | GRAND JUNCTION SUBSTATION (PSCO) | XCEL | 70113 | 70206 | Xcel Owned | CLIF-GJCT-230.0-1 | FACILITY |  | 1227 | 1435 | 1466 | 1600 | 489 | 571 | 584 | 637
CLIF-GJCT-230.0-1 | 5557 | CLIFTON SUBSTATION | XCEL | GRAND JUNCTION SUBSTATION (PSCO) | XCEL | 70113 | 70206 | Xcel Owned | Narcissus | BUSBAR_SECTION | CLIF | 1227 | 1435 | 1466 | 1634 | 489 | 571 | 584 | 651
CLIF-GJCT-230.0-1 | 5557 | CLIFTON SUBSTATION | XCEL | GRAND JUNCTION SUBSTATION (PSCO) | XCEL | 70113 | 70206 | Xcel Owned | 5557_87LP | SECONDARY_CURRENT_LIMITATION | GJCT | 1600 | 1600 | 1600 | 1600 | 637 | 637 | 637 | 637
CLIF-GJCT-230.0-1 | 5557 | CLIFTON SUBSTATION | XCEL | GRAND JUNCTION SUBSTATION (PSCO) | XCEL | 70113 | 70206 | Xcel Owned | 5557 246Y | CURRENT_TRANSFORMER | GJCT | 1600 | 1600 | 1600 | 1600 | 637 | 637 | 637 | 637
CLIF-GJCT-230.0-1 | 5557 | CLIFTON SUBSTATION | XCEL | GRAND JUNCTION SUBSTATION (PSCO) | XCEL | 70113 | 70206 | Xcel Owned | 5557 PK | SECONDARY_CURRENT_LIMITATION | GJCT | 1600 | 1600 | 1600 | 1600 | 637 | 637 | 637 | 637
CLIF-GJCT-230.0-1 | 5557 | CLIFTON SUBSTATION | XCEL | GRAND JUNCTION SUBSTATION (PSCO) | XCEL | 70113 | 70206 | Xcel Owned | 5557-1 | CIRCUIT_SWITCHER | CLIF | 1600 | 1600 | 1600 | 1600 | 637 | 637 | 637 | 637
CLIF-GJCT-230.0-1 | 5557 | CLIFTON SUBSTATION | XCEL | GRAND JUNCTION SUBSTATION (PSCO) | XCEL | 70113 | 70206 | Xcel Owned | 5557 246X | CURRENT_TRANSFORMER | GJCT | 1600 | 1600 | 1600 | 1600 | 637 | 637 | 637 | 637
CLIF-UTEG-230.0-1 | 5557 | CLIFTON SUBSTATION | XCEL | UTE GRAND JUNCTION SUBSTATION | XCEL | 70113 | 70205 | Xcel Owned | CLIF-UTEG-230.0-1 | FACILITY |  | 1200 | 1280 | 1280 | 1280 | 478 | 510 | 510 | 510
CLIF-UTEG-230.0-1 | 5557 | CLIFTON SUBSTATION | XCEL | UTE GRAND JUNCTION SUBSTATION | XCEL | 70113 | 70205 | Xcel Owned | 5557M | SWITCH | UTEG | 1200 | 1549 | 1486 | 1780 | 478 | 617 | 592 | 709
CLIF-UTEG-230.0-1 | 5557 | CLIFTON SUBSTATION | XCEL | UTE GRAND JUNCTION SUBSTATION | XCEL | 70113 | 70205 | Xcel Owned | 5557_230KV_50BF | SECONDARY_CURRENT_LIMITATION | UTEG | 1280 | 1280 | 1280 | 1280 | 510 | 510 | 510 | 510
RMEC-KEEN-230.0-1 | 5565 | ROCKY MOUNTAIN ENERGY CENTER | XCEL | KEENESBURG SUBSTATION | XCEL | 70590 | 70820 | Xcel Owned | RMEC-KEEN-230.0-1 | FACILITY |  | 2000 | 2000 | 2000 | 2000 | 797 | 797 | 797 | 797
RMEC-KEEN-230.0-1 | 5565 | ROCKY MOUNTAIN ENERGY CENTER | XCEL | KEENESBURG SUBSTATION | XCEL | 70590 | 70820 | Xcel Owned | 5565_MU_TS_230KV | SECONDARY_CURRENT_LIMITATION | RMEC | 2000 | 2000 | 2000 | 2000 | 797 | 797 | 797 | 797
RMEC-KEEN-230.0-1 | 5565 | ROCKY MOUNTAIN ENERGY CENTER | XCEL | KEENESBURG SUBSTATION | XCEL | 70590 | 70820 | Xcel Owned | 5565_MU_PK-2_230KV | SECONDARY_CURRENT_LIMITATION | RMEC | 2000 | 2000 | 2000 | 2000 | 797 | 797 | 797 | 797
RMEC-KEEN-230.0-1 | 5565 | ROCKY MOUNTAIN ENERGY CENTER | XCEL | KEENESBURG SUBSTATION | XCEL | 70590 | 70820 | Xcel Owned | 230 5565 MU A | CURRENT_TRANSFORMER | RMEC | 2000 | 2000 | 2000 | 2000 | 797 | 797 | 797 | 797
RMEC-KEEN-230.0-1 | 5565 | ROCKY MOUNTAIN ENERGY CENTER | XCEL | KEENESBURG SUBSTATION | XCEL | 70590 | 70820 | Xcel Owned | 5565_MU_A2_230KV | SECONDARY_CURRENT_LIMITATION | RMEC | 2000 | 2000 | 2000 | 2000 | 797 | 797 | 797 | 797
RMEC-KEEN-230.0-1 | 5565 | ROCKY MOUNTAIN ENERGY CENTER | XCEL | KEENESBURG SUBSTATION | XCEL | 70590 | 70820 | Xcel Owned | 230 5565 MU B | CURRENT_TRANSFORMER | RMEC | 2000 | 2000 | 2000 | 2000 | 797 | 797 | 797 | 797
RMEC-KEEN-230.0-1 | 5565 | ROCKY MOUNTAIN ENERGY CENTER | XCEL | KEENESBURG SUBSTATION | XCEL | 70590 | 70820 | Xcel Owned | 230 5565 MU C | CURRENT_TRANSFORMER | RMEC | 2000 | 2000 | 2000 | 2000 | 797 | 797 | 797 | 797
CAME-UINT-230.0-1 | 5607 | CAMEO SUBSTATION | XCEL | UINTAH SUBSTATION | XCEL | 70078 | 70438 | Xcel Owned | CAME-UINT-230.0-1 | FACILITY |  | 800 | 800 | 800 | 800 | 319 | 319 | 319 | 319
CAME-UINT-230.0-1 | 5607 | CAMEO SUBSTATION | XCEL | UINTAH SUBSTATION | XCEL | 70078 | 70438 | Xcel Owned | CAME-UINT-230.0-1 | Transmission Line | 5607 | 800 | 800 | 800 | 800 | 319 | 319 | 319 | 319 | Railroad Documentation
ARAP-DAKO-230.0-1 | 5623 | ARAPAHOE SUBSTATION | XCEL | DAKOTA SUBSTATION | XCEL | 70038 | 70141 | Xcel Owned | ARAP-DAKO-230.0-1 | FACILITY |  | 1213 | 1241 | 1241 | 1241 | 483 | 494 | 494 | 494
ARAP-DAKO-230.0-1 | 5623 | ARAPAHOE SUBSTATION | XCEL | DAKOTA SUBSTATION | XCEL | 70038 | 70141 | Xcel Owned | ARAP-DAKO-230.0-1 | Transmission Line | 5623 | 1213 | 1241 | 1241 | 1241 | 483 | 494 | 494 | 494
DAKO-DTER-230.0-1 | 5623 | DAKOTA SUBSTATION | XCEL | DENVER TERMINAL SUBSTATION | XCEL | 70141 | 70149 | Xcel Owned | DAKO-DTER-230.0-1 | FACILITY |  | 1188 | 1188 | 1379 | 1379 | 473 | 473 | 549 | 549
DAKO-DTER-230.0-1 | 5623 | DAKOTA SUBSTATION | XCEL | DENVER TERMINAL SUBSTATION | XCEL | 70141 | 70149 | Xcel Owned | DAKO-DTER-230.0-1 | Transmission Line | 5623 | 1188 | 1188 | 1379 | 1379 | 473 | 473 | 549 | 549
DTER-ELAT-230.0-1 | 5625 | DENVER TERMINAL SUBSTATION | XCEL | ELATI SUBSTATION | XCEL | 70149 | 70163 | Xcel Owned | DTER-ELAT-230.0-1 | FACILITY |  | 1091 | 1200 | 1105 | 1200 | 435 | 478 | 440 | 478
DTER-ELAT-230.0-1 | 5625 | DENVER TERMINAL SUBSTATION | XCEL | ELATI SUBSTATION | XCEL | 70149 | 70163 | Xcel Owned | Curlew | BUSBAR_SECTION | DTER | 1091 | 1271 | 1302 | 1448 | 435 | 506 | 519 | 577
DTER-ELAT-230.0-1 | 5625 | DENVER TERMINAL SUBSTATION | XCEL | ELATI SUBSTATION | XCEL | 70149 | 70163 | Xcel Owned | DTER-ELAT-230.0-1 | Transmission Line | 5625 | 1105 | 1216 | 1105 | 1216 | 440 | 484 | 440 | 484
DTER-ELAT-230.0-1 | 5625 | DENVER TERMINAL SUBSTATION | XCEL | ELATI SUBSTATION | XCEL | 70149 | 70163 | Xcel Owned | 5689_PK-2-1_230KV | SECONDARY_CURRENT_LIMITATION | ELAT | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
DTER-ELAT-230.0-1 | 5625 | DENVER TERMINAL SUBSTATION | XCEL | ELATI SUBSTATION | XCEL | 70149 | 70163 | Xcel Owned | 5689 CT1 A | CURRENT_TRANSFORMER | ELAT | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
DTER-ELAT-230.0-1 | 5625 | DENVER TERMINAL SUBSTATION | XCEL | ELATI SUBSTATION | XCEL | 70149 | 70163 | Xcel Owned | 5680_PK-2-1_230KV | SECONDARY_CURRENT_LIMITATION | ELAT | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
DTER-ELAT-230.0-1 | 5625 | DENVER TERMINAL SUBSTATION | XCEL | ELATI SUBSTATION | XCEL | 70149 | 70163 | Xcel Owned | 5625 CT1 B | CURRENT_TRANSFORMER | ELAT | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
DTER-ELAT-230.0-1 | 5625 | DENVER TERMINAL SUBSTATION | XCEL | ELATI SUBSTATION | XCEL | 70149 | 70163 | Xcel Owned | 5625 CT1 C | CURRENT_TRANSFORMER | ELAT | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
DTER-ELAT-230.0-1 | 5625 | DENVER TERMINAL SUBSTATION | XCEL | ELATI SUBSTATION | XCEL | 70149 | 70163 | Xcel Owned | 5680 CT1 C | CURRENT_TRANSFORMER | ELAT | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
DTER-ELAT-230.0-1 | 5625 | DENVER TERMINAL SUBSTATION | XCEL | ELATI SUBSTATION | XCEL | 70149 | 70163 | Xcel Owned | 5689 CT1 B | CURRENT_TRANSFORMER | ELAT | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
DTER-ELAT-230.0-1 | 5625 | DENVER TERMINAL SUBSTATION | XCEL | ELATI SUBSTATION | XCEL | 70149 | 70163 | Xcel Owned | 5625_PK-2-4_230KV | SECONDARY_CURRENT_LIMITATION | ELAT | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
DTER-ELAT-230.0-1 | 5625 | DENVER TERMINAL SUBSTATION | XCEL | ELATI SUBSTATION | XCEL | 70149 | 70163 | Xcel Owned | 5689 CT1 C | CURRENT_TRANSFORMER | ELAT | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
DTER-ELAT-230.0-1 | 5625 | DENVER TERMINAL SUBSTATION | XCEL | ELATI SUBSTATION | XCEL | 70149 | 70163 | Xcel Owned | 5625 CT1 A | CURRENT_TRANSFORMER | ELAT | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
DTER-ELAT-230.0-1 | 5625 | DENVER TERMINAL SUBSTATION | XCEL | ELATI SUBSTATION | XCEL | 70149 | 70163 | Xcel Owned | 5680 CT1 B | CURRENT_TRANSFORMER | ELAT | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
DTER-ELAT-230.0-1 | 5625 | DENVER TERMINAL SUBSTATION | XCEL | ELATI SUBSTATION | XCEL | 70149 | 70163 | Xcel Owned | 5680 CT1 A | CURRENT_TRANSFORMER | ELAT | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
DTER-LACO-230.0-1 | 5627 | DENVER TERMINAL SUBSTATION | XCEL | LACOMBE SUBSTATION | XCEL | 70149 | 70324 | Xcel Owned | DTER-LACO-230.0-1 | FACILITY |  | 1800 | 1800 | 1800 | 1800 | 717 | 717 | 717 | 717
DTER-LACO-230.0-1 | 5627 | DENVER TERMINAL SUBSTATION | XCEL | LACOMBE SUBSTATION | XCEL | 70149 | 70324 | Xcel Owned | TL5627 AMP | SECONDARY_CURRENT_LIMITATION | DTER | 1800 | 1800 | 1800 | 1800 | 717 | 717 | 717 | 717
DTER-WEST-230.0-1 | 5629 | DENVER TERMINAL SUBSTATION | XCEL | WEST SUBSTATION | XCEL | 70149 | 70480 | Xcel Owned | DTER-WEST-230.0-1 | FACILITY |  | 1418 | 1560 | 1600 | 1600 | 565 | 622 | 637 | 637
DTER-WEST-230.0-1 | 5629 | DENVER TERMINAL SUBSTATION | XCEL | WEST SUBSTATION | XCEL | 70149 | 70480 | Xcel Owned | Narcissus | BUSBAR_SECTION | WEST | 1418 | 1560 | 1617 | 1778 | 565 | 622 | 644 | 708
DTER-WEST-230.0-1 | 5629 | DENVER TERMINAL SUBSTATION | XCEL | WEST SUBSTATION | XCEL | 70149 | 70480 | Xcel Owned | 5629-1 | CIRCUIT_SWITCHER | WEST | 1600 | 1600 | 1600 | 1600 | 637 | 637 | 637 | 637
LOOK-WEST-230.0-1 | 5629 | LOOKOUT SUBSTATION | XCEL | WEST SUBSTATION | XCEL | 70266 | 70480 | Xcel Owned | LOOK-WEST-230.0-1 | FACILITY |  | 1016 | 1207 | 1227 | 1247 | 405 | 481 | 489 | 497
LOOK-WEST-230.0-1 | 5629 | LOOKOUT SUBSTATION | XCEL | WEST SUBSTATION | XCEL | 70266 | 70480 | Xcel Owned | Narcissus | BUSBAR_SECTION | WEST | 1016 | 1207 | 1227 | 1382 | 405 | 481 | 489 | 550
LOOK-WEST-230.0-1 | 5629 | LOOKOUT SUBSTATION | XCEL | WEST SUBSTATION | XCEL | 70266 | 70480 | Xcel Owned | LOOK-WEST-230.0-1 | Transmission Line | 5629 | 1247 | 1247 | 1247 | 1247 | 497 | 497 | 497 | 497
LEGG-NIWO-230.0-1 | 5633 | LEGGETT SUBSTATION | XCEL | NIWOT SUBSTATION | XCEL | 70261 | 70297 | Xcel Owned | LEGG-NIWO-230.0-1 | FACILITY |  | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
LEGG-NIWO-230.0-1 | 5633 | LEGGETT SUBSTATION | XCEL | NIWOT SUBSTATION | XCEL | 70261 | 70297 | Xcel Owned | 5633-1 | CIRCUIT_SWITCHER | LEGG | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
LEGG-NIWO-230.0-1 | 5633 | LEGGETT SUBSTATION | XCEL | NIWOT SUBSTATION | XCEL | 70261 | 70297 | Xcel Owned |  | LINE_TRAP | NIWO | 1200 | 1200 | 1325 | 1325 | 478 | 478 | 528 | 528
LEGG-PLEN-230.0-1 | 5633 | LEGGETT SUBSTATION | XCEL | PLAINS END SWITCHING STATION | XCEL | 70261 | 70570 | Xcel Owned | LEGG-PLEN-230.0-1 | FACILITY |  | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
LEGG-PLEN-230.0-1 | 5633 | LEGGETT SUBSTATION | XCEL | PLAINS END SWITCHING STATION | XCEL | 70261 | 70570 | Xcel Owned | 5633-2 | CIRCUIT_SWITCHER | LEGG | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
LEGG-PLEN-230.0-1 | 5633 | LEGGETT SUBSTATION | XCEL | PLAINS END SWITCHING STATION | XCEL | 70261 | 70570 | Xcel Owned |  | LINE_TRAP | PLEN | 1200 | 1200 | 1248 | 1248 | 478 | 478 | 497 | 497
GUNB-NIWO-230.0-1 | 5635 | GUNBARREL SUBSTATION | XCEL | NIWOT SUBSTATION | XCEL | 70213 | 70297 | Xcel Owned | GUNB-NIWO-230.0-1 | FACILITY |  | 793 | 872 | 793 | 872 | 316 | 347 | 316 | 347
GUNB-NIWO-230.0-1 | 5635 | GUNBARREL SUBSTATION | XCEL | NIWOT SUBSTATION | XCEL | 70213 | 70297 | Xcel Owned | GUNB-NIWO-230.0-1 | Transmission Line | 5635 | 793 | 872 | 793 | 872 | 316 | 347 | 316 | 347
NIWO-ISAB-230.0-1 | 5637 | NIWOT SUBSTATION | XCEL | ISABELLE SUBSTATION | XCEL | 70297 | 70544 | Xcel Owned | NIWO-ISAB-230.0-1 | FACILITY |  | 1219 | 1341 | 1456 | 1602 | 486 | 534 | 580 | 638
NIWO-ISAB-230.0-1 | 5637 | NIWOT SUBSTATION | XCEL | ISABELLE SUBSTATION | XCEL | 70297 | 70544 | Xcel Owned | Narcissus | BUSBAR_SECTION | NIWO | 1219 | 1341 | 1456 | 1602 | 486 | 534 | 580 | 638
GUNB-NIWO-230.0-2 | 5639 | GUNBARREL SUBSTATION | XCEL | NIWOT SUBSTATION | XCEL | 70213 | 70297 | Xcel Owned | GUNB-NIWO-230.0-2 | FACILITY |  | 720 | 792 | 720 | 792 | 287 | 316 | 287 | 316
GUNB-NIWO-230.0-2 | 5639 | GUNBARREL SUBSTATION | XCEL | NIWOT SUBSTATION | XCEL | 70213 | 70297 | Xcel Owned | GUNB-NIWO-230.0-2 | Transmission Line | 5639 | 720 | 792 | 720 | 792 | 287 | 316 | 287 | 316
MONA-GREE-230.0-2 | 5705 | MONACO SUBSTATION | XCEL | GREENWOOD SUBSTATION | XCEL | 70212 | 70481 | Xcel Owned | MONA-GREE-230.0-2 | FACILITY |  | 1017 | 1180 | 1180 | 1180 | 405 | 470 | 470 | 470
MONA-GREE-230.0-2 | 5705 | MONACO SUBSTATION | XCEL | GREENWOOD SUBSTATION | XCEL | 70212 | 70481 | Xcel Owned | Narcissus | BUSBAR_SECTION | MONA | 1017 | 1208 | 1228 | 1383 | 405 | 481 | 489 | 551
MONA-GREE-230.0-2 | 5705 | MONACO SUBSTATION | XCEL | GREENWOOD SUBSTATION | XCEL | 70212 | 70481 | Xcel Owned | MONA-GREE-230.0-2 | Transmission Line | 5705 | 1180 | 1180 | 1180 | 1180 | 470 | 470 | 470 | 470
MONA-TECH-230.0-1 | 5705 | MONACO SUBSTATION | XCEL | TECH CENTER SUBSTATION | XCEL | 70212 | 70428 | Xcel Owned | MONA-TECH-230.0-1 | FACILITY |  | 1017 | 1208 | 1180 | 1298 | 405 | 481 | 470 | 517
MONA-TECH-230.0-1 | 5705 | MONACO SUBSTATION | XCEL | TECH CENTER SUBSTATION | XCEL | 70212 | 70428 | Xcel Owned | Narcissus | BUSBAR_SECTION | MONA | 1017 | 1208 | 1228 | 1383 | 405 | 481 | 489 | 551
MONA-TECH-230.0-1 | 5705 | MONACO SUBSTATION | XCEL | TECH CENTER SUBSTATION | XCEL | 70212 | 70428 | Xcel Owned | MONA-TECH-230.0-1 | Transmission Line | 5705 | 1180 | 1298 | 1180 | 1298 | 470 | 517 | 470 | 517
SULL-TECH-230.0-1 | 5705 | SULLIVAN SUBSTATION | XCEL | TECH CENTER SUBSTATION | XCEL | 70417 | 70428 | Xcel Owned | SULL-TECH-230.0-1 | FACILITY |  | 1134 | 1134 | 1334 | 1334 | 452 | 452 | 531 | 531
SULL-TECH-230.0-1 | 5705 | SULLIVAN SUBSTATION | XCEL | TECH CENTER SUBSTATION | XCEL | 70417 | 70428 | Xcel Owned | SULL-TECH-230.0-1 | Transmission Line | 5705 | 1134 | 1134 | 1334 | 1334 | 452 | 452 | 531 | 531
DANI-PRAI-230.0-2 | 5707 | DANIELS PARK 115 & 230KV SUBSTATION | XCEL | PRAIRIE SUBSTATION | XCEL | 70139 | 70331 | Xcel Owned | DANI-PRAI-230.0-2 | FACILITY |  | 1409 | 1550 | 1600 | 1600 | 561 | 618 | 637 | 637
DANI-PRAI-230.0-2 | 5707 | DANIELS PARK 115 & 230KV SUBSTATION | XCEL | PRAIRIE SUBSTATION | XCEL | 70139 | 70331 | Xcel Owned | Narcissus | BUSBAR_SECTION | DANI | 1409 | 1550 | 1607 | 1768 | 561 | 618 | 640 | 704
DANI-PRAI-230.0-2 | 5707 | DANIELS PARK 115 & 230KV SUBSTATION | XCEL | PRAIRIE SUBSTATION | XCEL | 70139 | 70331 | Xcel Owned | 5707-1 | CIRCUIT_SWITCHER | PRAI | 1600 | 1600 | 1600 | 1600 | 637 | 637 | 637 | 637
GREE-PRAI-230.0-1 | 5707 | GREENWOOD SUBSTATION | XCEL | PRAIRIE SUBSTATION | XCEL | 70481 | 70323 | Xcel Owned | GREE-PRAI-230.0-1 | FACILITY |  | 1200 | 1200 | 1248 | 1248 | 478 | 478 | 497 | 497
GREE-PRAI-230.0-1 | 5707 | GREENWOOD SUBSTATION | XCEL | PRAIRIE SUBSTATION | XCEL | 70481 | 70323 | Xcel Owned |  | LINE_TRAP | GREE | 1200 | 1200 | 1248 | 1248 | 478 | 478 | 497 | 497
GREE-MONA-230.0-1 | 5717 | GREENWOOD SUBSTATION | XCEL | MONACO SUBSTATION | XCEL | 70481 | 70212 | Xcel Owned | GREE-MONA-230.0-1 | FACILITY |  | 1017 | 1208 | 1228 | 1383 | 405 | 481 | 489 | 551
GREE-MONA-230.0-1 | 5717 | GREENWOOD SUBSTATION | XCEL | MONACO SUBSTATION | XCEL | 70481 | 70212 | Xcel Owned | Narcissus | BUSBAR_SECTION | MONA | 1017 | 1208 | 1228 | 1383 | 405 | 481 | 489 | 551
MONA-SULL-230.0-1 | 5717 | MONACO SUBSTATION | XCEL | SULLIVAN SUBSTATION | XCEL | 70212 | 70417 | Xcel Owned | MONA-SULL-230.0-1 | FACILITY |  | 995 | 1095 | 1180 | 1298 | 396 | 436 | 470 | 517
MONA-SULL-230.0-1 | 5717 | MONACO SUBSTATION | XCEL | SULLIVAN SUBSTATION | XCEL | 70212 | 70417 | Xcel Owned | MONA-SULL-230.0-1 | Transmission Line | 5717 | 995 | 1095 | 1180 | 1298 | 396 | 436 | 470 | 517
SKYR-SPRU-230.0-1 | 5735 | SKY RANCH SUBSTATION | XCEL | SPRUCE SUBSTATION | XCEL | 70392 | 70528 | Xcel Owned | SKYR-SPRU-230.0-1 | FACILITY |  | 1215 | 1393 | 1443 | 1587 | 484 | 555 | 575 | 632
SKYR-SPRU-230.0-1 | 5735 | SKY RANCH SUBSTATION | XCEL | SPRUCE SUBSTATION | XCEL | 70392 | 70528 | Xcel Owned | Narcissus | BUSBAR_SECTION | SKYR | 1215 | 1422 | 1452 | 1621 | 484 | 566 | 578 | 646
SKYR-SPRU-230.0-1 | 5735 | SKY RANCH SUBSTATION | XCEL | SPRUCE SUBSTATION | XCEL | 70392 | 70528 | Xcel Owned | SKYR-SPRU-230.0-1 | Transmission Line | 5735 | 1266 | 1393 | 1443 | 1587 | 504 | 555 | 575 | 632
PONC-PNCW-230.0-1 | 5747 | PONCHA JUNCTION SUBSTATION | XCEL | Poncha WAPA | FOREIGN | 70393 | 79054 | Xcel Owned | PONC-PNCW-230.0-1 | FACILITY |  | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
PONC-PNCW-230.0-1 | 5747 | PONCHA JUNCTION SUBSTATION | XCEL | Poncha WAPA | FOREIGN | 70393 | 79054 | Xcel Owned | Foreign Ratings | Foreign Ratings | PNCW | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
BARR-GRVL-230.0-1 | 5759 | BARR LAKE SUBSTATION | XCEL | GREEN VALLEY SUBSTATION | XCEL | 70047 | 70048 | Xcel Owned | BARR-GRVL-230.0-1 | FACILITY |  | 1270 | 1397 | 1446 | 1591 | 506 | 557 | 576 | 634
BARR-GRVL-230.0-1 | 5759 | BARR LAKE SUBSTATION | XCEL | GREEN VALLEY SUBSTATION | XCEL | 70047 | 70048 | Xcel Owned | BARR-GRVL-230.0-1 | Transmission Line | 5759 | 1270 | 1397 | 1446 | 1591 | 506 | 557 | 576 | 634
COOL-BASA-230.0-1 | 5787 | COOLEY MESA (HOLY CROSS) | FOREIGN | BASALT SUBSTATION | XCEL | 70535 | 79004 | Xcel Owned | COOL-BASA-230.0-1 | FACILITY |  | 1422 | 1564 | 1600 | 1600 | 566 | 623 | 637 | 637
COOL-BASA-230.0-1 | 5787 | COOLEY MESA (HOLY CROSS) | FOREIGN | BASALT SUBSTATION | XCEL | 70535 | 79004 | Xcel Owned | Bittern | BUSBAR_SECTION | BASA | 1422 | 1564 | 1622 | 1784 | 566 | 623 | 646 | 711
COOL-BASA-230.0-1 | 5787 | COOLEY MESA (HOLY CROSS) | FOREIGN | BASALT SUBSTATION | XCEL | 70535 | 79004 | Xcel Owned | Foreign Ratings | Foreign Ratings | COOL | 1600 | 1600 | 1600 | 1600 | 637 | 637 | 637 | 637
TARR-WATE-230.0-1 | 5803 | TARRYALL SUBSTATION | XCEL | WATERTON SUBSTATION | XCEL | 70427 | 70464 | Xcel Owned | TARR-WATE-230.0-1 | FACILITY |  | 1200 | 1200 | 1325 | 1325 | 478 | 478 | 528 | 528
TARR-WATE-230.0-1 | 5803 | TARRYALL SUBSTATION | XCEL | WATERTON SUBSTATION | XCEL | 70427 | 70464 | Xcel Owned |  | LINE_TRAP | TARR | 1200 | 1200 | 1325 | 1325 | 478 | 478 | 528 | 528
STEA-FOID-230.0-2 | 5811 | STEAMBOAT SUBSTATION | XCEL | FOIDEL CREEK SUBSTATION | XCEL | 79065 | 79091 | Xcel Owned | STEA-FOID-230.0-2 | FACILITY |  | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
STEA-FOID-230.0-2 | 5811 | STEAMBOAT SUBSTATION | XCEL | FOIDEL CREEK SUBSTATION | XCEL | 79065 | 79091 | Xcel Owned | 5811 XDCR AMP | SECONDARY_CURRENT_LIMITATION | STEA | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
STEA-FOID-230.0-2 | 5811 | STEAMBOAT SUBSTATION | XCEL | FOIDEL CREEK SUBSTATION | XCEL | 79065 | 79091 | Xcel Owned | 5811 XDCR WVAR | SECONDARY_CURRENT_LIMITATION | STEA | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
WOLC-FOID-230.0-1 | 5813 | WOLCOTT | FOREIGN | FOIDEL CREEK SUBSTATION | XCEL | 79069 | 79091 | Xcel Owned | WOLC-FOID-230.0-1 | FACILITY |  | 1402 | 1543 | 1599 | 1599 | 559 | 615 | 637 | 637
WOLC-FOID-230.0-1 | 5813 | WOLCOTT | FOREIGN | FOIDEL CREEK SUBSTATION | XCEL | 79069 | 79091 | Xcel Owned | Narcissus | BUSBAR_SECTION | FOID | 1402 | 1543 | 1600 | 1759 | 559 | 615 | 637 | 701
WOLC-FOID-230.0-1 | 5813 | WOLCOTT | FOREIGN | FOIDEL CREEK SUBSTATION | XCEL | 79069 | 79091 | Xcel Owned | Foreign Ratings | Foreign Ratings | WOLC | 1461 | 1599 | 1599 | 1599 | 582 | 637 | 637 | 637
HAYD-FOID-230.0-1 | 5815 | HAYDEN (WAPA) | FOREIGN | FOIDEL CREEK SUBSTATION | XCEL | 79039 | 79091 | Xcel Owned | HAYD-FOID-230.0-1 | FACILITY |  | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
HAYD-FOID-230.0-1 | 5815 | HAYDEN (WAPA) | FOREIGN | FOIDEL CREEK SUBSTATION | XCEL | 79039 | 79091 | Xcel Owned | Foreign Ratings | Foreign Ratings | HAYD | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
STEA-FOID-230.0-1 | 5817 | STEAMBOAT SUBSTATION | XCEL | FOIDEL CREEK SUBSTATION | XCEL | 79065 | 79091 | Xcel Owned | STEA-FOID-230.0-1 | FACILITY |  | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
STEA-FOID-230.0-1 | 5817 | STEAMBOAT SUBSTATION | XCEL | FOIDEL CREEK SUBSTATION | XCEL | 79065 | 79091 | Xcel Owned | 5817 XDCR AMP | SECONDARY_CURRENT_LIMITATION | STEA | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
STEA-FOID-230.0-1 | 5817 | STEAMBOAT SUBSTATION | XCEL | FOIDEL CREEK SUBSTATION | XCEL | 79065 | 79091 | Xcel Owned | 5817 XDCR WVAR | SECONDARY_CURRENT_LIMITATION | STEA | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
CRAT-CRAI-230.0-1 | 5831 | CRAIG TRANSFER | XCEL | CRAIG SW YARD (TRI STATE) | FOREIGN | 79013 | 70009 | Xcel Owned | CRAT-CRAI-230.0-1 | FACILITY |  | 399 | 678 | 399 | 678 | 159 | 270 | 159 | 270
CRAT-CRAI-230.0-1 | 5831 | CRAIG TRANSFER | XCEL | CRAIG SW YARD (TRI STATE) | FOREIGN | 79013 | 70009 | Xcel Owned | Foreign Ratings | Foreign Ratings | CRAI | 399 | 678 | 399 | 678 | 159 | 270 | 159 | 270
SODA-LOOK-230.0-1 | 5851 | SODA LAKES SUBSTATION | XCEL | LOOKOUT SUBSTATION | XCEL | 70018 | 70266 | Xcel Owned | SODA-LOOK-230.0-1 | FACILITY |  | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
SODA-LOOK-230.0-1 | 5851 | SODA LAKES SUBSTATION | XCEL | LOOKOUT SUBSTATION | XCEL | 70018 | 70266 | Xcel Owned | 5851 METER VAR | SECONDARY_CURRENT_LIMITATION | LOOK | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
BARR-REUN-230.0-1 | 5875 | BARR LAKE SUBSTATION | XCEL | Reunion (Tri State) | FOREIGN | 70047 | 70610 | Xcel Owned | BARR-REUN-230.0-1 | FACILITY |  | 1270 | 1397 | 1447 | 1592 | 506 | 557 | 576 | 634
BARR-REUN-230.0-1 | 5875 | BARR LAKE SUBSTATION | XCEL | Reunion (Tri State) | FOREIGN | 70047 | 70610 | Xcel Owned | BARR-REUN-230.0-1 | Transmission Line | 5875 | 1270 | 1397 | 1447 | 1592 | 506 | 557 | 576 | 634
BARR-REUN-230.0-1 | 5875 | BARR LAKE SUBSTATION | XCEL | Reunion (Tri State) | FOREIGN | 70047 | 70610 | Xcel Owned | Ortolan | BUSBAR_SECTION | BARR | 1271 | 1398 | 1447 | 1592 | 506 | 557 | 577 | 634
SISA-REUN-230.0-1 | 5877 | SILVER SADDLE SUBSTATION | XCEL | Reunion (Tri State) | FOREIGN | 70609 | 70610 | Xcel Owned | SISA-REUN-230.0-1 | FACILITY |  | 1627 | 1627 | 1627 | 1627 | 648 | 648 | 648 | 648
SISA-REUN-230.0-1 | 5877 | SILVER SADDLE SUBSTATION | XCEL | Reunion (Tri State) | FOREIGN | 70609 | 70610 | Xcel Owned | Foreign Ratings | Foreign Ratings | REUN | 1627 | 1627 | 1627 | 1627 | 648 | 648 | 648 | 648
NOYM-SPCA-230.0-1 | 5921 | NORTH YUMA | FOREIGN | SPRING CANYON SUBSTATION | XCEL | 73143 | 73579 | Jointly Owned | NOYM-SPCA-230.0-1 | FACILITY |  | 1082 | 1082 | 1082 | 1082 | 431 | 431 | 431 | 431
NOYM-SPCA-230.0-1 | 5921 | NORTH YUMA | FOREIGN | SPRING CANYON SUBSTATION | XCEL | 73143 | 73579 | Jointly Owned | Foreign Ratings | Foreign Ratings | NOYM | 1082 | 1082 | 1082 | 1082 | 431 | 431 | 431 | 431
SPCA-SDNY-230.0-1 | 5925 | SPRING CANYON SUBSTATION | XCEL | Sidney (TSGT) | FOREIGN | 73579 | 2052 | Jointly Owned | SPCA-SDNY-230.0-1 | FACILITY |  | 1110 | 1220 | 1110 | 1220 | 442 | 486 | 442 | 486
SPCA-SDNY-230.0-1 | 5925 | SPRING CANYON SUBSTATION | XCEL | Sidney (TSGT) | FOREIGN | 73579 | 2052 | Jointly Owned | SPCA-SDNY-230.0-1 | Transmission Line | 5925 | 1110 | 1220 | 1110 | 1220 | 442 | 486 | 442 | 486
FSVR-SPIN-230.0-1 | 5953 | FORT SAINT VRAIN SWITCHYARD | XCEL | SPINDLE SUBSTATION | XCEL | 70410 | 70592 | Xcel Owned | FSVR-SPIN-230.0-1 | FACILITY |  | 1270 | 1397 | 1447 | 1592 | 506 | 557 | 576 | 634
FSVR-SPIN-230.0-1 | 5953 | FORT SAINT VRAIN SWITCHYARD | XCEL | SPINDLE SUBSTATION | XCEL | 70410 | 70592 | Xcel Owned | FSVR-SPIN-230.0-1 | Transmission Line | 5953 | 1270 | 1397 | 1447 | 1592 | 506 | 557 | 576 | 634
GRVL-KEEN-230.0-2 | 5961 | GREEN VALLEY SUBSTATION | XCEL | KEENESBURG SUBSTATION | XCEL | 70048 | 70820 | Xcel Owned | GRVL-KEEN-230.0-2 | FACILITY |  | 1800 | 1800 | 1800 | 1800 | 717 | 717 | 717 | 717
GRVL-KEEN-230.0-2 | 5961 | GREEN VALLEY SUBSTATION | XCEL | KEENESBURG SUBSTATION | XCEL | 70048 | 70820 | Xcel Owned | TL5961 AMP XDCR | SECONDARY_CURRENT_LIMITATION | GRVL | 1800 | 1800 | 1800 | 1800 | 717 | 717 | 717 | 717
TARR-HARS-230.0-1 | 5995 | TARRYALL SUBSTATION | XCEL | HARTSEL (IREA) | XCEL | 70427 | 70927 | Xcel Owned | TARR-HARS-230.0-1 | FACILITY |  | 1200 | 1200 | 1325 | 1325 | 478 | 478 | 528 | 528
TARR-HARS-230.0-1 | 5995 | TARRYALL SUBSTATION | XCEL | HARTSEL (IREA) | XCEL | 70427 | 70927 | Xcel Owned |  | LINE_TRAP | TARR | 1200 | 1200 | 1325 | 1325 | 478 | 478 | 528 | 528
TARR-HARS-230.0-1 | 5995 | TARRYALL SUBSTATION | XCEL | HARTSEL (IREA) | XCEL | 70427 | 70927 | Xcel Owned | TARR-HARS-230.0-1 | Transmission Line | 5995 | 1200 | 1320 | 1390 | 1529 | 478 | 526 | 554 | 609
DANI-COMA-345.0-1 | 7015 | DANIELS PARK 115 & 230KV SUBSTATION | XCEL | COMANCHE SUBSTATION | XCEL | 70601 | 70654 | Xcel Owned | DANI-COMA-345.0-1 | FACILITY |  | 2000 | 2000 | 2208 | 2208 | 1195 | 1195 | 1319 | 1319
DANI-COMA-345.0-1 | 7015 | DANIELS PARK 115 & 230KV SUBSTATION | XCEL | COMANCHE SUBSTATION | XCEL | 70601 | 70654 | Xcel Owned |  | LINE_TRAP | DANI | 2000 | 2000 | 2208 | 2208 | 1195 | 1195 | 1319 | 1319
DANI-COMA-345.0-1 | 7015 | DANIELS PARK 115 & 230KV SUBSTATION | XCEL | COMANCHE SUBSTATION | XCEL | 70601 | 70654 | Xcel Owned |  | LINE_TRAP | COMA | 2000 | 2000 | 2208 | 2208 | 1195 | 1195 | 1319 | 1319
DANI-COMA-345.0-2 | 7017 | DANIELS PARK 115 & 230KV SUBSTATION | XCEL | COMANCHE SUBSTATION | XCEL | 70601 | 70654 | Xcel Owned | DANI-COMA-345.0-2 | FACILITY |  | 2000 | 2000 | 2208 | 2208 | 1195 | 1195 | 1319 | 1319
DANI-COMA-345.0-2 | 7017 | DANIELS PARK 115 & 230KV SUBSTATION | XCEL | COMANCHE SUBSTATION | XCEL | 70601 | 70654 | Xcel Owned |  | LINE_TRAP | DANI | 2000 | 2000 | 2208 | 2208 | 1195 | 1195 | 1319 | 1319
DANI-COMA-345.0-2 | 7017 | DANIELS PARK 115 & 230KV SUBSTATION | XCEL | COMANCHE SUBSTATION | XCEL | 70601 | 70654 | Xcel Owned |  | LINE_TRAP | COMA | 2000 | 2000 | 2208 | 2208 | 1195 | 1195 | 1319 | 1319
MIDW-WATE-345.0-1 | 7051 | MIDWAY SUBSTATION | XCEL | WATERTON SUBSTATION | XCEL | 70465 | 70466 | Xcel Owned | MIDW-WATE-345.0-1 | FACILITY |  | 2000 | 2000 | 2208 | 2208 | 1195 | 1195 | 1319 | 1319
MIDW-WATE-345.0-1 | 7051 | MIDWAY SUBSTATION | XCEL | WATERTON SUBSTATION | XCEL | 70465 | 70466 | Xcel Owned |  | LINE_TRAP | WATE | 2000 | 2000 | 2208 | 2208 | 1195 | 1195 | 1319 | 1319
MIDW-WATE-345.0-1 | 7051 | MIDWAY SUBSTATION | XCEL | WATERTON SUBSTATION | XCEL | 70465 | 70466 | Xcel Owned |  | LINE_TRAP | MIDW | 2000 | 2000 | 2208 | 2208 | 1195 | 1195 | 1319 | 1319
HMIL-MSST-345.0-1 | 7081 | HARVEST MILE | XCEL | MISSILE SITE | XCEL | 70597 | 70624 | Xcel Owned | HMIL-MSST-345.0-1 | FACILITY |  | 2821 | 3000 | 3214 | 3312 | 1686 | 1793 | 1921 | 1979
HMIL-MSST-345.0-1 | 7081 | HARVEST MILE | XCEL | MISSILE SITE | XCEL | 70597 | 70624 | Xcel Owned | Narcissus | BUSBAR_SECTION | MSST | 2821 | 3103 | 3214 | 3536 | 1686 | 1854 | 1921 | 2113
HMIL-MSST-345.0-1 | 7081 | HARVEST MILE | XCEL | MISSILE SITE | XCEL | 70597 | 70624 | Xcel Owned |  | LINE_TRAP | MSST | 3000 | 3000 | 3312 | 3312 | 1793 | 1793 | 1979 | 1979
HMIL-SMOK-345.0-1 | 7081 | HARVEST MILE | XCEL | SMOKY HILL SUBSTATION | XCEL | 70597 | 70599 | Xcel Owned | HMIL-SMOK-345.0-1 | FACILITY |  | 2832 | 3000 | 3228 | 3312 | 1692 | 1793 | 1929 | 1979
HMIL-SMOK-345.0-1 | 7081 | HARVEST MILE | XCEL | SMOKY HILL SUBSTATION | XCEL | 70597 | 70599 | Xcel Owned | Narcissus | BUSBAR_SECTION | SMOK | 2832 | 3115 | 3228 | 3551 | 1692 | 1862 | 1929 | 2122
HMIL-SMOK-345.0-1 | 7081 | HARVEST MILE | XCEL | SMOKY HILL SUBSTATION | XCEL | 70597 | 70599 | Xcel Owned |  | LINE_TRAP | SMOK | 3000 | 3000 | 3312 | 3312 | 1793 | 1793 | 1979 | 1979
HMIL-SMOK-345.0-2 | 7087 | HARVEST MILE | XCEL | SMOKY HILL SUBSTATION | XCEL | 70597 | 70599 | Xcel Owned | HMIL-SMOK-345.0-2 | FACILITY |  | 2820 | 3102 | 3214 | 3536 | 1685 | 1854 | 1921 | 2113
HMIL-SMOK-345.0-2 | 7087 | HARVEST MILE | XCEL | SMOKY HILL SUBSTATION | XCEL | 70597 | 70599 | Xcel Owned | Narcissus | BUSBAR_SECTION | SMOK | 2820 | 3102 | 3214 | 3536 | 1685 | 1854 | 1921 | 2113
PAWN-MSST-345.0-1 | 7091 | PAWNEE 345KV | XCEL | MISSILE SITE | XCEL | 70598 | 70624 | Xcel Owned | PAWN-MSST-345.0-1 | FACILITY |  | 2821 | 3000 | 3214 | 3312 | 1686 | 1793 | 1921 | 1979
PAWN-MSST-345.0-1 | 7091 | PAWNEE 345KV | XCEL | MISSILE SITE | XCEL | 70598 | 70624 | Xcel Owned | Narcissus | BUSBAR_SECTION | MSST | 2821 | 3103 | 3214 | 3536 | 1686 | 1854 | 1921 | 2113
PAWN-MSST-345.0-1 | 7091 | PAWNEE 345KV | XCEL | MISSILE SITE | XCEL | 70598 | 70624 | Xcel Owned |  | LINE_TRAP | MSST | 3000 | 3000 | 3312 | 3312 | 1793 | 1793 | 1979 | 1979
PAWN-MSST-345.0-1 | 7091 | PAWNEE 345KV | XCEL | MISSILE SITE | XCEL | 70598 | 70624 | Xcel Owned |  | LINE_TRAP | PAWN | 3000 | 3000 | 3312 | 3312 | 1793 | 1793 | 1979 | 1979
UTER-MEEK-345.0-1 | 7300 | RIFLE UTE 230/345KV SUBSTATION | XCEL | MEEKER (TRI STATE) | FOREIGN | 79058 | 79266 | Xcel Owned | UTER-MEEK-345.0-1 | FACILITY |  | 1600 | 1600 | 1600 | 1600 | 956 | 956 | 956 | 956
UTER-MEEK-345.0-1 | 7300 | RIFLE UTE 230/345KV SUBSTATION | XCEL | MEEKER (TRI STATE) | FOREIGN | 79058 | 79266 | Xcel Owned | 7300 METER VAR | SECONDARY_CURRENT_LIMITATION | UTER | 1600 | 1600 | 1600 | 1600 | 956 | 956 | 956 | 956
UTER-MEEK-345.0-1 | 7300 | RIFLE UTE 230/345KV SUBSTATION | XCEL | MEEKER (TRI STATE) | FOREIGN | 79058 | 79266 | Xcel Owned |  | LINE_TRAP | UTER | 1600 | 1600 | 1664 | 1664 | 956 | 956 | 994 | 994
UTER-MEEK-345.0-1 | 7300 | RIFLE UTE 230/345KV SUBSTATION | XCEL | MEEKER (TRI STATE) | FOREIGN | 79058 | 79266 | Xcel Owned | UTER-MEEK-345.0-1 | Transmission Line | 7300 | 1600 | 1760 | 2520 | 2772 | 956 | 1052 | 1506 | 1656
UTER-MEEK-345.0-1 | 7300 | RIFLE UTE 230/345KV SUBSTATION | XCEL | MEEKER (TRI STATE) | FOREIGN | 79058 | 79266 | Xcel Owned | Foreign Ratings | Foreign Ratings | MEEK | 1600 | 2063 | 1600 | 2063 | 956 | 1233 | 956 | 1233
UTEG-UTER-345.0-1 | 7302 | UTE GRAND JUNCTION SUBSTATION | XCEL | RIFLE UTE 230/345KV SUBSTATION | XCEL | 79036 | 79058 | Xcel Owned | UTEG-UTER-345.0-1 | FACILITY |  | 1200 | 1200 | 1200 | 1200 | 717 | 717 | 717 | 717
UTEG-UTER-345.0-1 | 7302 | UTE GRAND JUNCTION SUBSTATION | XCEL | RIFLE UTE 230/345KV SUBSTATION | XCEL | 79036 | 79058 | Xcel Owned | 7302_21P | SECONDARY_CURRENT_LIMITATION | UTEG | 1200 | 1200 | 1200 | 1200 | 717 | 717 | 717 | 717
ATER-BLPK-115.0-1 | 8004 | ALAMOSA TERMINAL SUBSTATION | XCEL | BLANCA PEAK SUBSTATION | XCEL | 70025 | 70937 | Xcel Owned | ATER-BLPK-115.0-1 | FACILITY |  | 715 | 787 | 841 | 925 | 142 | 157 | 168 | 184
ATER-BLPK-115.0-1 | 8004 | ALAMOSA TERMINAL SUBSTATION | XCEL | BLANCA PEAK SUBSTATION | XCEL | 70025 | 70937 | Xcel Owned | ATER-BLPK-115.0-1 | Transmission Line | 8004 | 715 | 787 | 841 | 925 | 142 | 157 | 168 | 184
ROSE-UNCS-115.0-1 | 8014 | ROSEDALE SUBSTATION | XCEL | UNC SWITCHING STATION | XCEL | 70368 | 70439 | Xcel Owned | ROSE-UNCS-115.0-1 | FACILITY |  | 923 | 1074 | 928 | 1021 | 184 | 214 | 185 | 203
ROSE-UNCS-115.0-1 | 8014 | ROSEDALE SUBSTATION | XCEL | UNC SWITCHING STATION | XCEL | 70368 | 70439 | Xcel Owned | Arbutus | BUSBAR_SECTION | UNCS | 923 | 1074 | 1099 | 1222 | 184 | 214 | 219 | 243
ROSE-UNCS-115.0-1 | 8014 | ROSEDALE SUBSTATION | XCEL | UNC SWITCHING STATION | XCEL | 70368 | 70439 | Xcel Owned | ROSE-UNCS-115.0-1 | Transmission Line | 8014 | 1104 | 1214 | 928 | 1021 | 220 | 242 | 185 | 203
ALLI-KEND-115.0-1 | 8024 | ALLISON SUBSTATION | XCEL | KENDRICK SUBSTATION | XCEL | 70023 | 70242 | Xcel Owned | ALLI-KEND-115.0-1 | FACILITY |  | 710 | 781 | 710 | 781 | 141 | 156 | 141 | 156
ALLI-KEND-115.0-1 | 8024 | ALLISON SUBSTATION | XCEL | KENDRICK SUBSTATION | XCEL | 70023 | 70242 | Xcel Owned | ALLI-KEND-115.0-1 | Transmission Line | 8024 | 710 | 781 | 710 | 781 | 141 | 156 | 141 | 156
ALLI-SODA-115.0-1 | 8024 | ALLISON SUBSTATION | XCEL | SODA LAKES SUBSTATION | XCEL | 70023 | 70400 | Xcel Owned | ALLI-SODA-115.0-1 | FACILITY |  | 767 | 874 | 904 | 994 | 153 | 174 | 180 | 198
ALLI-SODA-115.0-1 | 8024 | ALLISON SUBSTATION | XCEL | SODA LAKES SUBSTATION | XCEL | 70023 | 70400 | Xcel Owned | Arbutus | BUSBAR_SECTION | ALLI | 767 | 905 | 922 | 1034 | 153 | 180 | 184 | 206
ALLI-SODA-115.0-1 | 8024 | ALLISON SUBSTATION | XCEL | SODA LAKES SUBSTATION | XCEL | 70023 | 70400 | Xcel Owned | Hawk | BUSBAR_SECTION | SODA | 795 | 874 | 904 | 994 | 158 | 174 | 180 | 198
BANC-KEND-115.0-1 | 8024 | BANCROFT SUBSTATION | XCEL | KENDRICK SUBSTATION | XCEL | 70045 | 70242 | Xcel Owned | BANC-KEND-115.0-1 | FACILITY |  | 795 | 874 | 904 | 994 | 158 | 174 | 180 | 198
BANC-KEND-115.0-1 | 8024 | BANCROFT SUBSTATION | XCEL | KENDRICK SUBSTATION | XCEL | 70045 | 70242 | Xcel Owned | Hawk | BUSBAR_SECTION | KEND | 795 | 874 | 904 | 994 | 158 | 174 | 180 | 198
CONI_TP1-CONI-115.0-1 | 8026 | CONIFER | XCEL | CONIFER SUBSTATION | XCEL | 2108 | 70124 | Xcel Owned | CONI_TP1-CONI-115.0-1 | FACILITY |  | 825 | 907 | 904 | 994 | 164 | 181 | 180 | 198
CONI_TP1-CONI-115.0-1 | 8026 | CONIFER | XCEL | CONIFER SUBSTATION | XCEL | 2108 | 70124 | Xcel Owned | CONI_TP1-CONI-115.0-1 | Transmission Line | 8026 | 825 | 907 | 904 | 994 | 164 | 181 | 180 | 198
CONI_TP2-CONI-115.0-1 | 8026 | CONIFER | XCEL | CONIFER SUBSTATION | XCEL | 2109 | 2110 | Xcel Owned | CONI_TP2-CONI-115.0-1 | FACILITY |  | 825 | 907 | 904 | 994 | 164 | 181 | 180 | 198
CONI_TP2-CONI-115.0-1 | 8026 | CONIFER | XCEL | CONIFER SUBSTATION | XCEL | 2109 | 2110 | Xcel Owned | CONI_TP2-CONI-115.0-1 | Transmission Line | 8026 | 825 | 907 | 904 | 994 | 164 | 181 | 180 | 198
CONI_TP2-CONI-115.0-2 | 8026 | CONIFER | XCEL | CONIFER SUBSTATION | XCEL | 2109 | 2111 | Xcel Owned | CONI_TP2-CONI-115.0-2 | FACILITY |  | 825 | 907 | 904 | 994 | 164 | 181 | 180 | 198
CONI_TP2-CONI-115.0-2 | 8026 | CONIFER | XCEL | CONIFER SUBSTATION | XCEL | 2109 | 2111 | Xcel Owned | CONI_TP2-CONI-115.0-2 | Transmission Line | 8026 | 825 | 907 | 904 | 994 | 164 | 181 | 180 | 198
HEND-PORT-115.0-1 | 8054 | HENDERSON SUBSTATION | XCEL | PORTAL SUBSTATION | XCEL | 70218 | 70328 | Jointly Owned | HEND-PORT-115.0-1 | FACILITY |  | 600 | 600 | 600 | 600 | 120 | 120 | 120 | 120
HEND-PORT-115.0-1 | 8054 | HENDERSON SUBSTATION | XCEL | PORTAL SUBSTATION | XCEL | 70218 | 70328 | Jointly Owned | 8054 METER VAR | SECONDARY_CURRENT_LIMITATION | HEND | 600 | 600 | 600 | 600 | 120 | 120 | 120 | 120
HEND-PORT-115.0-1 | 8054 | HENDERSON SUBSTATION | XCEL | PORTAL SUBSTATION | XCEL | 70218 | 70328 | Jointly Owned | 8054 METER AMP | SECONDARY_CURRENT_LIMITATION | HEND | 600 | 600 | 600 | 600 | 120 | 120 | 120 | 120
HEND-PORT-115.0-1 | 8054 | HENDERSON SUBSTATION | XCEL | PORTAL SUBSTATION | XCEL | 70218 | 70328 | Jointly Owned | 8054 METER W | SECONDARY_CURRENT_LIMITATION | HEND | 600 | 600 | 600 | 600 | 120 | 120 | 120 | 120
MILL-PORT-115.0-1 | 8054 | MILL SUBSTATION | XCEL | PORTAL SUBSTATION | XCEL | 70287 | 70328 | Jointly Owned | MILL-PORT-115.0-1 | FACILITY |  | 767 | 844 | 874 | 900 | 153 | 168 | 174 | 179
MILL-PORT-115.0-1 | 8054 | MILL SUBSTATION | XCEL | PORTAL SUBSTATION | XCEL | 70287 | 70328 | Jointly Owned | Hawk | BUSBAR_SECTION | MILL | 767 | 844 | 874 | 962 | 153 | 168 | 174 | 192
MILL-PORT-115.0-1 | 8054 | MILL SUBSTATION | XCEL | PORTAL SUBSTATION | XCEL | 70287 | 70328 | Jointly Owned | 8054 246Y | CURRENT_TRANSFORMER | MILL | 900 | 900 | 900 | 900 | 179 | 179 | 179 | 179
MILL-PORT-115.0-1 | 8054 | MILL SUBSTATION | XCEL | PORTAL SUBSTATION | XCEL | 70287 | 70328 | Jointly Owned | 8054 135X | CURRENT_TRANSFORMER | MILL | 900 | 900 | 900 | 900 | 179 | 179 | 179 | 179
MILL-PORT-115.0-1 | 8054 | MILL SUBSTATION | XCEL | PORTAL SUBSTATION | XCEL | 70287 | 70328 | Jointly Owned | 8054 135Y | CURRENT_TRANSFORMER | MILL | 900 | 900 | 900 | 900 | 179 | 179 | 179 | 179
BLUE-MILL-115.0-1 | 8055 | BLUE RIVER SUBSTATION | XCEL | MILL SUBSTATION | XCEL | 70052 | 70287 | Jointly Owned | BLUE-MILL-115.0-1 | FACILITY |  | 767 | 800 | 832 | 832 | 153 | 159 | 166 | 166
BLUE-MILL-115.0-1 | 8055 | BLUE RIVER SUBSTATION | XCEL | MILL SUBSTATION | XCEL | 70052 | 70287 | Jointly Owned | Hawk | BUSBAR_SECTION | MILL | 767 | 844 | 874 | 962 | 153 | 168 | 174 | 192
BLUE-MILL-115.0-1 | 8055 | BLUE RIVER SUBSTATION | XCEL | MILL SUBSTATION | XCEL | 70052 | 70287 | Jointly Owned |  | LINE_TRAP | BLUE | 800 | 800 | 832 | 832 | 159 | 159 | 166 | 166
CLIM-MAYF-115.0-1 | 8174 | CLIMAX SUBSTATION | XCEL | MAYFLOWER SUBSTATION | XCEL | 70114 | 70281 | Xcel Owned | CLIM-MAYF-115.0-1 | FACILITY |  | 418 | 460 | 475 | 500 | 83 | 92 | 95 | 100
CLIM-MAYF-115.0-1 | 8174 | CLIMAX SUBSTATION | XCEL | MAYFLOWER SUBSTATION | XCEL | 70114 | 70281 | Xcel Owned | CLIM-MAYF-115.0-1 | Transmission Line | 8174 | 418 | 460 | 475 | 523 | 83 | 92 | 95 | 104
CLIM-MAYF-115.0-1 | 8174 | CLIMAX SUBSTATION | XCEL | MAYFLOWER SUBSTATION | XCEL | 70114 | 70281 | Xcel Owned | 8174 METER VAR | SECONDARY_CURRENT_LIMITATION | CLIM | 500 | 500 | 500 | 500 | 100 | 100 | 100 | 100
DILL-SUMM-115.0-1 | 8189 | DILLON SUBSTATION | XCEL | SUMMIT SUBSTATION | XCEL | 70155 | 70421 | Xcel Owned | DILL-SUMM-115.0-1 | FACILITY |  | 418 | 460 | 475 | 523 | 83 | 92 | 95 | 104
DILL-SUMM-115.0-1 | 8189 | DILLON SUBSTATION | XCEL | SUMMIT SUBSTATION | XCEL | 70155 | 70421 | Xcel Owned | DILL-SUMM-115.0-1 | Transmission Line | 8189 | 418 | 460 | 475 | 523 | 83 | 92 | 95 | 104
MAYF-SUMM-115.0-1 | 8189 | MAYFLOWER SUBSTATION | XCEL | SUMMIT SUBSTATION | XCEL | 70281 | 70421 | Xcel Owned | MAYF-SUMM-115.0-1 | FACILITY |  | 418 | 460 | 475 | 523 | 83 | 92 | 95 | 104
MAYF-SUMM-115.0-1 | 8189 | MAYFLOWER SUBSTATION | XCEL | SUMMIT SUBSTATION | XCEL | 70281 | 70421 | Xcel Owned | MAYF-SUMM-115.0-1 | Transmission Line | 8189 | 418 | 460 | 475 | 523 | 83 | 92 | 95 | 104
MONF-TMON-115.0-1 | 8264 | MONFORT SUBSTATION | XCEL | Termo Monfort Co-Gen | FOREIGN | 70290 | 2009 | Xcel Owned | MONF-TMON-115.0-1 | FACILITY |  | 300 | 300 | 300 | 300 | 60 | 60 | 60 | 60
MONF-TMON-115.0-1 | 8264 | MONFORT SUBSTATION | XCEL | Termo Monfort Co-Gen | FOREIGN | 70290 | 2009 | Xcel Owned | 8264 246X | CURRENT_TRANSFORMER | MONF | 300 | 300 | 300 | 300 | 60 | 60 | 60 | 60
MONF-TMON-115.0-1 | 8264 | MONFORT SUBSTATION | XCEL | Termo Monfort Co-Gen | FOREIGN | 70290 | 2009 | Xcel Owned | Foreign Ratings | Foreign Ratings | TMON | 300 | 300 | 300 | 300 | 60 | 60 | 60 | 60
MONF-LPNO_TP-115.0-1 | 8265 | MONFORT SUBSTATION | XCEL | LEPRINO TAP | XCEL | 70290 | 70805 | Xcel Owned | MONF-LPNO_TP-115.0-1 | FACILITY |  | 924 | 1075 | 1099 | 1200 | 184 | 214 | 219 | 239
MONF-LPNO_TP-115.0-1 | 8265 | MONFORT SUBSTATION | XCEL | LEPRINO TAP | XCEL | 70290 | 70805 | Xcel Owned | Arbutus | BUSBAR_SECTION | MONF | 924 | 1075 | 1099 | 1223 | 184 | 214 | 219 | 244
MONF-LPNO_TP-115.0-1 | 8265 | MONFORT SUBSTATION | XCEL | LEPRINO TAP | XCEL | 70290 | 70805 | Xcel Owned | 8265 135X | CURRENT_TRANSFORMER | MONF | 1200 | 1200 | 1200 | 1200 | 239 | 239 | 239 | 239
MONF-LPNO_TP-115.0-1 | 8265 | MONFORT SUBSTATION | XCEL | LEPRINO TAP | XCEL | 70290 | 70805 | Xcel Owned | 8265 246Y | CURRENT_TRANSFORMER | MONF | 1200 | 1200 | 1200 | 1200 | 239 | 239 | 239 | 239
MONF-LPNO_TP-115.0-1 | 8265 | MONFORT SUBSTATION | XCEL | LEPRINO TAP | XCEL | 70290 | 70805 | Xcel Owned | 8265 135Y | CURRENT_TRANSFORMER | MONF | 1200 | 1200 | 1200 | 1200 | 239 | 239 | 239 | 239
UNCS-LPNO_TP-115.0-1 | 8265 | UNC SWITCHING STATION | XCEL | LEPRINO TAP | XCEL | 70439 | 70805 | Xcel Owned | UNCS-LPNO_TP-115.0-1 | FACILITY |  | 923 | 1074 | 1099 | 1200 | 184 | 214 | 219 | 239
UNCS-LPNO_TP-115.0-1 | 8265 | UNC SWITCHING STATION | XCEL | LEPRINO TAP | XCEL | 70439 | 70805 | Xcel Owned | Arbutus | BUSBAR_SECTION | UNCS | 923 | 1074 | 1099 | 1222 | 184 | 214 | 219 | 243
UNCS-LPNO_TP-115.0-1 | 8265 | UNC SWITCHING STATION | XCEL | LEPRINO TAP | XCEL | 70439 | 70805 | Xcel Owned | 8265 246Y | CURRENT_TRANSFORMER | UNCS | 1200 | 1200 | 1200 | 1200 | 239 | 239 | 239 | 239
UNCS-LPNO_TP-115.0-1 | 8265 | UNC SWITCHING STATION | XCEL | LEPRINO TAP | XCEL | 70439 | 70805 | Xcel Owned | 8265 135Y | CURRENT_TRANSFORMER | UNCS | 1200 | 1200 | 1200 | 1200 | 239 | 239 | 239 | 239
UNCS-LPNO_TP-115.0-1 | 8265 | UNC SWITCHING STATION | XCEL | LEPRINO TAP | XCEL | 70439 | 70805 | Xcel Owned | 8265 135X | CURRENT_TRANSFORMER | UNCS | 1200 | 1200 | 1200 | 1200 | 239 | 239 | 239 | 239
UNCS-LPNO_TP-115.0-1 | 8265 | UNC SWITCHING STATION | XCEL | LEPRINO TAP | XCEL | 70439 | 70805 | Xcel Owned | 8265 246X | CURRENT_TRANSFORMER | UNCS | 1200 | 1200 | 1200 | 1200 | 239 | 239 | 239 | 239
UNCS-UNCC-115.0-1 | 8271 | UNC SWITCHING STATION | XCEL | UNC QF | XCEL | 70439 | 2007 | Xcel Owned | UNCS-UNCC-115.0-1 | FACILITY |  | 811 | 811 | 670 | 670 | 162 | 162 | 133 | 133
UNCS-UNCC-115.0-1 | 8271 | UNC SWITCHING STATION | XCEL | UNC QF | XCEL | 70439 | 2007 | Xcel Owned | UNCS-UNCC-115.0-1 | Transmission Line | 8271 | 811 | 811 | 670 | 670 | 162 | 162 | 133 | 133
GODF-JOHN-115.0-1 | 8365 | GODFREY SUBSTATION | XCEL | JOHNSTOWN SUBSTATION | XCEL | 70202 | 70240 | Xcel Owned | GODF-JOHN-115.0-1 | FACILITY |  | 804 | 884 | 914 | 1005 | 160 | 176 | 182 | 200
GODF-JOHN-115.0-1 | 8365 | GODFREY SUBSTATION | XCEL | JOHNSTOWN SUBSTATION | XCEL | 70202 | 70240 | Xcel Owned | Hawk | BUSBAR_SECTION | GODF | 804 | 884 | 914 | 1005 | 160 | 176 | 182 | 200
JOHN-WELD-115.0-1 | 8365 | JOHNSTOWN SUBSTATION | XCEL | WELD SUBSTATION | XCEL | 70246 | 70470 | Xcel Owned | JOHN-WELD-115.0-1 | FACILITY |  | 939 | 1033 | 1068 | 1175 | 187 | 206 | 213 | 234
JOHN-WELD-115.0-1 | 8365 | JOHNSTOWN SUBSTATION | XCEL | WELD SUBSTATION | XCEL | 70246 | 70470 | Xcel Owned | Swift | BUSBAR_SECTION | JOHN | 939 | 1033 | 1068 | 1175 | 187 | 206 | 213 | 234
DIVI-LKGE-115.0-1 | 8384 | DIVIDE SUBSTATION | XCEL | LAKE GEORGE | XCEL | 70157 | 70419 | Xcel Owned | DIVI-LKGE-115.0-1 | FACILITY |  | 1060 | 1166 | 1200 | 1200 | 211 | 232 | 239 | 239
DIVI-LKGE-115.0-1 | 8384 | DIVIDE SUBSTATION | XCEL | LAKE GEORGE | XCEL | 70157 | 70419 | Xcel Owned | Drake | BUSBAR_SECTION | DIVI | 1060 | 1166 | 1210 | 1331 | 211 | 232 | 241 | 265
DIVI-LKGE-115.0-1 | 8384 | DIVIDE SUBSTATION | XCEL | LAKE GEORGE | XCEL | 70157 | 70419 | Xcel Owned | 8384 | BREAKER | DIVI | 1200 | 1200 | 1200 | 1200 | 239 | 239 | 239 | 239
LKGE-TARR-115.0-1 | 8384 | LAKE GEORGE | XCEL | TARRYALL SUBSTATION | XCEL | 70419 | 70426 | Xcel Owned | LKGE-TARR-115.0-1 | FACILITY |  | 600 | 600 | 600 | 600 | 120 | 120 | 120 | 120
LKGE-TARR-115.0-1 | 8384 | LAKE GEORGE | XCEL | TARRYALL SUBSTATION | XCEL | 70419 | 70426 | Xcel Owned | 8384 135X | CURRENT_TRANSFORMER | TARR | 600 | 600 | 600 | 600 | 120 | 120 | 120 | 120
BCRK-WOLC-115.0-1 | 8415 | BEAVER CREEK WEST SUBSTATION | XCEL | WOLCOTT | FOREIGN | 79006 | 79068 | Jointly Owned | BCRK-WOLC-115.0-1 | FACILITY |  | 600 | 600 | 600 | 600 | 120 | 120 | 120 | 120
BCRK-WOLC-115.0-1 | 8415 | BEAVER CREEK WEST SUBSTATION | XCEL | WOLCOTT | FOREIGN | 79006 | 79068 | Jointly Owned | BC541 METER VAR | SECONDARY_CURRENT_LIMITATION | BCRK | 600 | 600 | 600 | 600 | 120 | 120 | 120 | 120
BCRK-WOLC-115.0-1 | 8415 | BEAVER CREEK WEST SUBSTATION | XCEL | WOLCOTT | FOREIGN | 79006 | 79068 | Jointly Owned | BC541 135Y | CURRENT_TRANSFORMER | BCRK | 600 | 600 | 600 | 600 | 120 | 120 | 120 | 120
BCRK-WOLC-115.0-1 | 8415 | BEAVER CREEK WEST SUBSTATION | XCEL | WOLCOTT | FOREIGN | 79006 | 79068 | Jointly Owned | BC541 135X | CURRENT_TRANSFORMER | BCRK | 600 | 600 | 600 | 600 | 120 | 120 | 120 | 120
BCRK-WOLC-115.0-1 | 8415 | BEAVER CREEK WEST SUBSTATION | XCEL | WOLCOTT | FOREIGN | 79006 | 79068 | Jointly Owned | Foreign Ratings | Foreign Ratings | WOLC | 600 | 600 | 743 | 743 | 120 | 120 | 148 | 148
VAIL-WOLC-115.0-1 | 8416 | VAIL SUBSTATION | XCEL | WOLCOTT | FOREIGN | 79066 | 79068 | Jointly Owned | VAIL-WOLC-115.0-1 | FACILITY |  | 600 | 600 | 600 | 600 | 120 | 120 | 120 | 120
VAIL-WOLC-115.0-1 | 8416 | VAIL SUBSTATION | XCEL | WOLCOTT | FOREIGN | 79066 | 79068 | Jointly Owned | 8430 246X | CURRENT_TRANSFORMER | VAIL | 600 | 600 | 600 | 600 | 120 | 120 | 120 | 120
VAIL-WOLC-115.0-1 | 8416 | VAIL SUBSTATION | XCEL | WOLCOTT | FOREIGN | 79066 | 79068 | Jointly Owned | 8416 246X | CURRENT_TRANSFORMER | VAIL | 600 | 600 | 600 | 600 | 120 | 120 | 120 | 120
VAIL-WOLC-115.0-1 | 8416 | VAIL SUBSTATION | XCEL | WOLCOTT | FOREIGN | 79066 | 79068 | Jointly Owned | 8430 135X | CURRENT_TRANSFORMER | VAIL | 600 | 600 | 600 | 600 | 120 | 120 | 120 | 120
BCRK-AVON-115.0-1 | 8424 | BEAVER CREEK WEST SUBSTATION | XCEL | AVON SUBSTATION | XCEL | 79006 | 79092 | Jointly Owned | BCRK-AVON-115.0-1 | FACILITY |  | 600 | 600 | 600 | 600 | 120 | 120 | 120 | 120
BCRK-AVON-115.0-1 | 8424 | BEAVER CREEK WEST SUBSTATION | XCEL | AVON SUBSTATION | XCEL | 79006 | 79092 | Jointly Owned | BC551 135X | CURRENT_TRANSFORMER | BCRK | 600 | 600 | 600 | 600 | 120 | 120 | 120 | 120
BCRK-AVON-115.0-1 | 8424 | BEAVER CREEK WEST SUBSTATION | XCEL | AVON SUBSTATION | XCEL | 79006 | 79092 | Jointly Owned | BC551 METER VAR | SECONDARY_CURRENT_LIMITATION | BCRK | 600 | 600 | 600 | 600 | 120 | 120 | 120 | 120
BCRK-AVON-115.0-1 | 8424 | BEAVER CREEK WEST SUBSTATION | XCEL | AVON SUBSTATION | XCEL | 79006 | 79092 | Jointly Owned | BC551 135Y | CURRENT_TRANSFORMER | BCRK | 600 | 600 | 600 | 600 | 120 | 120 | 120 | 120
VAIL-AVON-115.0-1 | 8425 | VAIL SUBSTATION | XCEL | AVON SUBSTATION | XCEL | 79066 | 79092 | Jointly Owned | VAIL-AVON-115.0-1 | FACILITY |  | 600 | 600 | 600 | 600 | 120 | 120 | 120 | 120
VAIL-AVON-115.0-1 | 8425 | VAIL SUBSTATION | XCEL | AVON SUBSTATION | XCEL | 79066 | 79092 | Jointly Owned | 8430 246X | CURRENT_TRANSFORMER | VAIL | 600 | 600 | 600 | 600 | 120 | 120 | 120 | 120
VAIL-AVON-115.0-1 | 8425 | VAIL SUBSTATION | XCEL | AVON SUBSTATION | XCEL | 79066 | 79092 | Jointly Owned | 8425 246X | CURRENT_TRANSFORMER | VAIL | 600 | 600 | 600 | 600 | 120 | 120 | 120 | 120
VAIL-AVON-115.0-1 | 8425 | VAIL SUBSTATION | XCEL | AVON SUBSTATION | XCEL | 79066 | 79092 | Jointly Owned | 8430 135X | CURRENT_TRANSFORMER | VAIL | 600 | 600 | 600 | 600 | 120 | 120 | 120 | 120
WOOD-DIVI-115.0-1 | 8455 | WOODLAND PARK SUBSTATION | XCEL | DIVIDE SUBSTATION | XCEL | 70476 | 70157 | Xcel Owned | WOOD-DIVI-115.0-1 | FACILITY |  | 600 | 775 | 743 | 890 | 120 | 154 | 148 | 177
WOOD-DIVI-115.0-1 | 8455 | WOODLAND PARK SUBSTATION | XCEL | DIVIDE SUBSTATION | XCEL | 70476 | 70157 | Xcel Owned | 8450 | SWITCH | WOOD | 600 | 775 | 743 | 890 | 120 | 154 | 148 | 177
WOOD-FLAK-115.0-1 | 8455 | WOODLAND PARK SUBSTATION | XCEL | FOREST LAKE | XCEL | 70476 | 73476 | Xcel Owned | WOOD-FLAK-115.0-1 | FACILITY |  | 600 | 600 | 600 | 600 | 120 | 120 | 120 | 120
WOOD-FLAK-115.0-1 | 8455 | WOODLAND PARK SUBSTATION | XCEL | FOREST LAKE | XCEL | 70476 | 73476 | Xcel Owned | 115 BUSW MU A | CURRENT_TRANSFORMER | FLAK | 600 | 600 | 600 | 600 | 120 | 120 | 120 | 120
WOOD-FLAK-115.0-1 | 8455 | WOODLAND PARK SUBSTATION | XCEL | FOREST LAKE | XCEL | 70476 | 73476 | Xcel Owned | 115 BUSW MU B | CURRENT_TRANSFORMER | FLAK | 600 | 600 | 600 | 600 | 120 | 120 | 120 | 120
WOOD-FLAK-115.0-1 | 8455 | WOODLAND PARK SUBSTATION | XCEL | FOREST LAKE | XCEL | 70476 | 73476 | Xcel Owned | 115 BUSW MU C | CURRENT_TRANSFORMER | FLAK | 600 | 600 | 600 | 600 | 120 | 120 | 120 | 120
WOOD-FLAK-115.0-1 | 8455 | WOODLAND PARK SUBSTATION | XCEL | FOREST LAKE | XCEL | 70476 | 73476 | Xcel Owned | 8450 | SWITCH | WOOD | 600 | 775 | 743 | 890 | 120 | 154 | 148 | 177
GRAY-LAKE-115.0-1 | 9000 | GRAY STREET SUBSTATION | XCEL | LAKEWOOD SUBSTATION | XCEL | 70208 | 70251 | Xcel Owned | GRAY-LAKE-115.0-1 | FACILITY |  | 557 | 600 | 600 | 600 | 111 | 120 | 120 | 120
GRAY-LAKE-115.0-1 | 9000 | GRAY STREET SUBSTATION | XCEL | LAKEWOOD SUBSTATION | XCEL | 70208 | 70251 | Xcel Owned | 4/0 - 7 | BUSBAR_SECTION | LAKE | 557 | 613 | 640 | 704 | 111 | 122 | 127 | 140
GRAY-LAKE-115.0-1 | 9000 | GRAY STREET SUBSTATION | XCEL | LAKEWOOD SUBSTATION | XCEL | 70208 | 70251 | Xcel Owned | 9000 METER VAR | SECONDARY_CURRENT_LIMITATION | GRAY | 600 | 600 | 600 | 600 | 120 | 120 | 120 | 120
LAKE-RIDG-115.0-1 | 9000 | LAKEWOOD SUBSTATION | XCEL | RIDGE SUBSTATION | XCEL | 70251 | 70354 | Xcel Owned | LAKE-RIDG-115.0-1 | FACILITY |  | 557 | 600 | 600 | 600 | 111 | 120 | 120 | 120
LAKE-RIDG-115.0-1 | 9000 | LAKEWOOD SUBSTATION | XCEL | RIDGE SUBSTATION | XCEL | 70251 | 70354 | Xcel Owned | 4/0 - 7 | BUSBAR_SECTION | LAKE | 557 | 613 | 640 | 704 | 111 | 122 | 127 | 140
LAKE-RIDG-115.0-1 | 9000 | LAKEWOOD SUBSTATION | XCEL | RIDGE SUBSTATION | XCEL | 70251 | 70354 | Xcel Owned | 9000 METER VAR | SECONDARY_CURRENT_LIMITATION | RIDG | 600 | 600 | 600 | 600 | 120 | 120 | 120 | 120
ARGO-DTER-115.0-1 | 9004 | ARGO SUBSTATION | XCEL | DENVER TERMINAL SUBSTATION | XCEL | 70039 | 70148 | Xcel Owned | ARGO-DTER-115.0-1 | FACILITY |  | 2394 | 2400 | 2400 | 2400 | 477 | 478 | 478 | 478
ARGO-DTER-115.0-1 | 9004 | ARGO SUBSTATION | XCEL | DENVER TERMINAL SUBSTATION | XCEL | 70039 | 70148 | Xcel Owned | ARGO-DTER-115.0-1 | Transmission Line | 9004 | 2394 | 2633 | 2726 | 2999 | 477 | 524 | 543 | 597
ARGO-DTER-115.0-1 | 9004 | ARGO SUBSTATION | XCEL | DENVER TERMINAL SUBSTATION | XCEL | 70039 | 70148 | Xcel Owned | 9004 135Y | CURRENT_TRANSFORMER | DTER | 2400 | 2400 | 2400 | 2400 | 478 | 478 | 478 | 478
ARGO-DTER-115.0-1 | 9004 | ARGO SUBSTATION | XCEL | DENVER TERMINAL SUBSTATION | XCEL | 70039 | 70148 | Xcel Owned | 9004 135Y PK-2 | SECONDARY_CURRENT_LIMITATION | DTER | 2400 | 2400 | 2400 | 2400 | 478 | 478 | 478 | 478
ARGO-DTER-115.0-1 | 9004 | ARGO SUBSTATION | XCEL | DENVER TERMINAL SUBSTATION | XCEL | 70039 | 70148 | Xcel Owned | 9004 246X PK | SECONDARY_CURRENT_LIMITATION | DTER | 2400 | 2400 | 2400 | 2400 | 478 | 478 | 478 | 478
ARGO-DTER-115.0-1 | 9004 | ARGO SUBSTATION | XCEL | DENVER TERMINAL SUBSTATION | XCEL | 70039 | 70148 | Xcel Owned | 9004 PK | SECONDARY_CURRENT_LIMITATION | ARGO | 2400 | 2400 | 2400 | 2400 | 478 | 478 | 478 | 478
ARGO-DTER-115.0-1 | 9004 | ARGO SUBSTATION | XCEL | DENVER TERMINAL SUBSTATION | XCEL | 70039 | 70148 | Xcel Owned | 9004 135X | CURRENT_TRANSFORMER | ARGO | 2400 | 2400 | 2400 | 2400 | 478 | 478 | 478 | 478
ARGO-DTER-115.0-1 | 9004 | ARGO SUBSTATION | XCEL | DENVER TERMINAL SUBSTATION | XCEL | 70039 | 70148 | Xcel Owned | 9004 135Y | CURRENT_TRANSFORMER | ARGO | 2400 | 2400 | 2400 | 2400 | 478 | 478 | 478 | 478
GRAY-LAKE-115.0-2 | 9005 | GRAY STREET SUBSTATION | XCEL | LAKEWOOD SUBSTATION | XCEL | 70208 | 70252 | Xcel Owned | GRAY-LAKE-115.0-2 | FACILITY |  | 557 | 600 | 600 | 600 | 111 | 120 | 120 | 120
GRAY-LAKE-115.0-2 | 9005 | GRAY STREET SUBSTATION | XCEL | LAKEWOOD SUBSTATION | XCEL | 70208 | 70252 | Xcel Owned | 4/0 - 7 | BUSBAR_SECTION | LAKE | 557 | 613 | 640 | 704 | 111 | 122 | 127 | 140
GRAY-LAKE-115.0-2 | 9005 | GRAY STREET SUBSTATION | XCEL | LAKEWOOD SUBSTATION | XCEL | 70208 | 70252 | Xcel Owned | 9005 METER VAR | SECONDARY_CURRENT_LIMITATION | GRAY | 600 | 600 | 600 | 600 | 120 | 120 | 120 | 120
LAKE-RIDG-115.0-2 | 9005 | LAKEWOOD SUBSTATION | XCEL | RIDGE SUBSTATION | XCEL | 70252 | 70354 | Xcel Owned | LAKE-RIDG-115.0-2 | FACILITY |  | 557 | 600 | 600 | 600 | 111 | 120 | 120 | 120
LAKE-RIDG-115.0-2 | 9005 | LAKEWOOD SUBSTATION | XCEL | RIDGE SUBSTATION | XCEL | 70252 | 70354 | Xcel Owned | 4/0 - 7 | BUSBAR_SECTION | LAKE | 557 | 613 | 640 | 704 | 111 | 122 | 127 | 140
LAKE-RIDG-115.0-2 | 9005 | LAKEWOOD SUBSTATION | XCEL | RIDGE SUBSTATION | XCEL | 70252 | 70354 | Xcel Owned | 9005 METER VAR | SECONDARY_CURRENT_LIMITATION | RIDG | 600 | 600 | 600 | 600 | 120 | 120 | 120 | 120
CAPI-DTER-115.0-1 | 9007 | CAPITOL HILL SUBSTATION | XCEL | DENVER TERMINAL SUBSTATION | XCEL | 70087 | 70148 | Xcel Owned | CAPI-DTER-115.0-1 | FACILITY |  | 660 | 726 | 660 | 726 | 131 | 145 | 131 | 145
CAPI-DTER-115.0-1 | 9007 | CAPITOL HILL SUBSTATION | XCEL | DENVER TERMINAL SUBSTATION | XCEL | 70087 | 70148 | Xcel Owned | CAPI-DTER-115.0-1 | Transmission Line | 9007 | 660 | 726 | 660 | 726 | 131 | 145 | 131 | 145
DTER-GRAY-115.0-1 | 9008 | DENVER TERMINAL SUBSTATION | XCEL | GRAY STREET SUBSTATION | XCEL | 70148 | 70208 | Xcel Owned | DTER-GRAY-115.0-1 | FACILITY |  | 1200 | 1200 | 1200 | 1200 | 239 | 239 | 239 | 239
DTER-GRAY-115.0-1 | 9008 | DENVER TERMINAL SUBSTATION | XCEL | GRAY STREET SUBSTATION | XCEL | 70148 | 70208 | Xcel Owned | 9008 METER VAR | SECONDARY_CURRENT_LIMITATION | GRAY | 1200 | 1200 | 1200 | 1200 | 239 | 239 | 239 | 239
DTER-GRAY-115.0-1 | 9008 | DENVER TERMINAL SUBSTATION | XCEL | GRAY STREET SUBSTATION | XCEL | 70148 | 70208 | Xcel Owned | 9008 135Y 21Z1/2 | SECONDARY_CURRENT_LIMITATION | DTER | 1200 | 1200 | 1200 | 1200 | 239 | 239 | 239 | 239
DTER-GRAY-115.0-1 | 9008 | DENVER TERMINAL SUBSTATION | XCEL | GRAY STREET SUBSTATION | XCEL | 70148 | 70208 | Xcel Owned | 9008 246X 50BF | SECONDARY_CURRENT_LIMITATION | DTER | 1200 | 1200 | 1200 | 1200 | 239 | 239 | 239 | 239
DTER-GRAY-115.0-1 | 9008 | DENVER TERMINAL SUBSTATION | XCEL | GRAY STREET SUBSTATION | XCEL | 70148 | 70208 | Xcel Owned | 9008L | SWITCH | GRAY | 1200 | 1549 | 1486 | 1780 | 239 | 309 | 296 | 355
DTER-GRAY-115.0-1 | 9008 | DENVER TERMINAL SUBSTATION | XCEL | GRAY STREET SUBSTATION | XCEL | 70148 | 70208 | Xcel Owned | 9008M | SWITCH | GRAY | 1200 | 1549 | 1486 | 1780 | 239 | 309 | 296 | 355
DTER-GRAY-115.0-1 | 9008 | DENVER TERMINAL SUBSTATION | XCEL | GRAY STREET SUBSTATION | XCEL | 70148 | 70208 | Xcel Owned | 9008M | SWITCH | DTER | 1200 | 1549 | 1486 | 1780 | 239 | 309 | 296 | 355
ELDO-VALM-115.0-1 | 9046 | ELDORADO SPRINGS SUBSTATION | XCEL | VALMONT SWITCHYARD SUBSTATION | XCEL | 70164 | 70444 | Xcel Owned | ELDO-VALM-115.0-1 | FACILITY |  | 600 | 600 | 600 | 600 | 120 | 120 | 120 | 120
ELDO-VALM-115.0-1 | 9046 | ELDORADO SPRINGS SUBSTATION | XCEL | VALMONT SWITCHYARD SUBSTATION | XCEL | 70164 | 70444 | Xcel Owned | 9046 C7C8C9 | CURRENT_TRANSFORMER | ELDO | 600 | 600 | 600 | 600 | 120 | 120 | 120 | 120
ELDO-VALM-115.0-1 | 9046 | ELDORADO SPRINGS SUBSTATION | XCEL | VALMONT SWITCHYARD SUBSTATION | XCEL | 70164 | 70444 | Xcel Owned | 9046 246Y | CURRENT_TRANSFORMER | VALM | 600 | 600 | 600 | 600 | 120 | 120 | 120 | 120
ELDO-VALM-115.0-1 | 9046 | ELDORADO SPRINGS SUBSTATION | XCEL | VALMONT SWITCHYARD SUBSTATION | XCEL | 70164 | 70444 | Xcel Owned | 9046 135Y | CURRENT_TRANSFORMER | VALM | 600 | 600 | 600 | 600 | 120 | 120 | 120 | 120
ELDO-VALM-115.0-1 | 9046 | ELDORADO SPRINGS SUBSTATION | XCEL | VALMONT SWITCHYARD SUBSTATION | XCEL | 70164 | 70444 | Xcel Owned | 9046 C4C5C6 | CURRENT_TRANSFORMER | ELDO | 600 | 600 | 600 | 600 | 120 | 120 | 120 | 120
ELDO-VALM-115.0-1 | 9046 | ELDORADO SPRINGS SUBSTATION | XCEL | VALMONT SWITCHYARD SUBSTATION | XCEL | 70164 | 70444 | Xcel Owned | 9046 246X | CURRENT_TRANSFORMER | VALM | 600 | 600 | 600 | 600 | 120 | 120 | 120 | 120
ELDO-VALM-115.0-1 | 9046 | ELDORADO SPRINGS SUBSTATION | XCEL | VALMONT SWITCHYARD SUBSTATION | XCEL | 70164 | 70444 | Xcel Owned | 9046 METER VAR | SECONDARY_CURRENT_LIMITATION | ELDO | 600 | 600 | 600 | 600 | 120 | 120 | 120 | 120
ELDO-VALM-115.0-1 | 9046 | ELDORADO SPRINGS SUBSTATION | XCEL | VALMONT SWITCHYARD SUBSTATION | XCEL | 70164 | 70444 | Xcel Owned | 9046 C1C2C3 | CURRENT_TRANSFORMER | ELDO | 600 | 600 | 600 | 600 | 120 | 120 | 120 | 120
ELDO-VALM-115.0-1 | 9046 | ELDORADO SPRINGS SUBSTATION | XCEL | VALMONT SWITCHYARD SUBSTATION | XCEL | 70164 | 70444 | Xcel Owned | 9046M | SWITCH | ELDO | 600 | 775 | 743 | 890 | 120 | 154 | 148 | 177
BROO-LOUI-115.0-1 | 9052 | BROOMFIELD SUBSTATION | XCEL | LOUISVILLE SUBSTATION | XCEL | 70065 | 70269 | Xcel Owned | BROO-LOUI-115.0-1 | FACILITY |  | 800 | 800 | 832 | 832 | 159 | 159 | 166 | 166
BROO-LOUI-115.0-1 | 9052 | BROOMFIELD SUBSTATION | XCEL | LOUISVILLE SUBSTATION | XCEL | 70065 | 70269 | Xcel Owned |  | LINE_TRAP | BROO | 800 | 800 | 832 | 832 | 159 | 159 | 166 | 166
LOUI-VALM-115.0-1 | 9052 | LOUISVILLE SUBSTATION | XCEL | VALMONT SWITCHYARD SUBSTATION | XCEL | 70269 | 70444 | Xcel Owned | LOUI-VALM-115.0-1 | FACILITY |  | 1066 | 1173 | 1200 | 1200 | 212 | 234 | 239 | 239
LOUI-VALM-115.0-1 | 9052 | LOUISVILLE SUBSTATION | XCEL | VALMONT SWITCHYARD SUBSTATION | XCEL | 70269 | 70444 | Xcel Owned | Arbutus | BUSBAR_SECTION | LOUI | 1066 | 1173 | 1214 | 1335 | 212 | 234 | 242 | 266
LOUI-VALM-115.0-1 | 9052 | LOUISVILLE SUBSTATION | XCEL | VALMONT SWITCHYARD SUBSTATION | XCEL | 70269 | 70444 | Xcel Owned | 9052 135Y | CURRENT_TRANSFORMER | VALM | 1200 | 1200 | 1200 | 1200 | 239 | 239 | 239 | 239
LOUI-VALM-115.0-1 | 9052 | LOUISVILLE SUBSTATION | XCEL | VALMONT SWITCHYARD SUBSTATION | XCEL | 70269 | 70444 | Xcel Owned | 9052 135X | CURRENT_TRANSFORMER | VALM | 1200 | 1200 | 1200 | 1200 | 239 | 239 | 239 | 239
LOUI-VALM-115.0-1 | 9052 | LOUISVILLE SUBSTATION | XCEL | VALMONT SWITCHYARD SUBSTATION | XCEL | 70269 | 70444 | Xcel Owned | 9052-1 | CIRCUIT_SWITCHER | LOUI | 1200 | 1200 | 1200 | 1200 | 239 | 239 | 239 | 239
LOUI-VALM-115.0-1 | 9052 | LOUISVILLE SUBSTATION | XCEL | VALMONT SWITCHYARD SUBSTATION | XCEL | 70269 | 70444 | Xcel Owned | 9052 246X | CURRENT_TRANSFORMER | VALM | 1200 | 1200 | 1200 | 1200 | 239 | 239 | 239 | 239
LOUI-VALM-115.0-1 | 9052 | LOUISVILLE SUBSTATION | XCEL | VALMONT SWITCHYARD SUBSTATION | XCEL | 70269 | 70444 | Xcel Owned | 9052 246Y | CURRENT_TRANSFORMER | VALM | 1200 | 1200 | 1200 | 1200 | 239 | 239 | 239 | 239
FULT-PKWY-115.0-1 | 9053 | FULTON SUBSTATION | XCEL | PARKWAY (Tri State) | FOREIGN | 70194 | 70604 | Xcel Owned | FULT-PKWY-115.0-1 | FACILITY |  | 921 | 1072 | 1096 | 1200 | 183 | 213 | 218 | 239
FULT-PKWY-115.0-1 | 9053 | FULTON SUBSTATION | XCEL | PARKWAY (Tri State) | FOREIGN | 70194 | 70604 | Xcel Owned | Arbutus | BUSBAR_SECTION | FULT | 921 | 1072 | 1096 | 1219 | 183 | 213 | 218 | 243
FULT-PKWY-115.0-1 | 9053 | FULTON SUBSTATION | XCEL | PARKWAY (Tri State) | FOREIGN | 70194 | 70604 | Xcel Owned | 9053-11 | CIRCUIT_SWITCHER | FULT | 1200 | 1200 | 1200 | 1200 | 239 | 239 | 239 | 239
RECY-FLUP-115.0-1 | 9053 | RECYCLING - COORS | XCEL | FORT LUPTON SUBSTATION | XCEL | 70127 | 70191 | Xcel Owned | RECY-FLUP-115.0-1 | FACILITY |  | 1200 | 1200 | 1200 | 1200 | 239 | 239 | 239 | 239
RECY-FLUP-115.0-1 | 9053 | RECYCLING - COORS | XCEL | FORT LUPTON SUBSTATION | XCEL | 70127 | 70191 | Xcel Owned | 9053 246Y | CURRENT_TRANSFORMER | FLUP | 1200 | 1200 | 1200 | 1200 | 239 | 239 | 239 | 239
RECY-FLUP-115.0-1 | 9053 | RECYCLING - COORS | XCEL | FORT LUPTON SUBSTATION | XCEL | 70127 | 70191 | Xcel Owned | 9053 135X | CURRENT_TRANSFORMER | FLUP | 1200 | 1200 | 1200 | 1200 | 239 | 239 | 239 | 239
RECY-FLUP-115.0-1 | 9053 | RECYCLING - COORS | XCEL | FORT LUPTON SUBSTATION | XCEL | 70127 | 70191 | Xcel Owned | 9053 246X | CURRENT_TRANSFORMER | FLUP | 1200 | 1200 | 1200 | 1200 | 239 | 239 | 239 | 239
RECY-FLUP-115.0-1 | 9053 | RECYCLING - COORS | XCEL | FORT LUPTON SUBSTATION | XCEL | 70127 | 70191 | Xcel Owned | 9053 | BREAKER | FLUP | 1200 | 1200 | 1200 | 1200 | 239 | 239 | 239 | 239
RECY-FLUP-115.0-1 | 9053 | RECYCLING - COORS | XCEL | FORT LUPTON SUBSTATION | XCEL | 70127 | 70191 | Xcel Owned | 9053 135Y | CURRENT_TRANSFORMER | FLUP | 1200 | 1200 | 1200 | 1200 | 239 | 239 | 239 | 239
RECY-FLUP-115.0-1 | 9053 | RECYCLING - COORS | XCEL | FORT LUPTON SUBSTATION | XCEL | 70127 | 70191 | Xcel Owned | 9053M | SWITCH | FLUP | 1200 | 1549 | 1486 | 1780 | 239 | 309 | 296 | 355
RECY-FLUP-115.0-1 | 9053 | RECYCLING - COORS | XCEL | FORT LUPTON SUBSTATION | XCEL | 70127 | 70191 | Xcel Owned | 9053-7 | SWITCH | RECY | 1200 | 1549 | 1486 | 1780 | 239 | 309 | 296 | 355
RECY-FLUP-115.0-1 | 9053 | RECYCLING - COORS | XCEL | FORT LUPTON SUBSTATION | XCEL | 70127 | 70191 | Xcel Owned | 8340 | SWITCH | RECY | 1200 | 1549 | 1486 | 1780 | 239 | 309 | 296 | 355
RECY-FULT-115.0-1 | 9053 | RECYCLING - COORS | XCEL | FULTON SUBSTATION | XCEL | 70127 | 70194 | Xcel Owned | RECY-FULT-115.0-1 | FACILITY |  | 1072 | 1179 | 1219 | 1341 | 213 | 235 | 243 | 267
RECY-FULT-115.0-1 | 9053 | RECYCLING - COORS | XCEL | FULTON SUBSTATION | XCEL | 70127 | 70194 | Xcel Owned | Arbutus | BUSBAR_SECTION | RECY | 1072 | 1179 | 1219 | 1341 | 213 | 235 | 243 | 267
RECY-FULT-115.0-1 | 9053 | RECYCLING - COORS | XCEL | FULTON SUBSTATION | XCEL | 70127 | 70194 | Xcel Owned | Arbutus | BUSBAR_SECTION | FULT | 1072 | 1179 | 1219 | 1341 | 213 | 235 | 243 | 267
RALS-RIDG-115.0-1 | 9054 | RALSTON SUBSTATION | XCEL | RIDGE SUBSTATION | XCEL | 70345 | 70354 | Xcel Owned | RALS-RIDG-115.0-1 | FACILITY |  | 600 | 600 | 600 | 600 | 120 | 120 | 120 | 120
RALS-RIDG-115.0-1 | 9054 | RALSTON SUBSTATION | XCEL | RIDGE SUBSTATION | XCEL | 70345 | 70354 | Xcel Owned | 9054 METER VAR | SECONDARY_CURRENT_LIMITATION | RIDG | 600 | 600 | 600 | 600 | 120 | 120 | 120 | 120
RALS-VALM-115.0-1 | 9054 | RALSTON SUBSTATION | XCEL | VALMONT SWITCHYARD SUBSTATION | XCEL | 70345 | 70444 | Xcel Owned | RALS-VALM-115.0-1 | FACILITY |  | 600 | 705 | 729 | 802 | 120 | 140 | 145 | 160
RALS-VALM-115.0-1 | 9054 | RALSTON SUBSTATION | XCEL | VALMONT SWITCHYARD SUBSTATION | XCEL | 70345 | 70444 | Xcel Owned | 9054M | SWITCH | VALM | 600 | 775 | 743 | 890 | 120 | 154 | 148 | 177
RALS-VALM-115.0-1 | 9054 | RALSTON SUBSTATION | XCEL | VALMONT SWITCHYARD SUBSTATION | XCEL | 70345 | 70444 | Xcel Owned | 9054L | SWITCH | VALM | 600 | 775 | 743 | 890 | 120 | 154 | 148 | 177
RALS-VALM-115.0-1 | 9054 | RALSTON SUBSTATION | XCEL | VALMONT SWITCHYARD SUBSTATION | XCEL | 70345 | 70444 | Xcel Owned | RALS-VALM-115.0-1 | Transmission Line | 9054 | 641 | 705 | 729 | 802 | 128 | 140 | 145 | 160
CHER-FEDE-115.0-2 | 9055 | CHEROKEE SWITCHYARD SUBSTATION | XCEL | FEDERAL HEIGHTS SUBSTATION | XCEL | 70110 | 70175 | Xcel Owned | CHER-FEDE-115.0-2 | FACILITY |  | 1032 | 1135 | 1110 | 1221 | 206 | 226 | 221 | 243
CHER-FEDE-115.0-2 | 9055 | CHEROKEE SWITCHYARD SUBSTATION | XCEL | FEDERAL HEIGHTS SUBSTATION | XCEL | 70110 | 70175 | Xcel Owned | CHER-FEDE-115.0-2 | Transmission Line | 9055 | 1032 | 1135 | 1110 | 1221 | 206 | 226 | 221 | 243
FEDE-SEMP-115.0-1 | 9055 | FEDERAL HEIGHTS SUBSTATION | XCEL | SEMPER SUBSTATION | XCEL | 70175 | 70382 | Xcel Owned | FEDE-SEMP-115.0-1 | FACILITY |  | 800 | 880 | 910 | 1001 | 159 | 175 | 181 | 199
FEDE-SEMP-115.0-1 | 9055 | FEDERAL HEIGHTS SUBSTATION | XCEL | SEMPER SUBSTATION | XCEL | 70175 | 70382 | Xcel Owned | FEDE-SEMP-115.0-1 | Transmission Line | 9055 | 800 | 880 | 910 | 1001 | 159 | 175 | 181 | 199
BTER-VALM-115.0-1 | 9065 | BOULDER TERMINAL SUBSTATION | XCEL | VALMONT SWITCHYARD SUBSTATION | XCEL | 70059 | 70444 | Xcel Owned | BTER-VALM-115.0-1 | FACILITY |  | 799 | 879 | 900 | 900 | 159 | 175 | 179 | 179
BTER-VALM-115.0-1 | 9065 | BOULDER TERMINAL SUBSTATION | XCEL | VALMONT SWITCHYARD SUBSTATION | XCEL | 70059 | 70444 | Xcel Owned | Hawk | BUSBAR_SECTION | BTER | 799 | 879 | 908 | 999 | 159 | 175 | 181 | 199
BTER-VALM-115.0-1 | 9065 | BOULDER TERMINAL SUBSTATION | XCEL | VALMONT SWITCHYARD SUBSTATION | XCEL | 70059 | 70444 | Xcel Owned | 9065 246X | CURRENT_TRANSFORMER | BTER | 900 | 900 | 900 | 900 | 179 | 179 | 179 | 179
BTER-VALM-115.0-1 | 9065 | BOULDER TERMINAL SUBSTATION | XCEL | VALMONT SWITCHYARD SUBSTATION | XCEL | 70059 | 70444 | Xcel Owned | 9065 135X | CURRENT_TRANSFORMER | BTER | 900 | 900 | 900 | 900 | 179 | 179 | 179 | 179
BTER-VALM-115.0-2 | 9067 | BOULDER TERMINAL SUBSTATION | XCEL | VALMONT SWITCHYARD SUBSTATION | XCEL | 70059 | 70444 | Xcel Owned | BTER-VALM-115.0-2 | FACILITY |  | 800 | 880 | 900 | 900 | 159 | 175 | 179 | 179
BTER-VALM-115.0-2 | 9067 | BOULDER TERMINAL SUBSTATION | XCEL | VALMONT SWITCHYARD SUBSTATION | XCEL | 70059 | 70444 | Xcel Owned | BTER-VALM-115.0-2 | Transmission Line | 9067 | 800 | 880 | 910 | 1001 | 159 | 175 | 181 | 199
BTER-VALM-115.0-2 | 9067 | BOULDER TERMINAL SUBSTATION | XCEL | VALMONT SWITCHYARD SUBSTATION | XCEL | 70059 | 70444 | Xcel Owned | 9067 135Y | CURRENT_TRANSFORMER | BTER | 900 | 900 | 900 | 900 | 179 | 179 | 179 | 179
BROO-VALM-115.0-1 | 9068 | BROOMFIELD SUBSTATION | XCEL | VALMONT SWITCHYARD SUBSTATION | XCEL | 70065 | 70444 | Xcel Owned | BROO-VALM-115.0-1 | FACILITY |  | 1445 | 1590 | 1648 | 1766 | 288 | 317 | 328 | 352
BROO-VALM-115.0-1 | 9068 | BROOMFIELD SUBSTATION | XCEL | VALMONT SWITCHYARD SUBSTATION | XCEL | 70065 | 70444 | Xcel Owned | BROO-VALM-115.0-1 | Transmission Line | 9068 | 1445 | 1590 | 1648 | 1813 | 288 | 317 | 328 | 361
BROO-VALM-115.0-1 | 9068 | BROOMFIELD SUBSTATION | XCEL | VALMONT SWITCHYARD SUBSTATION | XCEL | 70065 | 70444 | Xcel Owned |  | LINE_TRAP | VALM | 1600 | 1600 | 1766 | 1766 | 319 | 319 | 352 | 352
GRLY-MONF-115.0-1 | 9115 | GREELEY SUBSTATION | XCEL | MONFORT SUBSTATION | XCEL | 70209 | 70290 | Xcel Owned | GRLY-MONF-115.0-1 | FACILITY |  | 1110 | 1200 | 1200 | 1200 | 221 | 239 | 239 | 239
GRLY-MONF-115.0-1 | 9115 | GREELEY SUBSTATION | XCEL | MONFORT SUBSTATION | XCEL | 70209 | 70290 | Xcel Owned | GRLY-MONF-115.0-1 | Transmission Line | 9115 | 1110 | 1221 | 1264 | 1391 | 221 | 243 | 252 | 277
GRLY-MONF-115.0-1 | 9115 | GREELEY SUBSTATION | XCEL | MONFORT SUBSTATION | XCEL | 70209 | 70290 | Xcel Owned | 9915 135Y | CURRENT_TRANSFORMER | MONF | 1200 | 1200 | 1200 | 1200 | 239 | 239 | 239 | 239
GRLY-MONF-115.0-1 | 9115 | GREELEY SUBSTATION | XCEL | MONFORT SUBSTATION | XCEL | 70209 | 70290 | Xcel Owned | 9915 135X | CURRENT_TRANSFORMER | MONF | 1200 | 1200 | 1200 | 1200 | 239 | 239 | 239 | 239
GRLY-MONF-115.0-1 | 9115 | GREELEY SUBSTATION | XCEL | MONFORT SUBSTATION | XCEL | 70209 | 70290 | Xcel Owned | 9115 246Y | CURRENT_TRANSFORMER | MONF | 1200 | 1200 | 1200 | 1200 | 239 | 239 | 239 | 239
GRLY-MONF-115.0-1 | 9115 | GREELEY SUBSTATION | XCEL | MONFORT SUBSTATION | XCEL | 70209 | 70290 | Xcel Owned |  | LINE_TRAP | MONF | 1200 | 1200 | 1325 | 1325 | 239 | 239 | 264 | 264
GODF-GRLY-115.0-1 | 9118 | GODFREY SUBSTATION | XCEL | GREELEY SUBSTATION | XCEL | 70202 | 70209 | Xcel Owned | GODF-GRLY-115.0-1 | FACILITY |  | 781 | 800 | 800 | 800 | 156 | 159 | 159 | 159
GODF-GRLY-115.0-1 | 9118 | GODFREY SUBSTATION | XCEL | GREELEY SUBSTATION | XCEL | 70202 | 70209 | Xcel Owned | GODF-GRLY-115.0-1 | Transmission Line | 9118 | 781 | 859 | 894 | 983 | 156 | 171 | 178 | 196
GODF-GRLY-115.0-1 | 9118 | GODFREY SUBSTATION | XCEL | GREELEY SUBSTATION | XCEL | 70202 | 70209 | Xcel Owned | 9118 135X | CURRENT_TRANSFORMER | GRLY | 800 | 800 | 800 | 800 | 159 | 159 | 159 | 159
GODF-GRLY-115.0-1 | 9118 | GODFREY SUBSTATION | XCEL | GREELEY SUBSTATION | XCEL | 70202 | 70209 | Xcel Owned | 9118 135Y | CURRENT_TRANSFORMER | GRLY | 800 | 800 | 800 | 800 | 159 | 159 | 159 | 159
GODF-GRLY-115.0-1 | 9118 | GODFREY SUBSTATION | XCEL | GREELEY SUBSTATION | XCEL | 70202 | 70209 | Xcel Owned | 9118 246X | CURRENT_TRANSFORMER | GRLY | 800 | 800 | 800 | 800 | 159 | 159 | 159 | 159
DTER-FEDC_TP-115.0-1 | 9122 | DENVER TERMINAL SUBSTATION | XCEL | FEDERAL CENTER TAP | XCEL | 70148 | 70173 | Xcel Owned | DTER-FEDC_TP-115.0-1 | FACILITY |  | 1200 | 1200 | 1200 | 1200 | 239 | 239 | 239 | 239
DTER-FEDC_TP-115.0-1 | 9122 | DENVER TERMINAL SUBSTATION | XCEL | FEDERAL CENTER TAP | XCEL | 70148 | 70173 | Xcel Owned | 9122 246Y 21Z2 | SECONDARY_CURRENT_LIMITATION | DTER | 1200 | 1200 | 1200 | 1200 | 239 | 239 | 239 | 239
DTER-FEDC_TP-115.0-1 | 9122 | DENVER TERMINAL SUBSTATION | XCEL | FEDERAL CENTER TAP | XCEL | 70148 | 70173 | Xcel Owned | 9122 246X PKG-BF | SECONDARY_CURRENT_LIMITATION | DTER | 1200 | 1200 | 1200 | 1200 | 239 | 239 | 239 | 239
DTER-FEDC_TP-115.0-1 | 9122 | DENVER TERMINAL SUBSTATION | XCEL | FEDERAL CENTER TAP | XCEL | 70148 | 70173 | Xcel Owned | 9122 246X 21ZP | SECONDARY_CURRENT_LIMITATION | DTER | 1200 | 1200 | 1200 | 1200 | 239 | 239 | 239 | 239
DTER-FEDC_TP-115.0-1 | 9122 | DENVER TERMINAL SUBSTATION | XCEL | FEDERAL CENTER TAP | XCEL | 70148 | 70173 | Xcel Owned | 9122 246Y 21Z1 | SECONDARY_CURRENT_LIMITATION | DTER | 1200 | 1200 | 1200 | 1200 | 239 | 239 | 239 | 239
DTER-FEDC_TP-115.0-1 | 9122 | DENVER TERMINAL SUBSTATION | XCEL | FEDERAL CENTER TAP | XCEL | 70148 | 70173 | Xcel Owned | 9122 246X 67GP | SECONDARY_CURRENT_LIMITATION | DTER | 1200 | 1200 | 1200 | 1200 | 239 | 239 | 239 | 239
DTER-FEDC_TP-115.0-1 | 9122 | DENVER TERMINAL SUBSTATION | XCEL | FEDERAL CENTER TAP | XCEL | 70148 | 70173 | Xcel Owned | 9122M | SWITCH | DTER | 1200 | 1549 | 1486 | 1780 | 239 | 309 | 296 | 355
FEDC_TP-QUAK_TP-115.0-1 | 9122 | FEDERAL CENTER TAP | XCEL | QUAKER TAP | XCEL | 70173 | 70342 | Xcel Owned | FEDC_TP-QUAK_TP-115.0-1 | FACILITY |  | 1280 | 1408 | 1280 | 1408 | 255 | 280 | 255 | 280
FEDC_TP-QUAK_TP-115.0-1 | 9122 | FEDERAL CENTER TAP | XCEL | QUAKER TAP | XCEL | 70173 | 70342 | Xcel Owned | FEDC_TP-QUAK_TP-115.0-1 | Transmission Line | 9122 | 1280 | 1408 | 1280 | 1408 | 255 | 280 | 255 | 280
LOOK-QUAK_TP-115.0-1 | 9122 | LOOKOUT SUBSTATION | XCEL | QUAKER TAP | XCEL | 70265 | 70342 | Xcel Owned | LOOK-QUAK_TP-115.0-1 | FACILITY |  | 1159 | 1200 | 1200 | 1200 | 231 | 239 | 239 | 239
LOOK-QUAK_TP-115.0-1 | 9122 | LOOKOUT SUBSTATION | XCEL | QUAKER TAP | XCEL | 70265 | 70342 | Xcel Owned | 1½" (AL 40) | BUSBAR_SECTION | LOOK | 1159 | 1367 | 1394 | 1563 | 231 | 272 | 278 | 311
LOOK-QUAK_TP-115.0-1 | 9122 | LOOKOUT SUBSTATION | XCEL | QUAKER TAP | XCEL | 70265 | 70342 | Xcel Owned | 9122 METER VAR | SECONDARY_CURRENT_LIMITATION | LOOK | 1200 | 1200 | 1200 | 1200 | 239 | 239 | 239 | 239
BRSS-BCP-115.0-1 | 9153 | BRUSH SWITCHING STATION | XCEL | Brush4 | FOREIGN | 2003 | 2004 | Xcel Owned | BRSS-BCP-115.0-1 | FACILITY |  | 402 | 402 | 402 | 402 | 80 | 80 | 80 | 80
BRSS-BCP-115.0-1 | 9153 | BRUSH SWITCHING STATION | XCEL | Brush4 | FOREIGN | 2003 | 2004 | Xcel Owned | Foreign Ratings | Foreign Ratings | BCP | 402 | 402 | 402 | 402 | 80 | 80 | 80 | 80
BRSS-BRNG-115.0-1 | 9155 | BRUSH SWITCHING STATION | XCEL | BRUSH CO-GEN / CPP SW. YARD | XCEL | 2003 | 2005 | Xcel Owned | BRSS-BRNG-115.0-1 | FACILITY |  | 800 | 800 | 800 | 800 | 159 | 159 | 159 | 159
BRSS-BRNG-115.0-1 | 9155 | BRUSH SWITCHING STATION | XCEL | BRUSH CO-GEN / CPP SW. YARD | XCEL | 2003 | 2005 | Xcel Owned | 9155_PK-1-3_115KV | SECONDARY_CURRENT_LIMITATION | BRNG | 800 | 800 | 800 | 800 | 159 | 159 | 159 | 159
BRSS-BRNG-115.0-1 | 9155 | BRUSH SWITCHING STATION | XCEL | BRUSH CO-GEN / CPP SW. YARD | XCEL | 2003 | 2005 | Xcel Owned | 9155_W/VAR_XDCR_115KV | SECONDARY_CURRENT_LIMITATION | BRNG | 800 | 800 | 800 | 800 | 159 | 159 | 159 | 159
BRSS-BRNG-115.0-1 | 9155 | BRUSH SWITCHING STATION | XCEL | BRUSH CO-GEN / CPP SW. YARD | XCEL | 2003 | 2005 | Xcel Owned | 9155_PK-1-2_115KV | SECONDARY_CURRENT_LIMITATION | BRNG | 800 | 800 | 800 | 800 | 159 | 159 | 159 | 159
BRSS-BRNG-115.0-1 | 9155 | BRUSH SWITCHING STATION | XCEL | BRUSH CO-GEN / CPP SW. YARD | XCEL | 2003 | 2005 | Xcel Owned | 9155_A_115KV | SECONDARY_CURRENT_LIMITATION | BRNG | 800 | 800 | 800 | 800 | 159 | 159 | 159 | 159
BRSS-BRNG-115.0-1 | 9155 | BRUSH SWITCHING STATION | XCEL | BRUSH CO-GEN / CPP SW. YARD | XCEL | 2003 | 2005 | Xcel Owned | 9155 MU | CURRENT_TRANSFORMER | BRNG | 800 | 800 | 800 | 800 | 159 | 159 | 159 | 159
BRSS-BRNG-115.0-1 | 9155 | BRUSH SWITCHING STATION | XCEL | BRUSH CO-GEN / CPP SW. YARD | XCEL | 2003 | 2005 | Xcel Owned | 9155_PK-1-1_115KV | SECONDARY_CURRENT_LIMITATION | BRNG | 800 | 800 | 800 | 800 | 159 | 159 | 159 | 159
BRSS-BRNG-115.0-2 | 9156 | BRUSH SWITCHING STATION | XCEL | BRUSH CO-GEN / CPP SW. YARD | XCEL | 2003 | 2150 | Xcel Owned | BRSS-BRNG-115.0-2 | FACILITY |  | 600 | 600 | 600 | 600 | 120 | 120 | 120 | 120
BRSS-BRNG-115.0-2 | 9156 | BRUSH SWITCHING STATION | XCEL | BRUSH CO-GEN / CPP SW. YARD | XCEL | 2003 | 2150 | Xcel Owned | 9156 MU | CURRENT_TRANSFORMER | BRNG | 600 | 600 | 600 | 600 | 120 | 120 | 120 | 120
EAST-SMOK-115.0-1 | 9174 | EAST SUBSTATION | XCEL | SMOKY HILL SUBSTATION | XCEL | 70162 | 70395 | Xcel Owned | EAST-SMOK-115.0-1 | FACILITY |  | 600 | 600 | 600 | 600 | 120 | 120 | 120 | 120
EAST-SMOK-115.0-1 | 9174 | EAST SUBSTATION | XCEL | SMOKY HILL SUBSTATION | XCEL | 70162 | 70395 | Xcel Owned | 9174 135Y | CURRENT_TRANSFORMER | EAST | 600 | 600 | 600 | 600 | 120 | 120 | 120 | 120
EAST-CHAM-115.0-1 | 9175 | EAST SUBSTATION | XCEL | CHAMBERS SUBSTATION | XCEL | 70162 | 70538 | Xcel Owned | EAST-CHAM-115.0-1 | FACILITY |  | 800 | 880 | 910 | 1001 | 159 | 175 | 181 | 199
EAST-CHAM-115.0-1 | 9175 | EAST SUBSTATION | XCEL | CHAMBERS SUBSTATION | XCEL | 70162 | 70538 | Xcel Owned | EAST-CHAM-115.0-1 | Transmission Line | 9175 | 800 | 880 | 910 | 1001 | 159 | 175 | 181 | 199
EAST-FITZ-115.0-1 | 9178 | EAST SUBSTATION | XCEL | FITZSIMONS SUBSTATION | XCEL | 70162 | 70537 | Xcel Owned | EAST-FITZ-115.0-1 | FACILITY |  | 600 | 728 | 743 | 827 | 120 | 145 | 148 | 165
EAST-FITZ-115.0-1 | 9178 | EAST SUBSTATION | XCEL | FITZSIMONS SUBSTATION | XCEL | 70162 | 70537 | Xcel Owned | 9178L | SWITCH | EAST | 600 | 775 | 743 | 890 | 120 | 154 | 148 | 177
EAST-FITZ-115.0-1 | 9178 | EAST SUBSTATION | XCEL | FITZSIMONS SUBSTATION | XCEL | 70162 | 70537 | Xcel Owned | 9178M | SWITCH | EAST | 600 | 775 | 743 | 890 | 120 | 154 | 148 | 177
EAST-FITZ-115.0-1 | 9178 | EAST SUBSTATION | XCEL | FITZSIMONS SUBSTATION | XCEL | 70162 | 70537 | Xcel Owned | 300 - 19 | BUSBAR_SECTION | EAST | 629 | 728 | 745 | 827 | 125 | 145 | 148 | 165
FITZ-CHAM-115.0-1 | 9178 | FITZSIMONS SUBSTATION | XCEL | CHAMBERS SUBSTATION | XCEL | 70537 | 70538 | Xcel Owned | FITZ-CHAM-115.0-1 | FACILITY |  | 800 | 880 | 910 | 1001 | 159 | 175 | 181 | 199
FITZ-CHAM-115.0-1 | 9178 | FITZSIMONS SUBSTATION | XCEL | CHAMBERS SUBSTATION | XCEL | 70537 | 70538 | Xcel Owned | FITZ-CHAM-115.0-1 | Transmission Line | 9178 | 800 | 880 | 910 | 1001 | 159 | 175 | 181 | 199
CLIM-ROBI-115.0-2 | 9188 | CLIMAX SUBSTATION | XCEL | ROBINSON RACK | XCEL | 70114 | 70364 | Xcel Owned | CLIM-ROBI-115.0-2 | FACILITY |  | 418 | 460 | 475 | 523 | 83 | 92 | 95 | 104
CLIM-ROBI-115.0-2 | 9188 | CLIMAX SUBSTATION | XCEL | ROBINSON RACK | XCEL | 70114 | 70364 | Xcel Owned | CLIM-ROBI-115.0-2 | Transmission Line | 9188 | 418 | 460 | 475 | 523 | 83 | 92 | 95 | 104
ROBI-SUMM-115.0-1 | 9188 | ROBINSON RACK | XCEL | SUMMIT SUBSTATION | XCEL | 70389 | 70418 | Xcel Owned | ROBI-SUMM-115.0-1 | FACILITY |  | 418 | 460 | 475 | 523 | 83 | 92 | 95 | 104
ROBI-SUMM-115.0-1 | 9188 | ROBINSON RACK | XCEL | SUMMIT SUBSTATION | XCEL | 70389 | 70418 | Xcel Owned | ROBI-SUMM-115.0-1 | Transmission Line | 9188 | 418 | 460 | 475 | 523 | 83 | 92 | 95 | 104
BHYD-NCAR-115.0-1 | 9205 | BOULDER CANYON SWYD | XCEL | NCAR SUBSTATION | XCEL | 70058 | 70295 | Xcel Owned | BHYD-NCAR-115.0-1 | FACILITY |  | 808 | 889 | 909 | 1000 | 161 | 177 | 181 | 199
BHYD-NCAR-115.0-1 | 9205 | BOULDER CANYON SWYD | XCEL | NCAR SUBSTATION | XCEL | 70058 | 70295 | Xcel Owned | BHYD-NCAR-115.0-1 | Transmission Line | 9205 | 808 | 889 | 909 | 1000 | 161 | 177 | 181 | 199
ELDO-NCAR-115.0-1 | 9205 | ELDORADO SPRINGS SUBSTATION | XCEL | NCAR SUBSTATION | XCEL | 70164 | 70295 | Xcel Owned | ELDO-NCAR-115.0-1 | FACILITY |  | 800 | 800 | 800 | 800 | 159 | 159 | 159 | 159
ELDO-NCAR-115.0-1 | 9205 | ELDORADO SPRINGS SUBSTATION | XCEL | NCAR SUBSTATION | XCEL | 70164 | 70295 | Xcel Owned | 9205 METER VAR | SECONDARY_CURRENT_LIMITATION | ELDO | 800 | 800 | 800 | 800 | 159 | 159 | 159 | 159
BHYD-SUNS-115.0-1 | 9216 | BOULDER CANYON SWYD | XCEL | SUNSHINE CANYON SUBSTATION | XCEL | 70058 | 70423 | Xcel Owned | BHYD-SUNS-115.0-1 | FACILITY |  | 627 | 689 | 712 | 783 | 125 | 137 | 142 | 156
BHYD-SUNS-115.0-1 | 9216 | BOULDER CANYON SWYD | XCEL | SUNSHINE CANYON SUBSTATION | XCEL | 70058 | 70423 | Xcel Owned | Merlin | BUSBAR_SECTION | SUNS | 627 | 689 | 712 | 783 | 125 | 137 | 142 | 156
BTER-SUNS-115.0-1 | 9216 | BOULDER TERMINAL SUBSTATION | XCEL | SUNSHINE CANYON SUBSTATION | XCEL | 70059 | 70423 | Xcel Owned | BTER-SUNS-115.0-1 | FACILITY |  | 627 | 689 | 712 | 783 | 125 | 137 | 142 | 156
BTER-SUNS-115.0-1 | 9216 | BOULDER TERMINAL SUBSTATION | XCEL | SUNSHINE CANYON SUBSTATION | XCEL | 70059 | 70423 | Xcel Owned | Merlin | BUSBAR_SECTION | SUNS | 627 | 689 | 712 | 783 | 125 | 137 | 142 | 156
CLIM-LEAD_TP1-115.0-1 | 9254 | CLIMAX SUBSTATION | XCEL | LEADVILLE TAP 1 | XCEL | 70114 | 2114 | Xcel Owned | CLIM-LEAD_TP1-115.0-1 | FACILITY |  | 370 | 407 | 420 | 462 | 74 | 81 | 84 | 92
CLIM-LEAD_TP1-115.0-1 | 9254 | CLIMAX SUBSTATION | XCEL | LEADVILLE TAP 1 | XCEL | 70114 | 2114 | Xcel Owned | CLIM-LEAD_TP1-115.0-1 | Transmission Line | 9254 | 370 | 407 | 420 | 462 | 74 | 81 | 84 | 92
LEAD_TP1-LEAD-115.0-1 | 9254 | LEADVILLE TAP 1 | XCEL | LEADVILLE SUBSTATION | XCEL | 2114 | 70257 | Xcel Owned | LEAD_TP1-LEAD-115.0-1 | FACILITY |  | 477 | 554 | 567 | 629 | 95 | 110 | 113 | 125
LEAD_TP1-LEAD-115.0-1 | 9254 | LEADVILLE TAP 1 | XCEL | LEADVILLE SUBSTATION | XCEL | 2114 | 70257 | Xcel Owned | 4/0 - 7 | BUSBAR_SECTION | LEAD | 477 | 554 | 567 | 629 | 95 | 110 | 113 | 125
LEAD_TP1-MALT-115.0-1 | 9254 | LEADVILLE TAP 1 | XCEL | MALTA SUBSTATION | XCEL | 2114 | 70273 | Xcel Owned | LEAD_TP1-MALT-115.0-1 | FACILITY |  | 648 | 713 | 737 | 811 | 129 | 142 | 147 | 162
LEAD_TP1-MALT-115.0-1 | 9254 | LEADVILLE TAP 1 | XCEL | MALTA SUBSTATION | XCEL | 2114 | 70273 | Xcel Owned | LEAD_TP1-MALT-115.0-1 | Transmission Line | 9254 | 648 | 713 | 737 | 811 | 129 | 142 | 147 | 162
BUVI_TP-RAYL-115.0-1 | 9255 | BUENA VISTA TAP | XCEL | RAY LEWIS | XCEL | 70056 | 70312 | Xcel Owned | BUVI_TP-RAYL-115.0-1 | FACILITY | [9 empty] | See Ambient Adjusted Ratings Section
MALT-TWLA_TP-115.0-1 | 9255 | MALTA SUBSTATION | XCEL | TWIN LAKES TAP | XCEL | 70273 | 70435 | Xcel Owned | MALT-TWLA_TP-115.0-1 | FACILITY | [9 empty] | See Ambient Adjusted Ratings Section
OTER_TP-BUVI_TP-115.0-1 | 9255 | OTERO PUMPING STATION | XCEL | BUENA VISTA TAP | XCEL | 70304 | 70056 | Xcel Owned | OTER_TP-BUVI_TP-115.0-1 | FACILITY | [9 empty] | See Ambient Adjusted Ratings Section
RAYL-PONC-115.0-1 | 9255 | RAY LEWIS | XCEL | PONCHA JUNCTION SUBSTATION | XCEL | 70312 | 70327 | Xcel Owned | RAYL-PONC-115.0-1 | FACILITY | [9 empty] | See Ambient Adjusted Ratings Section
TWLA_TP-OTER_TP-115.0-1 | 9255 | TWIN LAKES TAP | XCEL | OTERO PUMPING STATION | XCEL | 70435 | 70304 | Xcel Owned | TWLA_TP-OTER_TP-115.0-1 | FACILITY | [9 empty] | See Ambient Adjusted Ratings Section
HOPK-BASA-115.0-1 | 9256 | HOPKINS SUBSTATION | XCEL | BASALT SUBSTATION | XCEL | 70231 | 79003 | Xcel Owned | HOPK-BASA-115.0-1 | FACILITY |  | 418 | 460 | 474 | 521 | 83 | 92 | 94 | 104
HOPK-BASA-115.0-1 | 9256 | HOPKINS SUBSTATION | XCEL | BASALT SUBSTATION | XCEL | 70231 | 79003 | Xcel Owned | HOPK-BASA-115.0-1 | Transmission Line | 9256 | 418 | 460 | 474 | 521 | 83 | 92 | 94 | 104
CLIM-ROBI-115.0-1 | 9257 | CLIMAX SUBSTATION | XCEL | ROBINSON RACK | XCEL | 70114 | 70389 | Xcel Owned | CLIM-ROBI-115.0-1 | FACILITY |  | 370 | 400 | 400 | 400 | 74 | 80 | 80 | 80
CLIM-ROBI-115.0-1 | 9257 | CLIMAX SUBSTATION | XCEL | ROBINSON RACK | XCEL | 70114 | 70389 | Xcel Owned | CLIM-ROBI-115.0-1 | Transmission Line | 9257 | 370 | 407 | 420 | 462 | 74 | 81 | 84 | 92
CLIM-ROBI-115.0-1 | 9257 | CLIMAX SUBSTATION | XCEL | ROBINSON RACK | XCEL | 70114 | 70389 | Xcel Owned | 9257 METER VAR | SECONDARY_CURRENT_LIMITATION | CLIM | 400 | 400 | 400 | 400 | 80 | 80 | 80 | 80
LEAD-MALT-115.0-1 | 9257 | LEADVILLE SUBSTATION | XCEL | MALTA SUBSTATION | XCEL | 70258 | 70273 | Xcel Owned | LEAD-MALT-115.0-1 | FACILITY |  | 477 | 554 | 567 | 629 | 95 | 110 | 113 | 125
LEAD-MALT-115.0-1 | 9257 | LEADVILLE SUBSTATION | XCEL | MALTA SUBSTATION | XCEL | 70258 | 70273 | Xcel Owned | 4/0 - 7 | BUSBAR_SECTION | LEAD | 477 | 554 | 567 | 629 | 95 | 110 | 113 | 125
LEAD_TP2-LEAD-115.0-1 | 9257 | LEADVILLE TAP 2 | XCEL | LEADVILLE SUBSTATION | XCEL | 2155 | 70257 | Xcel Owned | LEAD_TP2-LEAD-115.0-1 | FACILITY |  | 477 | 554 | 567 | 629 | 95 | 110 | 113 | 125
LEAD_TP2-LEAD-115.0-1 | 9257 | LEADVILLE TAP 2 | XCEL | LEADVILLE SUBSTATION | XCEL | 2155 | 70257 | Xcel Owned | 4/0 - 7 | BUSBAR_SECTION | LEAD | 477 | 554 | 567 | 629 | 95 | 110 | 113 | 125
LEAD_TP2-LEAD-115.0-2 | 9257 | LEADVILLE TAP 2 | XCEL | LEADVILLE SUBSTATION | XCEL | 2155 | 70258 | Xcel Owned | LEAD_TP2-LEAD-115.0-2 | FACILITY |  | 477 | 554 | 567 | 629 | 95 | 110 | 113 | 125
LEAD_TP2-LEAD-115.0-2 | 9257 | LEADVILLE TAP 2 | XCEL | LEADVILLE SUBSTATION | XCEL | 2155 | 70258 | Xcel Owned | 4/0 - 7 | BUSBAR_SECTION | LEAD | 477 | 554 | 567 | 629 | 95 | 110 | 113 | 125
LEAD_TP2-ROBI-115.0-1 | 9257 | LEADVILLE TAP 2 | XCEL | ROBINSON RACK | XCEL | 2155 | 70364 | Xcel Owned | LEAD_TP2-ROBI-115.0-1 | FACILITY |  | 418 | 460 | 475 | 523 | 83 | 92 | 95 | 104
LEAD_TP2-ROBI-115.0-1 | 9257 | LEADVILLE TAP 2 | XCEL | ROBINSON RACK | XCEL | 2155 | 70364 | Xcel Owned | LEAD_TP2-ROBI-115.0-1 | Transmission Line | 9257 | 418 | 460 | 475 | 523 | 83 | 92 | 95 | 104
GILM-ROBI-115.0-1 | 9257 | GILMAN SUBSTATION | XCEL | ROBINSON RACK | XCEL | 70199 | 70364 | Xcel Owned | GILM-ROBI-115.0-1 | FACILITY |  | 290 | 319 | 382 | 420 | 58 | 64 | 76 | 84
GILM-ROBI-115.0-1 | 9257 | GILMAN SUBSTATION | XCEL | ROBINSON RACK | XCEL | 70199 | 70364 | Xcel Owned | GILM-ROBI-115.0-1 | Transmission Line | 9257 | 290 | 319 | 382 | 420 | 58 | 64 | 76 | 84
LEET-SAND-115.0-1 | 9286 | LEETSDALE SUBSTATION | XCEL | SANDOWN SUBSTATION | XCEL | 70259 | 70377 | Xcel Owned | LEET-SAND-115.0-1 | FACILITY |  | 1213 | 1334 | 1213 | 1334 | 242 | 266 | 242 | 266
LEET-SAND-115.0-1 | 9286 | LEETSDALE SUBSTATION | XCEL | SANDOWN SUBSTATION | XCEL | 70259 | 70377 | Xcel Owned | LEET-SAND-115.0-1 | Transmission Line | 9286 | 1213 | 1334 | 1213 | 1334 | 242 | 266 | 242 | 266
NORT-SAND-115.0-1 | 9311 | NORTH SUBSTATION | XCEL | SANDOWN SUBSTATION | XCEL | 70298 | 70377 | Xcel Owned | NORT-SAND-115.0-1 | FACILITY |  | 959 | 960 | 960 | 960 | 191 | 191 | 191 | 191
NORT-SAND-115.0-1 | 9311 | NORTH SUBSTATION | XCEL | SANDOWN SUBSTATION | XCEL | 70298 | 70377 | Xcel Owned | Grosbeak | BUSBAR_SECTION | NORT | 959 | 1055 | 1091 | 1200 | 191 | 210 | 217 | 239
NORT-SAND-115.0-1 | 9311 | NORTH SUBSTATION | XCEL | SANDOWN SUBSTATION | XCEL | 70298 | 70377 | Xcel Owned | NORT-SAND-115.0-1 | Transmission Line | 9311 | 959 | 1055 | 1092 | 1201 | 191 | 210 | 218 | 239
NORT-SAND-115.0-1 | 9311 | NORTH SUBSTATION | XCEL | SANDOWN SUBSTATION | XCEL | 70298 | 70377 | Xcel Owned | 9311 A 67GP | SECONDARY_CURRENT_LIMITATION | SAND | 960 | 960 | 960 | 960 | 191 | 191 | 191 | 191
NORT-SAND-115.0-1 | 9311 | NORTH SUBSTATION | XCEL | SANDOWN SUBSTATION | XCEL | 70298 | 70377 | Xcel Owned | 9311 B 67GB | SECONDARY_CURRENT_LIMITATION | SAND | 960 | 960 | 960 | 960 | 191 | 191 | 191 | 191
NORT-SAND-115.0-1 | 9311 | NORTH SUBSTATION | XCEL | SANDOWN SUBSTATION | XCEL | 70298 | 70377 | Xcel Owned | 9311_67GS | SECONDARY_CURRENT_LIMITATION | NORT | 960 | 960 | 960 | 960 | 191 | 191 | 191 | 191
NORT-SAND-115.0-1 | 9311 | NORTH SUBSTATION | XCEL | SANDOWN SUBSTATION | XCEL | 70298 | 70377 | Xcel Owned | 9311 _67GP | SECONDARY_CURRENT_LIMITATION | NORT | 960 | 960 | 960 | 960 | 191 | 191 | 191 | 191
ARAP-ARLQ_TP-115.0-1 | 9332 | ARAPAHOE SUBSTATION | XCEL | AIR LIQUIDE TAP | XCEL | 70036 | 70531 | Xcel Owned | ARAP-ARLQ_TP-115.0-1 | FACILITY |  | 600 | 775 | 743 | 890 | 120 | 154 | 148 | 177
ARAP-ARLQ_TP-115.0-1 | 9332 | ARAPAHOE SUBSTATION | XCEL | AIR LIQUIDE TAP | XCEL | 70036 | 70531 | Xcel Owned | 9332M | SWITCH | ARAP | 600 | 775 | 743 | 890 | 120 | 154 | 148 | 177
GRAY-SOUT-115.0-1 | 9332 | GRAY STREET SUBSTATION | XCEL | SOUTH SUBSTATION | XCEL | 70208 | 70402 | Xcel Owned | GRAY-SOUT-115.0-1 | FACILITY |  | 600 | 775 | 743 | 890 | 120 | 154 | 148 | 177
GRAY-SOUT-115.0-1 | 9332 | GRAY STREET SUBSTATION | XCEL | SOUTH SUBSTATION | XCEL | 70208 | 70402 | Xcel Owned | 9332-2G | SWITCH | SOUT | 600 | 775 | 743 | 890 | 120 | 154 | 148 | 177
GRAY-SOUT-115.0-1 | 9332 | GRAY STREET SUBSTATION | XCEL | SOUTH SUBSTATION | XCEL | 70208 | 70402 | Xcel Owned | 9332M | SWITCH | GRAY | 600 | 775 | 743 | 890 | 120 | 154 | 148 | 177
GRAY-SOUT-115.0-1 | 9332 | GRAY STREET SUBSTATION | XCEL | SOUTH SUBSTATION | XCEL | 70208 | 70402 | Xcel Owned | 9332L | SWITCH | GRAY | 600 | 775 | 743 | 890 | 120 | 154 | 148 | 177
SOUT-ARLQ_TP-115.0-1 | 9332 | SOUTH SUBSTATION | XCEL | AIR LIQUIDE TAP | XCEL | 70402 | 70531 | Xcel Owned | SOUT-ARLQ_TP-115.0-1 | FACILITY |  | 600 | 775 | 743 | 890 | 120 | 154 | 148 | 177
SOUT-ARLQ_TP-115.0-1 | 9332 | SOUTH SUBSTATION | XCEL | AIR LIQUIDE TAP | XCEL | 70402 | 70531 | Xcel Owned | 9332-1G | SWITCH | SOUT | 600 | 775 | 743 | 890 | 120 | 154 | 148 | 177
ARAP-ENGL-115.0-1 | 9333 | ARAPAHOE SUBSTATION | XCEL | ENGLEWOOD SUBSTATION | XCEL | 70037 | 70167 | Xcel Owned | ARAP-ENGL-115.0-1 | FACILITY |  | 640 | 705 | 728 | 800 | 128 | 140 | 145 | 159
ARAP-ENGL-115.0-1 | 9333 | ARAPAHOE SUBSTATION | XCEL | ENGLEWOOD SUBSTATION | XCEL | 70037 | 70167 | Xcel Owned | Linnet | BUSBAR_SECTION | ARAP | 640 | 705 | 728 | 800 | 128 | 140 | 145 | 159
ARAP-SHER-115.0-1 | 9334 | ARAPAHOE SUBSTATION | XCEL | SHERIDAN SUBSTATION | XCEL | 70036 | 70384 | Xcel Owned | ARAP-SHER-115.0-1 | FACILITY |  | 640 | 705 | 728 | 800 | 128 | 140 | 145 | 159
ARAP-SHER-115.0-1 | 9334 | ARAPAHOE SUBSTATION | XCEL | SHERIDAN SUBSTATION | XCEL | 70036 | 70384 | Xcel Owned | Linnet | BUSBAR_SECTION | ARAP | 640 | 705 | 728 | 800 | 128 | 140 | 145 | 159
ARAP-SOUT_TP-115.0-1 | 9335 | ARAPAHOE SUBSTATION | XCEL | SOUTH TAP | XCEL | 70037 | 70398 | Xcel Owned | ARAP-SOUT_TP-115.0-1 | FACILITY |  | 775 | 853 | 843 | 927 | 154 | 170 | 168 | 185
ARAP-SOUT_TP-115.0-1 | 9335 | ARAPAHOE SUBSTATION | XCEL | SOUTH TAP | XCEL | 70037 | 70398 | Xcel Owned | ARAP-SOUT_TP-115.0-1 | Transmission Line | 9335 | 775 | 853 | 843 | 927 | 154 | 170 | 168 | 185
BANC-SOUT_TP-115.0-1 | 9335 | BANCROFT SUBSTATION | XCEL | SOUTH TAP | XCEL | 70045 | 70398 | Xcel Owned | BANC-SOUT_TP-115.0-1 | FACILITY |  | 800 | 880 | 910 | 1001 | 159 | 175 | 181 | 199
BANC-SOUT_TP-115.0-1 | 9335 | BANCROFT SUBSTATION | XCEL | SOUTH TAP | XCEL | 70045 | 70398 | Xcel Owned | BANC-SOUT_TP-115.0-1 | Transmission Line | 9335 | 800 | 880 | 910 | 1001 | 159 | 175 | 181 | 199
SOUT_TP-SOUT-115.0-1 | 9335 | SOUTH TAP | XCEL | SOUTH SUBSTATION | XCEL | 70398 | 70401 | Xcel Owned | SOUT_TP-SOUT-115.0-1 | FACILITY |  | 600 | 775 | 743 | 890 | 120 | 154 | 148 | 177
SOUT_TP-SOUT-115.0-1 | 9335 | SOUTH TAP | XCEL | SOUTH SUBSTATION | XCEL | 70398 | 70401 | Xcel Owned | 9335 | SWITCH | SOUT | 600 | 775 | 743 | 890 | 120 | 154 | 148 | 177
ARAP-ENGL_TP-115.0-1 | 9336 | ARAPAHOE SUBSTATION | XCEL | ENGLEWOOD TAP | XCEL | 70037 | 70165 | Xcel Owned | ARAP-ENGL_TP-115.0-1 | FACILITY |  | 799 | 879 | 909 | 999 | 159 | 175 | 181 | 199
ARAP-ENGL_TP-115.0-1 | 9336 | ARAPAHOE SUBSTATION | XCEL | ENGLEWOOD TAP | XCEL | 70037 | 70165 | Xcel Owned | Hawk | BUSBAR_SECTION | ARAP | 799 | 879 | 909 | 999 | 159 | 175 | 181 | 199
ENGL_TP-LITT-115.0-1 | 9336 | ENGLEWOOD TAP | XCEL | LITTLETON SUBSTATION | XCEL | 70165 | 70263 | Xcel Owned | ENGL_TP-LITT-115.0-1 | FACILITY |  | 800 | 880 | 910 | 1001 | 159 | 175 | 181 | 199
ENGL_TP-LITT-115.0-1 | 9336 | ENGLEWOOD TAP | XCEL | LITTLETON SUBSTATION | XCEL | 70165 | 70263 | Xcel Owned | ENGL_TP-LITT-115.0-1 | Transmission Line | 9336 | 800 | 880 | 910 | 1001 | 159 | 175 | 181 | 199
LITT-WATE_TP-115.0-1 | 9336 | LITTLETON SUBSTATION | XCEL | Waterton Tap 9336 | XCEL | 70263 | 70462 | Xcel Owned | LITT-WATE_TP-115.0-1 | FACILITY |  | 800 | 880 | 910 | 1001 | 159 | 175 | 181 | 199
LITT-WATE_TP-115.0-1 | 9336 | LITTLETON SUBSTATION | XCEL | Waterton Tap 9336 | XCEL | 70263 | 70462 | Xcel Owned | LITT-WATE_TP-115.0-1 | Transmission Line | 9336 | 800 | 880 | 910 | 1001 | 159 | 175 | 181 | 199
WATE-WATE_TP-115.0-1 | 9336 | WATERTON SUBSTATION | XCEL | Waterton Tap 9336 | XCEL | 70463 | 70462 | Xcel Owned | WATE-WATE_TP-115.0-1 | FACILITY |  | 695 | 765 | 799 | 879 | 139 | 152 | 159 | 175
WATE-WATE_TP-115.0-1 | 9336 | WATERTON SUBSTATION | XCEL | Waterton Tap 9336 | XCEL | 70463 | 70462 | Xcel Owned | 300 - 19 | BUSBAR_SECTION | WATE | 695 | 765 | 799 | 879 | 139 | 152 | 159 | 175
DEER-MART_TP-115.0-1 | 9337 | DEER CREEK SUBSTATION | XCEL | MARTIN TAP | XCEL | 70142 | 70484 | Xcel Owned | DEER-MART_TP-115.0-1 | FACILITY |  | 1262 | 1389 | 1438 | 1582 | 251 | 277 | 286 | 315
DEER-MART_TP-115.0-1 | 9337 | DEER CREEK SUBSTATION | XCEL | MARTIN TAP | XCEL | 70142 | 70484 | Xcel Owned | DEER-MART_TP-115.0-1 | Transmission Line | 9337 | 1262 | 1389 | 1438 | 1582 | 251 | 277 | 286 | 315
DEER-SODA-115.0-1 | 9337 | DEER CREEK SUBSTATION | XCEL | SODA LAKES SUBSTATION | XCEL | 70142 | 70400 | Xcel Owned | DEER-SODA-115.0-1 | FACILITY |  | 600 | 775 | 743 | 890 | 120 | 154 | 148 | 177
DEER-SODA-115.0-1 | 9337 | DEER CREEK SUBSTATION | XCEL | SODA LAKES SUBSTATION | XCEL | 70142 | 70400 | Xcel Owned | 9337L | SWITCH | SODA | 600 | 775 | 743 | 890 | 120 | 154 | 148 | 177
WATE-MART_TP-115.0-1 | 9337 | WATERTON SUBSTATION | XCEL | MARTIN TAP | XCEL | 70463 | 70484 | Xcel Owned | WATE-MART_TP-115.0-1 | FACILITY |  | 638 | 702 | 725 | 798 | 127 | 140 | 144 | 159
WATE-MART_TP-115.0-1 | 9337 | WATERTON SUBSTATION | XCEL | MARTIN TAP | XCEL | 70463 | 70484 | Xcel Owned | Linnet | BUSBAR_SECTION | WATE | 638 | 702 | 725 | 798 | 127 | 140 | 144 | 159
ARAP-UNIV-115.0-1 | 9338 | ARAPAHOE SUBSTATION | XCEL | UNIVERSITY SUBSTATION | XCEL | 70036 | 70441 | Xcel Owned | ARAP-UNIV-115.0-1 | FACILITY |  | 773 | 773 | 773 | 773 | 154 | 154 | 154 | 154
ARAP-UNIV-115.0-1 | 9338 | ARAPAHOE SUBSTATION | XCEL | UNIVERSITY SUBSTATION | XCEL | 70036 | 70441 | Xcel Owned | ARAP-UNIV-115.0-1 | Transmission Line | 9338 | 773 | 773 | 773 | 773 | 154 | 154 | 154 | 154
LEET-UNIV-115.0-1 | 9338 | LEETSDALE SUBSTATION | XCEL | UNIVERSITY SUBSTATION | XCEL | 70259 | 70441 | Xcel Owned | LEET-UNIV-115.0-1 | FACILITY |  | 957 | 1052 | 1088 | 1197 | 191 | 210 | 217 | 238
LEET-UNIV-115.0-1 | 9338 | LEETSDALE SUBSTATION | XCEL | UNIVERSITY SUBSTATION | XCEL | 70259 | 70441 | Xcel Owned | LEET-UNIV-115.0-1 | Transmission Line | 9338 | 957 | 1052 | 1088 | 1197 | 191 | 210 | 217 | 238
BRSS-BEAV-115.0-1 | 9406 | BRUSH SWITCHING STATION | XCEL | BEAVER CREEK EAST SUBSTATION | XCEL | 70005 | 70397 | Xcel Owned | BRSS-BEAV-115.0-1 | FACILITY |  | 1441 | 1585 | 1641 | 1800 | 287 | 316 | 327 | 359
BRSS-BEAV-115.0-1 | 9406 | BRUSH SWITCHING STATION | XCEL | BEAVER CREEK EAST SUBSTATION | XCEL | 70005 | 70397 | Xcel Owned | Narcissus | BUSBAR_SECTION | BEAV | 1441 | 1585 | 1641 | 1805 | 287 | 316 | 327 | 360
BRSS-BEAV-115.0-1 | 9406 | BRUSH SWITCHING STATION | XCEL | BEAVER CREEK EAST SUBSTATION | XCEL | 70005 | 70397 | Xcel Owned | Narcissus | BUSBAR_SECTION | BRSS | 1441 | 1586 | 1642 | 1806 | 287 | 316 | 327 | 360
BRSS-BEAV-115.0-1 | 9406 | BRUSH SWITCHING STATION | XCEL | BEAVER CREEK EAST SUBSTATION | XCEL | 70005 | 70397 | Xcel Owned | 9406-C AMP | SECONDARY_CURRENT_LIMITATION | BRSS | 1800 | 1800 | 1800 | 1800 | 359 | 359 | 359 | 359
BRSS-BEAV-115.0-2 | 9407 | BRUSH SWITCHING STATION | XCEL | BEAVER CREEK EAST SUBSTATION | XCEL | 70005 | 70397 | Xcel Owned | BRSS-BEAV-115.0-2 | FACILITY |  | 1600 | 1600 | 1600 | 1600 | 319 | 319 | 319 | 319
BRSS-BEAV-115.0-2 | 9407 | BRUSH SWITCHING STATION | XCEL | BEAVER CREEK EAST SUBSTATION | XCEL | 70005 | 70397 | Xcel Owned | 9400 | BREAKER | BEAV | 1600 | 1600 | 1600 | 1600 | 319 | 319 | 319 | 319
ARGO-ARGO_TP-115.0-1 | 9413 | ARGO SUBSTATION | XCEL | ARGO | XCEL | 70039 | 2119 | Xcel Owned | ARGO-ARGO_TP-115.0-1 | FACILITY |  | 2400 | 2400 | 2400 | 2400 | 478 | 478 | 478 | 478
ARGO-ARGO_TP-115.0-1 | 9413 | ARGO SUBSTATION | XCEL | ARGO | XCEL | 70039 | 2119 | Xcel Owned | 9413 135Y | CURRENT_TRANSFORMER | ARGO | 2400 | 2400 | 2400 | 2400 | 478 | 478 | 478 | 478
ARGO-ARGO_TP-115.0-1 | 9413 | ARGO SUBSTATION | XCEL | ARGO | XCEL | 70039 | 2119 | Xcel Owned | 9413 PK | SECONDARY_CURRENT_LIMITATION | ARGO | 2400 | 2400 | 2400 | 2400 | 478 | 478 | 478 | 478
ARGO-ARGO_TP-115.0-1 | 9413 | ARGO SUBSTATION | XCEL | ARGO | XCEL | 70039 | 2119 | Xcel Owned | 9413 135X | CURRENT_TRANSFORMER | ARGO | 2400 | 2400 | 2400 | 2400 | 478 | 478 | 478 | 478
ARGO_TP-CHER_TP-115.0-1 | 9413 | ARGO | XCEL | CHEROKEE SW YARD | XCEL | 2119 | 2112 | Xcel Owned | ARGO_TP-CHER_TP-115.0-1 | FACILITY |  | 2393 | 2632 | 2742 | 2997 | 477 | 524 | 546 | 597
ARGO_TP-CHER_TP-115.0-1 | 9413 | ARGO | XCEL | CHEROKEE SW YARD | XCEL | 2119 | 2112 | Xcel Owned | ARGO_TP-CHER_TP-115.0-1 | Transmission Line | 9413 | 2393 | 2632 | 2742 | 2997 | 477 | 524 | 546 | 597
CHER_TP-CHER-115.0-1 | 9413 | CHEROKEE SW YARD | XCEL | CHEROKEE SWITCHYARD SUBSTATION | XCEL | 2112 | 70108 | Xcel Owned | CHER_TP-CHER-115.0-1 | FACILITY |  | 2373 | 2400 | 2400 | 2400 | 473 | 478 | 478 | 478
CHER_TP-CHER-115.0-1 | 9413 | CHEROKEE SW YARD | XCEL | CHEROKEE SWITCHYARD SUBSTATION | XCEL | 2112 | 70108 | Xcel Owned | Curlew | BUSBAR_SECTION | CHER | 2373 | 2610 | 2703 | 2973 | 473 | 520 | 538 | 592
CHER_TP-CHER-115.0-1 | 9413 | CHEROKEE SW YARD | XCEL | CHEROKEE SWITCHYARD SUBSTATION | XCEL | 2112 | 70108 | Xcel Owned | 9556 135Y | CURRENT_TRANSFORMER | CHER | 2400 | 2400 | 2400 | 2400 | 478 | 478 | 478 | 478
CHER_TP-CHER-115.0-1 | 9413 | CHEROKEE SW YARD | XCEL | CHEROKEE SWITCHYARD SUBSTATION | XCEL | 2112 | 70108 | Xcel Owned | 9413 135Y | CURRENT_TRANSFORMER | CHER | 2400 | 2400 | 2400 | 2400 | 478 | 478 | 478 | 478
CHER_TP-CHER-115.0-1 | 9413 | CHEROKEE SW YARD | XCEL | CHEROKEE SWITCHYARD SUBSTATION | XCEL | 2112 | 70108 | Xcel Owned | 9413 246Y | CURRENT_TRANSFORMER | CHER | 2400 | 2400 | 2400 | 2400 | 478 | 478 | 478 | 478
CHER_TP-CHER-115.0-1 | 9413 | CHEROKEE SW YARD | XCEL | CHEROKEE SWITCHYARD SUBSTATION | XCEL | 2112 | 70108 | Xcel Owned | 9556 246X | CURRENT_TRANSFORMER | CHER | 2400 | 2400 | 2400 | 2400 | 478 | 478 | 478 | 478
CHER_TP-CHER-115.0-1 | 9413 | CHEROKEE SW YARD | XCEL | CHEROKEE SWITCHYARD SUBSTATION | XCEL | 2112 | 70108 | Xcel Owned | 9556 246Y | CURRENT_TRANSFORMER | CHER | 2400 | 2400 | 2400 | 2400 | 478 | 478 | 478 | 478
CHER_TP-CHER-115.0-1 | 9413 | CHEROKEE SW YARD | XCEL | CHEROKEE SWITCHYARD SUBSTATION | XCEL | 2112 | 70108 | Xcel Owned | 9413 246X | CURRENT_TRANSFORMER | CHER | 2400 | 2400 | 2400 | 2400 | 478 | 478 | 478 | 478
CHER_TP-CHER-115.0-1 | 9413 | CHEROKEE SW YARD | XCEL | CHEROKEE SWITCHYARD SUBSTATION | XCEL | 2112 | 70108 | Xcel Owned | 9556 135X | CURRENT_TRANSFORMER | CHER | 2400 | 2400 | 2400 | 2400 | 478 | 478 | 478 | 478
CHER_TP-CHER-115.0-1 | 9413 | CHEROKEE SW YARD | XCEL | CHEROKEE SWITCHYARD SUBSTATION | XCEL | 2112 | 70108 | Xcel Owned | 9413 135X | CURRENT_TRANSFORMER | CHER | 2400 | 2400 | 2400 | 2400 | 478 | 478 | 478 | 478
SLVA-BLPK-115.0-1 | 9431 | SAN LUIS VALLEY SUBSTATION | XCEL | BLANCA PEAK SUBSTATION | XCEL | 70374 | 70937 | Xcel Owned | SLVA-BLPK-115.0-1 | FACILITY |  | 300 | 300 | 300 | 300 | 60 | 60 | 60 | 60
SLVA-BLPK-115.0-1 | 9431 | SAN LUIS VALLEY SUBSTATION | XCEL | BLANCA PEAK SUBSTATION | XCEL | 70374 | 70937 | Xcel Owned | 9431 246Y | CURRENT_TRANSFORMER | SLVA | 300 | 300 | 300 | 300 | 60 | 60 | 60 | 60
BANC-GRAY-115.0-1 | 9448 | BANCROFT SUBSTATION | XCEL | GRAY STREET SUBSTATION | XCEL | 70045 | 70208 | Xcel Owned | BANC-GRAY-115.0-1 | FACILITY |  | 970 | 1067 | 1055 | 1161 | 193 | 213 | 210 | 231
BANC-GRAY-115.0-1 | 9448 | BANCROFT SUBSTATION | XCEL | GRAY STREET SUBSTATION | XCEL | 70045 | 70208 | Xcel Owned | BANC-GRAY-115.0-1 | Transmission Line | 9448 | 970 | 1067 | 1055 | 1161 | 193 | 213 | 210 | 231
BROO-SEMP-115.0-1 | 9464 | BROOMFIELD SUBSTATION | XCEL | SEMPER SUBSTATION | XCEL | 70065 | 70382 | Xcel Owned | BROO-SEMP-115.0-1 | FACILITY |  | 797 | 877 | 900 | 900 | 159 | 175 | 179 | 179
BROO-SEMP-115.0-1 | 9464 | BROOMFIELD SUBSTATION | XCEL | SEMPER SUBSTATION | XCEL | 70065 | 70382 | Xcel Owned | BROO-SEMP-115.0-1 | Transmission Line | 9464 | 797 | 877 | 907 | 998 | 159 | 175 | 181 | 199
BROO-SEMP-115.0-1 | 9464 | BROOMFIELD SUBSTATION | XCEL | SEMPER SUBSTATION | XCEL | 70065 | 70382 | Xcel Owned | 9464 XDCR AMP | SECONDARY_CURRENT_LIMITATION | SEMP | 900 | 900 | 900 | 900 | 179 | 179 | 179 | 179
LAFA-PKWY-115.0-1 | 9481 | LAFAYETTE SUBSTATION | XCEL | PARKWAY (Tri State) | FOREIGN | 70244 | 70604 | Jointly Owned | LAFA-PKWY-115.0-1 | FACILITY |  | 553 | 608 | 628 | 691 | 110 | 121 | 125 | 138
LAFA-PKWY-115.0-1 | 9481 | LAFAYETTE SUBSTATION | XCEL | PARKWAY (Tri State) | FOREIGN | 70244 | 70604 | Jointly Owned | Partridge | BUSBAR_SECTION | LAFA | 553 | 608 | 628 | 691 | 110 | 121 | 125 | 138
LAFA-VALM-115.0-1 | 9481 | LAFAYETTE SUBSTATION | XCEL | VALMONT SWITCHYARD SUBSTATION | XCEL | 70244 | 70444 | Xcel Owned | LAFA-VALM-115.0-1 | FACILITY |  | 800 | 880 | 910 | 1001 | 159 | 175 | 181 | 199
LAFA-VALM-115.0-1 | 9481 | LAFAYETTE SUBSTATION | XCEL | VALMONT SWITCHYARD SUBSTATION | XCEL | 70244 | 70444 | Xcel Owned | Hawk | BUSBAR_SECTION | VALM | 800 | 880 | 910 | 1001 | 159 | 175 | 181 | 199
LAFA-VALM-115.0-1 | 9481 | LAFAYETTE SUBSTATION | XCEL | VALMONT SWITCHYARD SUBSTATION | XCEL | 70244 | 70444 | Xcel Owned | LAFA-VALM-115.0-1 | Transmission Line | 9481 | 800 | 880 | 910 | 1001 | 159 | 175 | 181 | 199
ADKO_TP-GILC-115.0-1 | 9494 | ANADARKO TAP | XCEL | GILCREST SUBSTATION | XCEL | 2160 | 70198 | Xcel Owned | ADKO_TP-GILC-115.0-1 | FACILITY |  | 724 | 724 | 848 | 848 | 144 | 144 | 169 | 169
ADKO_TP-GILC-115.0-1 | 9494 | ANADARKO TAP | XCEL | GILCREST SUBSTATION | XCEL | 2160 | 70198 | Xcel Owned | ADKO_TP-GILC-115.0-1 | Transmission Line | 9494 | 724 | 724 | 848 | 848 | 144 | 144 | 169 | 169
ADKO_TP-VASQ-115.0-1 | 9494 | ANADARKO TAP | XCEL | VASQUEZ SUBSTATION | XCEL | 2160 | 70450 | Xcel Owned | ADKO_TP-VASQ-115.0-1 | FACILITY |  | 803 | 883 | 912 | 1004 | 160 | 176 | 182 | 200
ADKO_TP-VASQ-115.0-1 | 9494 | ANADARKO TAP | XCEL | VASQUEZ SUBSTATION | XCEL | 2160 | 70450 | Xcel Owned | ADKO_TP-VASQ-115.0-1 | Transmission Line | 9494 | 803 | 883 | 912 | 1004 | 160 | 176 | 182 | 200
FLUP-VASQ-115.0-1 | 9494 | FORT LUPTON SUBSTATION | XCEL | VASQUEZ SUBSTATION | XCEL | 70191 | 70450 | Xcel Owned | FLUP-VASQ-115.0-1 | FACILITY |  | 800 | 800 | 800 | 800 | 159 | 159 | 159 | 159
FLUP-VASQ-115.0-1 | 9494 | FORT LUPTON SUBSTATION | XCEL | VASQUEZ SUBSTATION | XCEL | 70191 | 70450 | Xcel Owned | 9494 246Y | CURRENT_TRANSFORMER | FLUP | 800 | 800 | 800 | 800 | 159 | 159 | 159 | 159
FLUP-VASQ-115.0-1 | 9494 | FORT LUPTON SUBSTATION | XCEL | VASQUEZ SUBSTATION | XCEL | 70191 | 70450 | Xcel Owned | 9494 135X | CURRENT_TRANSFORMER | FLUP | 800 | 800 | 800 | 800 | 159 | 159 | 159 | 159
FLUP-VASQ-115.0-1 | 9494 | FORT LUPTON SUBSTATION | XCEL | VASQUEZ SUBSTATION | XCEL | 70191 | 70450 | Xcel Owned | 9494 246X | CURRENT_TRANSFORMER | FLUP | 800 | 800 | 800 | 800 | 159 | 159 | 159 | 159
GILC-GODF-115.0-1 | 9494 | GILCREST SUBSTATION | XCEL | GODFREY SUBSTATION | XCEL | 70198 | 70202 | Xcel Owned | GILC-GODF-115.0-1 | FACILITY |  | 804 | 884 | 913 | 1005 | 160 | 176 | 182 | 200
GILC-GODF-115.0-1 | 9494 | GILCREST SUBSTATION | XCEL | GODFREY SUBSTATION | XCEL | 70198 | 70202 | Xcel Owned | GILC-GODF-115.0-1 | Transmission Line | 9494 | 804 | 884 | 913 | 1005 | 160 | 176 | 182 | 200
FLUP-PVAL-115.0-1 | 9499 | FORT LUPTON SUBSTATION | XCEL | PLATTE VALLEY | XCEL | 70191 | 70307 | Xcel Owned | FLUP-PVAL-115.0-1 | FACILITY |  | 1072 | 1179 | 1200 | 1200 | 213 | 235 | 239 | 239
FLUP-PVAL-115.0-1 | 9499 | FORT LUPTON SUBSTATION | XCEL | PLATTE VALLEY | XCEL | 70191 | 70307 | Xcel Owned | Lilac | BUSBAR_SECTION | PVAL | 1072 | 1179 | 1219 | 1341 | 213 | 235 | 243 | 267
FLUP-PVAL-115.0-1 | 9499 | FORT LUPTON SUBSTATION | XCEL | PLATTE VALLEY | XCEL | 70191 | 70307 | Xcel Owned | 9499 135X | CURRENT_TRANSFORMER | FLUP | 1200 | 1200 | 1200 | 1200 | 239 | 239 | 239 | 239
FLUP-PVAL-115.0-1 | 9499 | FORT LUPTON SUBSTATION | XCEL | PLATTE VALLEY | XCEL | 70191 | 70307 | Xcel Owned | 9499 135Y | CURRENT_TRANSFORMER | FLUP | 1200 | 1200 | 1200 | 1200 | 239 | 239 | 239 | 239
FLUP-PVAL-115.0-1 | 9499 | FORT LUPTON SUBSTATION | XCEL | PLATTE VALLEY | XCEL | 70191 | 70307 | Xcel Owned | 9499 246Y | CURRENT_TRANSFORMER | FLUP | 1200 | 1200 | 1200 | 1200 | 239 | 239 | 239 | 239
FLUP-PVAL-115.0-1 | 9499 | FORT LUPTON SUBSTATION | XCEL | PLATTE VALLEY | XCEL | 70191 | 70307 | Xcel Owned | 9499 246X | CURRENT_TRANSFORMER | FLUP | 1200 | 1200 | 1200 | 1200 | 239 | 239 | 239 | 239
FRGD-PVAL-115.0-1 | 9499 | FAIRGROUNDS SUBSTATION | XCEL | PLATTE VALLEY | XCEL | 72122 | 70307 | Xcel Owned | FRGD-PVAL-115.0-1 | FACILITY |  | 800 | 880 | 910 | 1001 | 159 | 175 | 181 | 199
FRGD-PVAL-115.0-1 | 9499 | FAIRGROUNDS SUBSTATION | XCEL | PLATTE VALLEY | XCEL | 72122 | 70307 | Xcel Owned | FRGD-PVAL-115.0-1 | Transmission Line | 9499 | 800 | 880 | 910 | 1001 | 159 | 175 | 181 | 199
FRGD-THTN-115.0-1 | 9499 | FAIRGROUNDS SUBSTATION | XCEL | THORNTON | XCEL | 72122 | 70099 | Xcel Owned | FRGD-THTN-115.0-1 | FACILITY |  | 800 | 880 | 909 | 1000 | 159 | 175 | 181 | 199
FRGD-THTN-115.0-1 | 9499 | FAIRGROUNDS SUBSTATION | XCEL | THORNTON | XCEL | 72122 | 70099 | Xcel Owned | FRGD-THTN-115.0-1 | Transmission Line | 9499 | 800 | 880 | 909 | 1000 | 159 | 175 | 181 | 199
NORT-CHER-115.0-1 | 9541 | NORTH SUBSTATION | XCEL | CHEROKEE SWITCHYARD SUBSTATION | XCEL | 70298 | 70108 | Xcel Owned | NORT-CHER-115.0-1 | FACILITY |  | 1001 | 1101 | 1139 | 1200 | 199 | 219 | 227 | 239
NORT-CHER-115.0-1 | 9541 | NORTH SUBSTATION | XCEL | CHEROKEE SWITCHYARD SUBSTATION | XCEL | 70298 | 70108 | Xcel Owned | NORT-CHER-115.0-1 | Transmission Line | 9541 | 1001 | 1101 | 1139 | 1253 | 199 | 219 | 227 | 250
NORT-CHER-115.0-1 | 9541 | NORTH SUBSTATION | XCEL | CHEROKEE SWITCHYARD SUBSTATION | XCEL | 70298 | 70108 | Xcel Owned | Violet | BUSBAR_SECTION | NORT | 1001 | 1101 | 1139 | 1253 | 199 | 219 | 227 | 249
NORT-CHER-115.0-1 | 9541 | NORTH SUBSTATION | XCEL | CHEROKEE SWITCHYARD SUBSTATION | XCEL | 70298 | 70108 | Xcel Owned | 9541 PKG-S | SECONDARY_CURRENT_LIMITATION | CHER | 1200 | 1200 | 1200 | 1200 | 239 | 239 | 239 | 239
NORT-CHER-115.0-1 | 9541 | NORTH SUBSTATION | XCEL | CHEROKEE SWITCHYARD SUBSTATION | XCEL | 70298 | 70108 | Xcel Owned | 9541 XDCR AMP | SECONDARY_CURRENT_LIMITATION | CHER | 1200 | 1200 | 1200 | 1200 | 239 | 239 | 239 | 239
CALI-CHER-115.0-1 | 9542 | CALIFORNIA SUBSTATION | XCEL | CHEROKEE SWITCHYARD SUBSTATION | XCEL | 70073 | 70108 | Xcel Owned | CALI-CHER-115.0-1 | FACILITY |  | 688 | 757 | 688 | 757 | 137 | 151 | 137 | 151
CALI-CHER-115.0-1 | 9542 | CALIFORNIA SUBSTATION | XCEL | CHEROKEE SWITCHYARD SUBSTATION | XCEL | 70073 | 70108 | Xcel Owned | CALI-CHER-115.0-1 | Transmission Line | 9542 | 688 | 757 | 688 | 757 | 137 | 151 | 137 | 151
CALI-HARR-115.0-1 | 9542 | CALIFORNIA SUBSTATION | XCEL | HARRISON SUBSTATION | XCEL | 70073 | 70215 | Xcel Owned | CALI-HARR-115.0-1 | FACILITY |  | 728 | 801 | 728 | 801 | 145 | 160 | 145 | 160
CALI-HARR-115.0-1 | 9542 | CALIFORNIA SUBSTATION | XCEL | HARRISON SUBSTATION | XCEL | 70073 | 70215 | Xcel Owned | CALI-HARR-115.0-1 | Transmission Line | 9542 | 728 | 801 | 728 | 801 | 145 | 160 | 145 | 160
ARSE-HAVA-115.0-1 | 9543 | ARSENAL | XCEL | HAVANA SUBSTATION | XCEL | 70040 | 70217 | Xcel Owned | ARSE-HAVA-115.0-1 | FACILITY |  | 799 | 879 | 909 | 999 | 159 | 175 | 181 | 199
ARSE-HAVA-115.0-1 | 9543 | ARSENAL | XCEL | HAVANA SUBSTATION | XCEL | 70040 | 70217 | Xcel Owned | Hawk | BUSBAR_SECTION | ARSE | 799 | 879 | 909 | 999 | 159 | 175 | 181 | 199
CHER-DERB_TP-115.0-1 | 9543 | CHEROKEE SWITCHYARD SUBSTATION | XCEL | DERBY TAP | XCEL | 70110 | 70153 | Xcel Owned | CHER-DERB_TP-115.0-1 | FACILITY |  | 800 | 880 | 910 | 1001 | 159 | 175 | 181 | 199
CHER-DERB_TP-115.0-1 | 9543 | CHEROKEE SWITCHYARD SUBSTATION | XCEL | DERBY TAP | XCEL | 70110 | 70153 | Xcel Owned | CHER-DERB_TP-115.0-1 | Transmission Line | 9543 | 800 | 880 | 910 | 1001 | 159 | 175 | 181 | 199
DERB_TP-ARSE-115.0-1 | 9543 | DERBY TAP | XCEL | ARSENAL | XCEL | 70153 | 70040 | Xcel Owned | DERB_TP-ARSE-115.0-1 | FACILITY |  | 799 | 879 | 909 | 999 | 159 | 175 | 181 | 199
DERB_TP-ARSE-115.0-1 | 9543 | DERBY TAP | XCEL | ARSENAL | XCEL | 70153 | 70040 | Xcel Owned | Hawk | BUSBAR_SECTION | ARSE | 799 | 879 | 909 | 999 | 159 | 175 | 181 | 199
DERB_TP-DERB-115.0-1 | 9543 | DERBY TAP | XCEL | DERBY SUBSTATION | XCEL | 70153 | 70154 | Xcel Owned | DERB_TP-DERB-115.0-1 | FACILITY |  | 600 | 730 | 743 | 829 | 120 | 145 | 148 | 165
DERB_TP-DERB-115.0-1 | 9543 | DERBY TAP | XCEL | DERBY SUBSTATION | XCEL | 70153 | 70154 | Xcel Owned | 9374 | SWITCH | DERB | 600 | 775 | 743 | 890 | 120 | 154 | 148 | 177
DERB_TP-DERB-115.0-1 | 9543 | DERBY TAP | XCEL | DERBY SUBSTATION | XCEL | 70153 | 70154 | Xcel Owned | 300 - 19 | BUSBAR_SECTION | DERB | 630 | 730 | 747 | 829 | 126 | 145 | 149 | 165
HAVA-CHAM-115.0-2 | 9543 | HAVANA SUBSTATION | XCEL | CHAMBERS SUBSTATION | XCEL | 70217 | 70538 | Xcel Owned | HAVA-CHAM-115.0-2 | FACILITY |  | 800 | 880 | 910 | 1001 | 159 | 175 | 181 | 199
HAVA-CHAM-115.0-2 | 9543 | HAVANA SUBSTATION | XCEL | CHAMBERS SUBSTATION | XCEL | 70217 | 70538 | Xcel Owned | HAVA-CHAM-115.0-2 | Transmission Line | 9543 | 800 | 880 | 910 | 1001 | 159 | 175 | 181 | 199
CHER-DERB-115.0-1 | 9544 | CHEROKEE SWITCHYARD SUBSTATION | XCEL | DERBY SUBSTATION | XCEL | 70110 | 70154 | Xcel Owned | CHER-DERB-115.0-1 | FACILITY |  | 600 | 730 | 743 | 829 | 120 | 145 | 148 | 165
CHER-DERB-115.0-1 | 9544 | CHEROKEE SWITCHYARD SUBSTATION | XCEL | DERBY SUBSTATION | XCEL | 70110 | 70154 | Xcel Owned | 9544-1 | SWITCH | DERB | 600 | 775 | 743 | 890 | 120 | 154 | 148 | 177
CHER-DERB-115.0-1 | 9544 | CHEROKEE SWITCHYARD SUBSTATION | XCEL | DERBY SUBSTATION | XCEL | 70110 | 70154 | Xcel Owned | 300 - 19 | BUSBAR_SECTION | DERB | 630 | 730 | 747 | 829 | 126 | 145 | 149 | 165
DERB-HAVA-115.0-1 | 9544 | DERBY SUBSTATION | XCEL | HAVANA SUBSTATION | XCEL | 70154 | 70216 | Xcel Owned | DERB-HAVA-115.0-1 | FACILITY |  | 600 | 662 | 743 | 827 | 120 | 132 | 148 | 165
DERB-HAVA-115.0-1 | 9544 | DERBY SUBSTATION | XCEL | HAVANA SUBSTATION | XCEL | 70154 | 70216 | Xcel Owned | 9544-4 | SWITCH | HAVA | 600 | 775 | 743 | 890 | 120 | 154 | 148 | 177
DERB-HAVA-115.0-1 | 9544 | DERBY SUBSTATION | XCEL | HAVANA SUBSTATION | XCEL | 70154 | 70216 | Xcel Owned | 9544-2 | SWITCH | DERB | 600 | 775 | 743 | 890 | 120 | 154 | 148 | 177
DERB-HAVA-115.0-1 | 9544 | DERBY SUBSTATION | XCEL | HAVANA SUBSTATION | XCEL | 70154 | 70216 | Xcel Owned | DERB-HAVA-115.0-1 | Transmission Line | 9544 | 602 | 662 | 752 | 827 | 120 | 132 | 150 | 165
HAVA-CHAM-115.0-1 | 9544 | HAVANA SUBSTATION | XCEL | CHAMBERS SUBSTATION | XCEL | 70216 | 70538 | Xcel Owned | HAVA-CHAM-115.0-1 | FACILITY |  | 600 | 775 | 743 | 890 | 120 | 154 | 148 | 177
HAVA-CHAM-115.0-1 | 9544 | HAVANA SUBSTATION | XCEL | CHAMBERS SUBSTATION | XCEL | 70216 | 70538 | Xcel Owned | 9544-5 | SWITCH | HAVA | 600 | 775 | 743 | 890 | 120 | 154 | 148 | 177
CHER-MAPL-115.0-1 | 9546 | CHEROKEE SWITCHYARD SUBSTATION | XCEL | MAPLETON SUBSTATION | XCEL | 70108 | 70276 | Xcel Owned | CHER-MAPL-115.0-1 | FACILITY |  | 800 | 880 | 909 | 1000 | 159 | 175 | 181 | 199
CHER-MAPL-115.0-1 | 9546 | CHEROKEE SWITCHYARD SUBSTATION | XCEL | MAPLETON SUBSTATION | XCEL | 70108 | 70276 | Xcel Owned | Hawk | BUSBAR_SECTION | CHER | 800 | 880 | 909 | 1000 | 159 | 175 | 181 | 199
CHER-MAPL-115.0-1 | 9546 | CHEROKEE SWITCHYARD SUBSTATION | XCEL | MAPLETON SUBSTATION | XCEL | 70108 | 70276 | Xcel Owned | CHER-MAPL-115.0-1 | Transmission Line | 9546 | 800 | 880 | 910 | 1001 | 159 | 175 | 181 | 199
MAPL-SAND-115.0-1 | 9546 | MAPLETON SUBSTATION | XCEL | SANDOWN SUBSTATION | XCEL | 70277 | 70377 | Xcel Owned | MAPL-SAND-115.0-1 | FACILITY |  | 799 | 879 | 909 | 999 | 159 | 175 | 181 | 199
MAPL-SAND-115.0-1 | 9546 | MAPLETON SUBSTATION | XCEL | SANDOWN SUBSTATION | XCEL | 70277 | 70377 | Xcel Owned | MAPL-SAND-115.0-1 | Transmission Line | 9546 | 799 | 879 | 909 | 999 | 159 | 175 | 181 | 199
CAPI-CALI_TP-115.0-1 | 9547 | CAPITOL HILL SUBSTATION | XCEL | CALIFORNIA TAP | XCEL | 70087 | 2050 | Xcel Owned | CAPI-CALI_TP-115.0-1 | FACILITY |  | 914 | 1005 | 914 | 1005 | 182 | 200 | 182 | 200
CAPI-CALI_TP-115.0-1 | 9547 | CAPITOL HILL SUBSTATION | XCEL | CALIFORNIA TAP | XCEL | 70087 | 2050 | Xcel Owned | CAPI-CALI_TP-115.0-1 | Transmission Line | 9547 | 914 | 1005 | 914 | 1005 | 182 | 200 | 182 | 200
CHER-MAPL-115.0-2 | 9547 | CHEROKEE SWITCHYARD SUBSTATION | XCEL | MAPLETON SUBSTATION | XCEL | 70108 | 70277 | Xcel Owned | CHER-MAPL-115.0-2 | FACILITY |  | 1200 | 1327 | 1375 | 1400 | 239 | 264 | 274 | 279
CHER-MAPL-115.0-2 | 9547 | CHEROKEE SWITCHYARD SUBSTATION | XCEL | MAPLETON SUBSTATION | XCEL | 70108 | 70277 | Xcel Owned | 9547-2 | SWITCH | MAPL | 1200 | 1549 | 1486 | 1780 | 239 | 309 | 296 | 355
CHER-MAPL-115.0-2 | 9547 | CHEROKEE SWITCHYARD SUBSTATION | XCEL | MAPLETON SUBSTATION | XCEL | 70108 | 70277 | Xcel Owned | CHER-MAPL-115.0-2 | Transmission Line | 9547 | 1206 | 1327 | 1375 | 1513 | 240 | 264 | 274 | 301
CHER-MAPL-115.0-2 | 9547 | CHEROKEE SWITCHYARD SUBSTATION | XCEL | MAPLETON SUBSTATION | XCEL | 70108 | 70277 | Xcel Owned | 9547 XDCR AMP | SECONDARY_CURRENT_LIMITATION | CHER | 1400 | 1400 | 1400 | 1400 | 279 | 279 | 279 | 279
MAPL-CALI_TP-115.0-1 | 9547 | MAPLETON SUBSTATION | XCEL | CALIFORNIA TAP | XCEL | 70276 | 2050 | Xcel Owned | MAPL-CALI_TP-115.0-1 | FACILITY |  | 914 | 1005 | 914 | 1005 | 182 | 200 | 182 | 200
MAPL-CALI_TP-115.0-1 | 9547 | MAPLETON SUBSTATION | XCEL | CALIFORNIA TAP | XCEL | 70276 | 2050 | Xcel Owned | MAPL-CALI_TP-115.0-1 | Transmission Line | 9547 | 914 | 1005 | 914 | 1005 | 182 | 200 | 182 | 200
CHER-THTN-115.0-1 | 9548 | CHEROKEE SWITCHYARD SUBSTATION | XCEL | THORNTON | XCEL | 70110 | 70099 | Xcel Owned | CHER-THTN-115.0-1 | FACILITY |  | 800 | 880 | 909 | 1000 | 159 | 175 | 181 | 199
CHER-THTN-115.0-1 | 9548 | CHEROKEE SWITCHYARD SUBSTATION | XCEL | THORNTON | XCEL | 70110 | 70099 | Xcel Owned | Hawk | BUSBAR_SECTION | CHER | 800 | 880 | 909 | 1000 | 159 | 175 | 181 | 199
CHER-THTN-115.0-1 | 9548 | CHEROKEE SWITCHYARD SUBSTATION | XCEL | THORNTON | XCEL | 70110 | 70099 | Xcel Owned | CHER-THTN-115.0-1 | Transmission Line | 9548 | 800 | 880 | 910 | 1001 | 159 | 175 | 181 | 199
CHER-CONS-115.0-1 | 9549 | CHEROKEE SWITCHYARD SUBSTATION | XCEL | CONOCO SOUTH SUBSTATION | XCEL | 70110 | 70126 | Xcel Owned | CHER-CONS-115.0-1 | FACILITY |  | 918 | 1069 | 1093 | 1154 | 183 | 213 | 218 | 230
CHER-CONS-115.0-1 | 9549 | CHEROKEE SWITCHYARD SUBSTATION | XCEL | CONOCO SOUTH SUBSTATION | XCEL | 70110 | 70126 | Xcel Owned | Arbutus | BUSBAR_SECTION | CONS | 918 | 1069 | 1093 | 1216 | 183 | 213 | 218 | 242
CHER-CONS-115.0-1 | 9549 | CHEROKEE SWITCHYARD SUBSTATION | XCEL | CONOCO SOUTH SUBSTATION | XCEL | 70110 | 70126 | Xcel Owned | CHER-CONS-115.0-1 | Transmission Line | 9549 | 1081 | 1081 | 1154 | 1154 | 215 | 215 | 230 | 230
CONS-SAND-115.0-1 | 9549 | CONOCO SOUTH SUBSTATION | XCEL | SANDOWN SUBSTATION | XCEL | 70126 | 70377 | Xcel Owned | CONS-SAND-115.0-1 | FACILITY |  | 799 | 879 | 909 | 999 | 159 | 175 | 181 | 199
CONS-SAND-115.0-1 | 9549 | CONOCO SOUTH SUBSTATION | XCEL | SANDOWN SUBSTATION | XCEL | 70126 | 70377 | Xcel Owned | CONS-SAND-115.0-1 | Transmission Line | 9549 | 799 | 879 | 909 | 999 | 159 | 175 | 181 | 199
BROO-FEDE-115.0-1 | 9558 | BROOMFIELD SUBSTATION | XCEL | FEDERAL HEIGHTS SUBSTATION | XCEL | 70065 | 70174 | Xcel Owned | BROO-FEDE-115.0-1 | FACILITY |  | 797 | 876 | 906 | 997 | 159 | 174 | 180 | 199
BROO-FEDE-115.0-1 | 9558 | BROOMFIELD SUBSTATION | XCEL | FEDERAL HEIGHTS SUBSTATION | XCEL | 70065 | 70174 | Xcel Owned | BROO-FEDE-115.0-1 | Transmission Line | 9558 | 797 | 876 | 906 | 997 | 159 | 174 | 180 | 199
CHER-FEDE-115.0-1 | 9558 | CHEROKEE SWITCHYARD SUBSTATION | XCEL | FEDERAL HEIGHTS SUBSTATION | XCEL | 70108 | 70174 | Xcel Owned | CHER-FEDE-115.0-1 | FACILITY |  | 1030 | 1133 | 1107 | 1217 | 205 | 226 | 220 | 242
CHER-FEDE-115.0-1 | 9558 | CHEROKEE SWITCHYARD SUBSTATION | XCEL | FEDERAL HEIGHTS SUBSTATION | XCEL | 70108 | 70174 | Xcel Owned | CHER-FEDE-115.0-1 | Transmission Line | 9558 | 1030 | 1133 | 1107 | 1217 | 205 | 226 | 220 | 242
ELDO-PLNV_TP-115.0-1 | 9584 | ELDORADO SPRINGS SUBSTATION | XCEL | PLAINVIEW TAP | XCEL | 70164 | 2106 | Xcel Owned | ELDO-PLNV_TP-115.0-1 | FACILITY |  | 794 | 874 | 900 | 990 | 158 | 174 | 179 | 197
ELDO-PLNV_TP-115.0-1 | 9584 | ELDORADO SPRINGS SUBSTATION | XCEL | PLAINVIEW TAP | XCEL | 70164 | 2106 | Xcel Owned | ELDO-PLNV_TP-115.0-1 | Transmission Line | 9584 | 794 | 874 | 900 | 990 | 158 | 174 | 179 | 197
LYDS_TP-PLNV_TP-115.0-1 | 9584 | LEYDEN SITE | XCEL | PLAINVIEW TAP | XCEL | 70262 | 2106 | Xcel Owned | LYDS_TP-PLNV_TP-115.0-1 | FACILITY |  | 793 | 873 | 900 | 990 | 158 | 174 | 179 | 197
LYDS_TP-PLNV_TP-115.0-1 | 9584 | LEYDEN SITE | XCEL | PLAINVIEW TAP | XCEL | 70262 | 2106 | Xcel Owned | LYDS_TP-PLNV_TP-115.0-1 | Transmission Line | 9584 | 793 | 873 | 900 | 990 | 158 | 174 | 179 | 197
LYDS_TP-RIDG-115.0-1 | 9584 | LEYDEN SITE | XCEL | RIDGE SUBSTATION | XCEL | 70262 | 70354 | Xcel Owned | LYDS_TP-RIDG-115.0-1 | FACILITY |  | 1270 | 1397 | 1447 | 1592 | 253 | 278 | 288 | 317
LYDS_TP-RIDG-115.0-1 | 9584 | LEYDEN SITE | XCEL | RIDGE SUBSTATION | XCEL | 70262 | 70354 | Xcel Owned | LYDS_TP-RIDG-115.0-1 | Transmission Line | 9584 | 1270 | 1397 | 1447 | 1592 | 253 | 278 | 288 | 317
LYDS_TP-QUAK-115.0-1 | 9584 | LEYDEN SITE | XCEL | QUAKER SUBSTATION | XCEL | 70262 | 70340 | Xcel Owned | LYDS_TP-QUAK-115.0-1 | FACILITY |  | 480 | 528 | 551 | 606 | 96 | 105 | 110 | 121
LYDS_TP-QUAK-115.0-1 | 9584 | LEYDEN SITE | XCEL | QUAKER SUBSTATION | XCEL | 70262 | 70340 | Xcel Owned | LYDS_TP-QUAK-115.0-1 | Transmission Line | 9584 | 480 | 528 | 551 | 606 | 96 | 105 | 110 | 121
CAST_TP1-CAST-115.0-1 | 9603 | CASTLE ROCK TAP 1 | XCEL | CASTLE ROCK SUBSTATION | XCEL | 70091 | 2105 | Xcel Owned | CAST_TP1-CAST-115.0-1 | FACILITY |  | 648 | 713 | 718 | 789 | 129 | 142 | 143 | 157
CAST_TP1-CAST-115.0-1 | 9603 | CASTLE ROCK TAP 1 | XCEL | CASTLE ROCK SUBSTATION | XCEL | 70091 | 2105 | Xcel Owned | CAST_TP1-CAST-115.0-1 | Transmission Line | 9603 | 648 | 713 | 718 | 789 | 129 | 142 | 143 | 157
CAST_TP1-PALM-115.0-1 | 9603 | CASTLE ROCK TAP 1 | XCEL | PALMER LAKE SUBSTATION | XCEL | 70091 | 70308 | Xcel Owned | CAST_TP1-PALM-115.0-1 | FACILITY |  | 641 | 705 | 729 | 802 | 128 | 140 | 145 | 160
CAST_TP1-PALM-115.0-1 | 9603 | CASTLE ROCK TAP 1 | XCEL | PALMER LAKE SUBSTATION | XCEL | 70091 | 70308 | Xcel Owned | CAST_TP1-PALM-115.0-1 | Transmission Line | 9603 | 641 | 705 | 729 | 802 | 128 | 140 | 145 | 160
PALM-MONU-115.0-1 | 9605 | PALMER LAKE SUBSTATION | XCEL | Monument TRI STATE | FOREIGN | 70308 | 73414 | Jointly Owned | PALM-MONU-115.0-1 | FACILITY |  | 541 | 541 | 541 | 541 | 108 | 108 | 108 | 108
PALM-MONU-115.0-1 | 9605 | PALMER LAKE SUBSTATION | XCEL | Monument TRI STATE | FOREIGN | 70308 | 73414 | Jointly Owned | Foreign Ratings | Foreign Ratings | MONU | 541 | 541 | 541 | 541 | 108 | 108 | 108 | 108
CAST_TP1-CAST_TP2-115.0-1 | 9606 | CASTLE ROCK TAP 1 | XCEL | CASTLE ROCK TAP 2 | XCEL | 70091 | 2131 | Xcel Owned | CAST_TP1-CAST_TP2-115.0-1 | FACILITY |  | 800 | 880 | 910 | 1001 | 159 | 175 | 181 | 199
CAST_TP1-CAST_TP2-115.0-1 | 9606 | CASTLE ROCK TAP 1 | XCEL | CASTLE ROCK TAP 2 | XCEL | 70091 | 2131 | Xcel Owned | CAST_TP1-CAST_TP2-115.0-1 | Transmission Line | 9606 | 800 | 880 | 910 | 1001 | 159 | 175 | 181 | 199
CAST_TP2-CAST-115.0-1 | 9606 | CASTLE ROCK TAP 2 | XCEL | CASTLE ROCK SUBSTATION | XCEL | 2131 | 2132 | Xcel Owned | CAST_TP2-CAST-115.0-1 | FACILITY |  | 800 | 880 | 900 | 900 | 159 | 175 | 179 | 179
CAST_TP2-CAST-115.0-1 | 9606 | CASTLE ROCK TAP 2 | XCEL | CASTLE ROCK SUBSTATION | XCEL | 2131 | 2132 | Xcel Owned | CAST_TP2-CAST-115.0-1 | Transmission Line | 9606 | 800 | 880 | 910 | 1001 | 159 | 175 | 181 | 199
CAST_TP2-CAST-115.0-1 | 9606 | CASTLE ROCK TAP 2 | XCEL | CASTLE ROCK SUBSTATION | XCEL | 2131 | 2132 | Xcel Owned | 9606_A1_115KV | SECONDARY_CURRENT_LIMITATION | CAST | 900 | 900 | 900 | 900 | 179 | 179 | 179 | 179
CAST_TP2-CROV-115.0-1 | 9606 | CASTLE ROCK TAP 2 | XCEL | CROWFOOT VALLEY | XCEL | 2131 | 70117 | Xcel Owned | CAST_TP2-CROV-115.0-1 | FACILITY |  | 800 | 880 | 910 | 1001 | 159 | 175 | 181 | 199
CAST_TP2-CROV-115.0-1 | 9606 | CASTLE ROCK TAP 2 | XCEL | CROWFOOT VALLEY | XCEL | 2131 | 70117 | Xcel Owned | CAST_TP2-CROV-115.0-1 | Transmission Line | 9606 | 800 | 880 | 910 | 1001 | 159 | 175 | 181 | 199
CROV-HACA-115.0-1 | 9652 | CROWFOOT VALLEY | XCEL | HAPPY CANYON SUBSTATION | XCEL | 70117 | 70115 | Xcel Owned | CROV-HACA-115.0-1 | FACILITY |  | 800 | 880 | 910 | 1001 | 159 | 175 | 181 | 199
CROV-HACA-115.0-1 | 9652 | CROWFOOT VALLEY | XCEL | HAPPY CANYON SUBSTATION | XCEL | 70117 | 70115 | Xcel Owned | CROV-HACA-115.0-1 | Transmission Line | 9652 | 800 | 880 | 910 | 1001 | 159 | 175 | 181 | 199
CABI-GEOR-115.0-1 | 9665 | CABIN CREEK HYDRO SUBSTATION | XCEL | GEORGETOWN HYDRO SUBSTATION | XCEL | 70071 | 70197 | Xcel Owned | CABI-GEOR-115.0-1 | FACILITY |  | 600 | 600 | 600 | 600 | 120 | 120 | 120 | 120
CABI-GEOR-115.0-1 | 9665 | CABIN CREEK HYDRO SUBSTATION | XCEL | GEORGETOWN HYDRO SUBSTATION | XCEL | 70071 | 70197 | Xcel Owned | 9665 METER VAR | SECONDARY_CURRENT_LIMITATION | CABI | 600 | 600 | 600 | 600 | 120 | 120 | 120 | 120
CABI-GEOR-115.0-1 | 9665 | CABIN CREEK HYDRO SUBSTATION | XCEL | GEORGETOWN HYDRO SUBSTATION | XCEL | 70071 | 70197 | Xcel Owned |  | LINE_TRAP | CABI | 600 | 600 | 624 | 624 | 120 | 120 | 124 | 124
CABI-GEOR-115.0-1 | 9665 | CABIN CREEK HYDRO SUBSTATION | XCEL | GEORGETOWN HYDRO SUBSTATION | XCEL | 70071 | 70197 | Xcel Owned | 9665-1 | SWITCH | GEOR | 600 | 775 | 743 | 890 | 120 | 154 | 148 | 177
GEOR-HEND-115.0-1 | 9665 | GEORGETOWN HYDRO SUBSTATION | XCEL | HENDERSON SUBSTATION | XCEL | 70197 | 70218 | Xcel Owned | GEOR-HEND-115.0-1 | FACILITY |  | 600 | 600 | 600 | 600 | 120 | 120 | 120 | 120
GEOR-HEND-115.0-1 | 9665 | GEORGETOWN HYDRO SUBSTATION | XCEL | HENDERSON SUBSTATION | XCEL | 70197 | 70218 | Xcel Owned | 9665 METER VAR | SECONDARY_CURRENT_LIMITATION | HEND | 600 | 600 | 600 | 600 | 120 | 120 | 120 | 120
GEOR-HEND-115.0-1 | 9665 | GEORGETOWN HYDRO SUBSTATION | XCEL | HENDERSON SUBSTATION | XCEL | 70197 | 70218 | Xcel Owned | 9665 METER AMP | SECONDARY_CURRENT_LIMITATION | HEND | 600 | 600 | 600 | 600 | 120 | 120 | 120 | 120
GEOR-HEND-115.0-1 | 9665 | GEORGETOWN HYDRO SUBSTATION | XCEL | HENDERSON SUBSTATION | XCEL | 70197 | 70218 | Xcel Owned | 9665 METER W | SECONDARY_CURRENT_LIMITATION | HEND | 600 | 600 | 600 | 600 | 120 | 120 | 120 | 120
DANI-HACA-115.0-1 | 9674 | DANIELS PARK 115 & 230KV SUBSTATION | XCEL | HAPPY CANYON SUBSTATION | XCEL | 70138 | 70115 | Xcel Owned | DANI-HACA-115.0-1 | FACILITY |  | 661 | 661 | 787 | 787 | 132 | 132 | 157 | 157
DANI-HACA-115.0-1 | 9674 | DANIELS PARK 115 & 230KV SUBSTATION | XCEL | HAPPY CANYON SUBSTATION | XCEL | 70138 | 70115 | Xcel Owned | DANI-HACA-115.0-1 | Transmission Line | 9674 | 661 | 661 | 787 | 787 | 132 | 132 | 157 | 157
ELDO-RALS-115.0-1 | 9688 | ELDORADO SPRINGS SUBSTATION | XCEL | RALSTON SUBSTATION | XCEL | 70164 | 70346 | Xcel Owned | ELDO-RALS-115.0-1 | FACILITY |  | 644 | 708 | 732 | 805 | 128 | 141 | 146 | 160
ELDO-RALS-115.0-1 | 9688 | ELDORADO SPRINGS SUBSTATION | XCEL | RALSTON SUBSTATION | XCEL | 70164 | 70346 | Xcel Owned | ELDO-RALS-115.0-1 | Transmission Line | 9688 | 644 | 708 | 732 | 805 | 128 | 141 | 146 | 160
RALS-RIDG-115.0-2 | 9688 | RALSTON SUBSTATION | XCEL | RIDGE SUBSTATION | XCEL | 70346 | 70354 | Xcel Owned | RALS-RIDG-115.0-2 | FACILITY |  | 600 | 600 | 600 | 600 | 120 | 120 | 120 | 120
RALS-RIDG-115.0-2 | 9688 | RALSTON SUBSTATION | XCEL | RIDGE SUBSTATION | XCEL | 70346 | 70354 | Xcel Owned | 9688 METER VAR | SECONDARY_CURRENT_LIMITATION | RIDG | 600 | 600 | 600 | 600 | 120 | 120 | 120 | 120
HOPK-SHOS-115.0-1 | 9714 | HOPKINS SUBSTATION | XCEL | SHOSHONE HYDRO SUBSTATION | XCEL | 70231 | 70387 | Xcel Owned | HOPK-SHOS-115.0-1 | FACILITY |  | 200 | 200 | 200 | 200 | 40 | 40 | 40 | 40
HOPK-SHOS-115.0-1 | 9714 | HOPKINS SUBSTATION | XCEL | SHOSHONE HYDRO SUBSTATION | XCEL | 70231 | 70387 | Xcel Owned | 9714 135Y | CURRENT_TRANSFORMER | SHOS | 200 | 200 | 200 | 200 | 40 | 40 | 40 | 40
CARB-HOPK-115.0-1 | 9715 | CARBONDALE SUBSTATION | XCEL | HOPKINS SUBSTATION | XCEL | 70089 | 70231 | Xcel Owned | CARB-HOPK-115.0-1 | FACILITY |  | 200 | 200 | 200 | 200 | 40 | 40 | 40 | 40
CARB-HOPK-115.0-1 | 9715 | CARBONDALE SUBSTATION | XCEL | HOPKINS SUBSTATION | XCEL | 70089 | 70231 | Xcel Owned | 9715 135Y | CURRENT_TRANSFORMER | HOPK | 200 | 200 | 200 | 200 | 40 | 40 | 40 | 40
HOGB-LOOK-115.0-1 | 9794 | HOGBACK SUBSTATION | XCEL | LOOKOUT SUBSTATION | XCEL | 70224 | 70265 | Xcel Owned | HOGB-LOOK-115.0-1 | FACILITY |  | 1000 | 1000 | 1000 | 1000 | 199 | 199 | 199 | 199
HOGB-LOOK-115.0-1 | 9794 | HOGBACK SUBSTATION | XCEL | LOOKOUT SUBSTATION | XCEL | 70224 | 70265 | Xcel Owned | 9794 246X | CURRENT_TRANSFORMER | LOOK | 1000 | 1000 | 1000 | 1000 | 199 | 199 | 199 | 199
HOGB-LOOK-115.0-1 | 9794 | HOGBACK SUBSTATION | XCEL | LOOKOUT SUBSTATION | XCEL | 70224 | 70265 | Xcel Owned | 9794 135X | CURRENT_TRANSFORMER | LOOK | 1000 | 1000 | 1000 | 1000 | 199 | 199 | 199 | 199
HOGB-LOOK-115.0-1 | 9794 | HOGBACK SUBSTATION | XCEL | LOOKOUT SUBSTATION | XCEL | 70224 | 70265 | Xcel Owned | 9794 135Y | CURRENT_TRANSFORMER | LOOK | 1000 | 1000 | 1000 | 1000 | 199 | 199 | 199 | 199
HOGB-LOOK-115.0-1 | 9794 | HOGBACK SUBSTATION | XCEL | LOOKOUT SUBSTATION | XCEL | 70224 | 70265 | Xcel Owned | 9794 METER VAR | SECONDARY_CURRENT_LIMITATION | LOOK | 1000 | 1000 | 1000 | 1000 | 199 | 199 | 199 | 199
HOGB-SODA-115.0-1 | 9794 | HOGBACK SUBSTATION | XCEL | SODA LAKES SUBSTATION | XCEL | 70224 | 70400 | Xcel Owned | HOGB-SODA-115.0-1 | FACILITY |  | 795 | 800 | 800 | 800 | 158 | 159 | 159 | 159
HOGB-SODA-115.0-1 | 9794 | HOGBACK SUBSTATION | XCEL | SODA LAKES SUBSTATION | XCEL | 70224 | 70400 | Xcel Owned | Hawk | BUSBAR_SECTION | SODA | 795 | 874 | 904 | 994 | 158 | 174 | 180 | 198
HOGB-SODA-115.0-1 | 9794 | HOGBACK SUBSTATION | XCEL | SODA LAKES SUBSTATION | XCEL | 70224 | 70400 | Xcel Owned | 9794 246Y | CURRENT_TRANSFORMER | SODA | 800 | 800 | 800 | 800 | 159 | 159 | 159 | 159
BERG-HOGB-115.0-1 | 9794 | BERGEN PARK SUBSTATION | XCEL | HOGBACK SUBSTATION | XCEL | 70050 | 70224 | Xcel Owned | BERG-HOGB-115.0-1 | FACILITY |  | 668 | 778 | 797 | 886 | 133 | 155 | 159 | 176
BERG-HOGB-115.0-1 | 9794 | BERGEN PARK SUBSTATION | XCEL | HOGBACK SUBSTATION | XCEL | 70050 | 70224 | Xcel Owned | Hawk | BUSBAR_SECTION | BERG | 668 | 778 | 797 | 886 | 133 | 155 | 159 | 176
PONC-SARG-115.0-1 | 9811 | PONCHA JUNCTION SUBSTATION | XCEL | SARGENT SUBSTATION | XCEL | 70327 | 70379 | Xcel Owned | PONC-SARG-115.0-1 | FACILITY |  | 492 | 570 | 584 | 600 | 98 | 114 | 116 | 120
PONC-SARG-115.0-1 | 9811 | PONCHA JUNCTION SUBSTATION | XCEL | SARGENT SUBSTATION | XCEL | 70327 | 70379 | Xcel Owned | 4/0 - 7 | BUSBAR_SECTION | PONC | 492 | 570 | 584 | 647 | 98 | 114 | 116 | 129
PONC-SARG-115.0-1 | 9811 | PONCHA JUNCTION SUBSTATION | XCEL | SARGENT SUBSTATION | XCEL | 70327 | 70379 | Xcel Owned | 9811 135X | CURRENT_TRANSFORMER | PONC | 600 | 600 | 600 | 600 | 120 | 120 | 120 | 120
PONC-SARG-115.0-1 | 9811 | PONCHA JUNCTION SUBSTATION | XCEL | SARGENT SUBSTATION | XCEL | 70327 | 70379 | Xcel Owned | 9811_A_XDCR_115KV | SECONDARY_CURRENT_LIMITATION | PONC | 600 | 600 | 600 | 600 | 120 | 120 | 120 | 120
PONC-SARG-115.0-1 | 9811 | PONCHA JUNCTION SUBSTATION | XCEL | SARGENT SUBSTATION | XCEL | 70327 | 70379 | Xcel Owned | 9811_KWH_IN_115KV | SECONDARY_CURRENT_LIMITATION | PONC | 600 | 600 | 600 | 600 | 120 | 120 | 120 | 120
PONC-SARG-115.0-1 | 9811 | PONCHA JUNCTION SUBSTATION | XCEL | SARGENT SUBSTATION | XCEL | 70327 | 70379 | Xcel Owned | 9811 246X | CURRENT_TRANSFORMER | PONC | 600 | 600 | 600 | 600 | 120 | 120 | 120 | 120
PONC-SARG-115.0-1 | 9811 | PONCHA JUNCTION SUBSTATION | XCEL | SARGENT SUBSTATION | XCEL | 70327 | 70379 | Xcel Owned | 9811_KWH_OUT_115KV | SECONDARY_CURRENT_LIMITATION | PONC | 600 | 600 | 600 | 600 | 120 | 120 | 120 | 120
PONC-SARG-115.0-1 | 9811 | PONCHA JUNCTION SUBSTATION | XCEL | SARGENT SUBSTATION | XCEL | 70327 | 70379 | Xcel Owned | 9811 246Y | CURRENT_TRANSFORMER | PONC | 600 | 600 | 600 | 600 | 120 | 120 | 120 | 120
SLVA-SARG-115.0-1 | 9811 | SAN LUIS VALLEY SUBSTATION | XCEL | SARGENT SUBSTATION | XCEL | 70374 | 70379 | Xcel Owned | SLVA-SARG-115.0-1 | FACILITY |  | 500 | 500 | 500 | 500 | 100 | 100 | 100 | 100
SLVA-SARG-115.0-1 | 9811 | SAN LUIS VALLEY SUBSTATION | XCEL | SARGENT SUBSTATION | XCEL | 70374 | 70379 | Xcel Owned | 9811 135X | CURRENT_TRANSFORMER | SLVA | 500 | 500 | 500 | 500 | 100 | 100 | 100 | 100
SLVA-SARG-115.0-1 | 9811 | SAN LUIS VALLEY SUBSTATION | XCEL | SARGENT SUBSTATION | XCEL | 70374 | 70379 | Xcel Owned | 9811 135Y | CURRENT_TRANSFORMER | SLVA | 500 | 500 | 500 | 500 | 100 | 100 | 100 | 100
PONC-SMEL-115.0-1 | 9812 | PONCHA JUNCTION SUBSTATION | XCEL | SMELTERTOWN | XCEL | 70327 | 70394 | Xcel Owned | PONC-SMEL-115.0-1 | FACILITY |  | 300 | 300 | 300 | 300 | 60 | 60 | 60 | 60
PONC-SMEL-115.0-1 | 9812 | PONCHA JUNCTION SUBSTATION | XCEL | SMELTERTOWN | XCEL | 70327 | 70394 | Xcel Owned | 115 9812 M C | CURRENT_TRANSFORMER | PONC | 300 | 300 | 300 | 300 | 60 | 60 | 60 | 60
PONC-SMEL-115.0-1 | 9812 | PONCHA JUNCTION SUBSTATION | XCEL | SMELTERTOWN | XCEL | 70327 | 70394 | Xcel Owned | 115 9812 M A | CURRENT_TRANSFORMER | PONC | 300 | 300 | 300 | 300 | 60 | 60 | 60 | 60
PONC-SMEL-115.0-1 | 9812 | PONCHA JUNCTION SUBSTATION | XCEL | SMELTERTOWN | XCEL | 70327 | 70394 | Xcel Owned | 9812_W_VAR_115KV | SECONDARY_CURRENT_LIMITATION | PONC | 300 | 300 | 300 | 300 | 60 | 60 | 60 | 60
EAST-SMOK-115.0-2 | 9866 | EAST SUBSTATION | XCEL | SMOKY HILL SUBSTATION | XCEL | 70162 | 70395 | Xcel Owned | EAST-SMOK-115.0-2 | FACILITY |  | 600 | 728 | 743 | 827 | 120 | 145 | 148 | 165
EAST-SMOK-115.0-2 | 9866 | EAST SUBSTATION | XCEL | SMOKY HILL SUBSTATION | XCEL | 70162 | 70395 | Xcel Owned | 9866M | SWITCH | EAST | 600 | 775 | 743 | 890 | 120 | 154 | 148 | 177
EAST-SMOK-115.0-2 | 9866 | EAST SUBSTATION | XCEL | SMOKY HILL SUBSTATION | XCEL | 70162 | 70395 | Xcel Owned | 9866L | SWITCH | EAST | 600 | 775 | 743 | 890 | 120 | 154 | 148 | 177
EAST-SMOK-115.0-2 | 9866 | EAST SUBSTATION | XCEL | SMOKY HILL SUBSTATION | XCEL | 70162 | 70395 | Xcel Owned | 300 - 19 | BUSBAR_SECTION | EAST | 629 | 728 | 745 | 827 | 125 | 145 | 148 | 165
HARR-LEET-115.0-1 | 9955 | HARRISON SUBSTATION | XCEL | LEETSDALE SUBSTATION | XCEL | 70215 | 70282 | Xcel Owned | HARR-LEET-115.0-1 | FACILITY |  | 708 | 779 | 708 | 779 | 141 | 155 | 141 | 155
HARR-LEET-115.0-1 | 9955 | HARRISON SUBSTATION | XCEL | LEETSDALE SUBSTATION | XCEL | 70215 | 70282 | Xcel Owned | HARR-LEET-115.0-1 | Transmission Line | 9955 | 708 | 779 | 708 | 779 | 141 | 155 | 141 | 155
CAPI-HARR-115.0-1 | 9956 | CAPITOL HILL SUBSTATION | XCEL | HARRISON SUBSTATION | XCEL | 70087 | 70215 | Xcel Owned | CAPI-HARR-115.0-1 | FACILITY |  | 1022 | 1213 | 1233 | 1386 | 204 | 242 | 246 | 276
CAPI-HARR-115.0-1 | 9956 | CAPITOL HILL SUBSTATION | XCEL | HARRISON SUBSTATION | XCEL | 70087 | 70215 | Xcel Owned | Narcissus | BUSBAR_SECTION | HARR | 1022 | 1213 | 1233 | 1388 | 204 | 242 | 246 | 276
CAPI-HARR-115.0-1 | 9956 | CAPITOL HILL SUBSTATION | XCEL | HARRISON SUBSTATION | XCEL | 70087 | 70215 | Xcel Owned | CAPI-HARR-115.0-1 | Transmission Line | 9956 | 1260 | 1386 | 1260 | 1386 | 251 | 276 | 251 | 276
COMA-READ-115.0-2 | 9984 | COMANCHE SUBSTATION | XCEL | Reader | FOREIGN | 70121 | 70352 | Jointly Owned | COMA-READ-115.0-2 | FACILITY |  | 1600 | 1600 | 1600 | 1600 | 319 | 319 | 319 | 319
COMA-READ-115.0-2 | 9984 | COMANCHE SUBSTATION | XCEL | Reader | FOREIGN | 70121 | 70352 | Jointly Owned | 9984 | BREAKER | COMA | 1600 | 1600 | 1600 | 1600 | 319 | 319 | 319 | 319
CFIS-COMA-115.0-1 | 9985 | CF&I SOUTHEAST SUBSTATION | XCEL | COMANCHE SUBSTATION | XCEL | 70098 | 70121 | Xcel Owned | CFIS-COMA-115.0-1 | FACILITY |  | 641 | 705 | 729 | 802 | 128 | 140 | 145 | 160
CFIS-COMA-115.0-1 | 9985 | CF&I SOUTHEAST SUBSTATION | XCEL | COMANCHE SUBSTATION | XCEL | 70098 | 70121 | Xcel Owned | CFIS-COMA-115.0-1 | Transmission Line | 9985 | 641 | 705 | 729 | 802 | 128 | 140 | 145 | 160
COMA-READ-115.0-1 | 9986 | COMANCHE SUBSTATION | XCEL | Reader | FOREIGN | 70121 | 70352 | Jointly Owned | COMA-READ-115.0-1 | FACILITY |  | 1900 | 2000 | 1900 | 2000 | 378 | 398 | 378 | 398
COMA-READ-115.0-1 | 9986 | COMANCHE SUBSTATION | XCEL | Reader | FOREIGN | 70121 | 70352 | Jointly Owned | COMA-READ-115.0-1 | Transmission Line | 9986 | 1900 | 2090 | 1900 | 2090 | 378 | 416 | 378 | 416
COMA-READ-115.0-1 | 9986 | COMANCHE SUBSTATION | XCEL | Reader | FOREIGN | 70121 | 70352 | Jointly Owned | Foreign Ratings | Foreign Ratings | READ | 2000 | 2000 | 2000 | 2000 | 398 | 398 | 398 | 398
CFIS_TP-CFIS-115.0-1 | 9987 | CF&I SOUTHEAST TAP | XCEL | CF&I SOUTHEAST SUBSTATION | XCEL | 2002 | 70098 | Xcel Owned | CFIS_TP-CFIS-115.0-1 | FACILITY |  | 641 | 705 | 729 | 802 | 128 | 140 | 145 | 160
CFIS_TP-CFIS-115.0-1 | 9987 | CF&I SOUTHEAST TAP | XCEL | CF&I SOUTHEAST SUBSTATION | XCEL | 2002 | 70098 | Xcel Owned | CFIS_TP-CFIS-115.0-1 | Transmission Line | 9987 | 641 | 705 | 729 | 802 | 128 | 140 | 145 | 160
COMA-CFIS_TP-115.0-1 | 9987 | COMANCHE SUBSTATION | XCEL | CF&I SOUTHEAST TAP | XCEL | 70121 | 2002 | Xcel Owned | COMA-CFIS_TP-115.0-1 | FACILITY |  | 800 | 880 | 820 | 902 | 159 | 175 | 163 | 180
COMA-CFIS_TP-115.0-1 | 9987 | COMANCHE SUBSTATION | XCEL | CF&I SOUTHEAST TAP | XCEL | 70121 | 2002 | Xcel Owned | COMA-CFIS_TP-115.0-1 | Transmission Line | 9987 | 800 | 880 | 820 | 902 | 159 | 175 | 163 | 180
GRLY-WELD-115.0-1 | 9995 | GREELEY SUBSTATION | XCEL | WELD SUBSTATION | XCEL | 70209 | 70470 | Xcel Owned | GRLY-WELD-115.0-1 | FACILITY |  | 1104 | 1200 | 1200 | 1200 | 220 | 239 | 239 | 239
GRLY-WELD-115.0-1 | 9995 | GREELEY SUBSTATION | XCEL | WELD SUBSTATION | XCEL | 70209 | 70470 | Xcel Owned | GRLY-WELD-115.0-1 | Transmission Line | 9995 | 1104 | 1214 | 1258 | 1384 | 220 | 242 | 251 | 276
GRLY-WELD-115.0-1 | 9995 | GREELEY SUBSTATION | XCEL | WELD SUBSTATION | XCEL | 70209 | 70470 | Xcel Owned | 9995 | BREAKER | GRLY | 1200 | 1200 | 1200 | 1200 | 239 | 239 | 239 | 239
GRLY-WELD-115.0-1 | 9995 | GREELEY SUBSTATION | XCEL | WELD SUBSTATION | XCEL | 70209 | 70470 | Xcel Owned | 9995 135X | CURRENT_TRANSFORMER | GRLY | 1200 | 1200 | 1200 | 1200 | 239 | 239 | 239 | 239
GRLY-WELD-115.0-1 | 9995 | GREELEY SUBSTATION | XCEL | WELD SUBSTATION | XCEL | 70209 | 70470 | Xcel Owned | 246Y | CURRENT_TRANSFORMER | GRLY | 1200 | 1200 | 1200 | 1200 | 239 | 239 | 239 | 239
GRLY-WELD-115.0-1 | 9995 | GREELEY SUBSTATION | XCEL | WELD SUBSTATION | XCEL | 70209 | 70470 | Xcel Owned | 246X | CURRENT_TRANSFORMER | GRLY | 1200 | 1200 | 1200 | 1200 | 239 | 239 | 239 | 239
GRLY-WELD-115.0-1 | 9995 | GREELEY SUBSTATION | XCEL | WELD SUBSTATION | XCEL | 70209 | 70470 | Xcel Owned | 9995 135Y | CURRENT_TRANSFORMER | GRLY | 1200 | 1200 | 1200 | 1200 | 239 | 239 | 239 | 239
ROSE-ARRL-115.0-1 | 9996 | ROSEDALE SUBSTATION | XCEL | ARROWHEAD SUBSTATION | XCEL | 70368 | 70475 | Xcel Owned | ROSE-ARRL-115.0-1 | FACILITY |  | 800 | 880 | 910 | 1001 | 159 | 175 | 181 | 199
ROSE-ARRL-115.0-1 | 9996 | ROSEDALE SUBSTATION | XCEL | ARROWHEAD SUBSTATION | XCEL | 70368 | 70475 | Xcel Owned | ROSE-ARRL-115.0-1 | Transmission Line | 9996 | 800 | 880 | 910 | 1001 | 159 | 175 | 181 | 199
WELD-ARRL-115.0-1 | 9996 | WELD SUBSTATION | XCEL | ARROWHEAD SUBSTATION | XCEL | 70470 | 70475 | Xcel Owned | WELD-ARRL-115.0-1 | FACILITY |  | 800 | 880 | 910 | 1001 | 159 | 175 | 181 | 199
WELD-ARRL-115.0-1 | 9996 | WELD SUBSTATION | XCEL | ARROWHEAD SUBSTATION | XCEL | 70470 | 70475 | Xcel Owned | WELD-ARRL-115.0-1 | Transmission Line | 9996 | 800 | 880 | 910 | 1001 | 159 | 175 | 181 | 199
FNSS-LASS-345.0-1 | J05, 7005 | FINNEY SWITCHING STATION | XCEL | LAMAR 345KV SWITCHING STATION | XCEL | 523853 | 599950 | Xcel Owned | FNSS-LASS-345.0-1 | FACILITY |  | 636 | 636 | 1000 | 1000 | 380 | 380 | 598 | 598
FNSS-LASS-345.0-1 | J05, 7005 | FINNEY SWITCHING STATION | XCEL | LAMAR 345KV SWITCHING STATION | XCEL | 523853 | 599950 | Xcel Owned | FNSS-LASS-345.0-1 | Transmission Line | J05, 7005 | 636 | 636 | 1471 | 1471 | 380 | 380 | 879 | 879
FNSS-LASS-345.0-1 | J05, 7005 | FINNEY SWITCHING STATION | XCEL | LAMAR 345KV SWITCHING STATION | XCEL | 523853 | 599950 | Xcel Owned | 7002 246X | CURRENT_TRANSFORMER | LASS | 1000 | 1000 | 1000 | 1000 | 598 | 598 | 598 | 598

## Cover
SUBSTATION / TRANSMISSION FACILITY EQUIPMENT RATINGS FAC-008-5 Revision 2025-02 September, 2025
Temporary Rating For Bancrroft Outage (Valid Until 11-01-17)
e

## Instruction Sheet
Temporary Rating For Bancrroft Outage (Valid Until 11-01-17)
Xcel Energy is utilizing a new report format to publish facility ratings in accordance with FAC-008-5. Below are some notes on the new format for the Line and Transformer rating sheets:
Previous versions of the FAC-008 publication may have been set up to record a single row per facility rating. This new version will have multiple rows per facility depending on the number of limiting equipments. All row records with the same Facility Designation are part of the same facility.
Line Rating or Line Ratings In Construction
This report only includes the overall FACILITY rating and the LIMITING EQUIPMENT that is part of the transmission line facility.
Facility designation uses the following convention: [From Sub Mnemonic]-[To Sub Mnemonic]-[voltage level in kV]-[circuit #]. “_TP” in the mnemonic is used to identify transmission taps.
Equip Type is FACILITY is the record for the overall facility rating. The overall facility ratings are in BOLD RED font.
Equip Type is not FACILITY is the record for the limiting equipment for that facility designation. The ratings for the equipment are in RED font if it equals the overall facility rating. This is done to distinguish which equipment limits which rating. For instance, the Summer Normal rating for a facility may be limited by a Substation switch while the Summer Emergency, Winter Normal and Winter Emergency ratings are limited by a Current Transformer. In this case, the only Summer Normal rating of the switch will be highlighted in RED and the Summer Emergency, Winter Normal and Winter Emergency of the Current Transformer will be highlighted in RED.
From PSSE/ To PSSE have been provided for convenience. In some cases where the PSSE bus number is unknown/ missing pseudo bus numbers are used. For PSC the pseudo bus numbers are in the 2000 series (2xxx).
Transformers or Transformers Ratings In Construction
This report only includes the overall FACILITY rating and the LIMITING EQUIPMENT that is part of the transmission transformer facility.
Facility designation uses the following convention: [Sub Mnemonic]-[Transformer Number]-[High side voltage in kV]-[Low side voltage level in kV]-[Tertiary voltage in kV, if applicable]-HX.
Equip Type is FACILITY is the record for the overall facility rating. The overall facility ratings are in BOLD RED font.
Equip Type is not FACILITY is the record for the limiting equipment for that facility designation. The ratings for the equipment are in RED font if it equals the overall facility rating. This is done to distinguish which equipment limits which rating. For instance, the Summer Normal rating for a facility may be limited by a Substation switch while the Summer Emergency, Winter Normal and Winter Emergency ratings are limited by a Current Transformer. In this case, the only Summer Normal rating of the switch will be highlighted in RED and the Summer Emergency, Winter Normal and Winter Emergency of the Current Transformer will be highlighted in RED.
High Side PSSE/ Low Side PSSE have been provided for convenience. In some cases where the PSSE bus number is unknown/ missing pseudo bus numbers are used. For PSC the pseudo bus numbers are in the 2000 series (2xxx) or -1.

## Line Ratings
|  |  | FAC-008-5 Transmission Lines |  |  |  | OPCO: PSC |  |  | VALIDATION STATUS: VALID | [5 empty] | OWNERSHIP: Jointly Owned,Xcel Owned
[7 empty] | BES: Y |  |  | LIFE CYCLE STATUS: AS BUILT
FACILITY DESIGNATION | LINE NAME | FROM SUB | FROM SUB OWNER | TO SUB | TO SUB OWNER | FROM PSSE | TO PSSE | FACILITY OWNERSHIP | EQUIP NAME | EQUIP TYPE | EQUIP LOCATION | SN (AMPS) | SE (AMPS) | WN (AMPS) | WE (AMPS) | SN (MVA) | SE (MVA) | WN (MVA) | WE (MVA) | COMMENTS
ADKO_TP-GILC-115.0-1 | 9494 | ANADARKO TAP | XCEL | GILCREST SUBSTATION | XCEL | 70219 | 70198 | Xcel Owned | ADKO_TP-GILC-115.0-1 | FACILITY |  | 803 | 883 | 913 | 1004 | 160 | 176 | 182 | 200
ADKO_TP-GILC-115.0-1 | 9494 | ANADARKO TAP | XCEL | GILCREST SUBSTATION | XCEL | 70219 | 70198 | Xcel Owned | ADKO_TP-GILC-115.0-1 | Transmission Line | 9494 | 803 | 883 | 913 | 1004 | 160 | 176 | 182 | 200
ADKO_TP-VASQ-115.0-1 | 9494 | ANADARKO TAP | XCEL | VASQUEZ SUBSTATION | XCEL | 70219 | 70450 | Xcel Owned | ADKO_TP-VASQ-115.0-1 | FACILITY |  | 803 | 883 | 912 | 1004 | 160 | 176 | 182 | 200
ADKO_TP-VASQ-115.0-1 | 9494 | ANADARKO TAP | XCEL | VASQUEZ SUBSTATION | XCEL | 70219 | 70450 | Xcel Owned | ADKO_TP-VASQ-115.0-1 | Transmission Line | 9494 | 803 | 883 | 912 | 1004 | 160 | 176 | 182 | 200
ADOB-UINT-230.0-1 | 5555 | ADOBE SUBSTATION | XCEL | UINTAH SUBSTATION | XCEL | 70268 | 70438 | Xcel Owned | ADOB-UINT-230.0-1 | FACILITY |  | 791 | 791 | 795 | 795 | 315 | 315 | 317 | 317 | Railroad Documentation
ADOB-UINT-230.0-1 | 5555 | ADOBE SUBSTATION | XCEL | UINTAH SUBSTATION | XCEL | 70268 | 70438 | Xcel Owned | ADOB-UINT-230.0-1 | Transmission Line | 5555 | 791 | 791 | 795 | 795 | 315 | 315 | 317 | 317
ALLI-KEND-115.0-1 | 8024 | ALLISON SUBSTATION | XCEL | KENDRICK SUBSTATION | XCEL | 70023 | 70242 | Xcel Owned | ALLI-KEND-115.0-1 | FACILITY |  | 710 | 781 | 710 | 781 | 141 | 156 | 141 | 156
ALLI-KEND-115.0-1 | 8024 | ALLISON SUBSTATION | XCEL | KENDRICK SUBSTATION | XCEL | 70023 | 70242 | Xcel Owned | ALLI-KEND-115.0-1 | Transmission Line | 8024 | 710 | 781 | 710 | 781 | 141 | 156 | 141 | 156
ALLI-SODA-115.0-1 | 8024 | ALLISON SUBSTATION | XCEL | SODA LAKES SUBSTATION | XCEL | 70023 | 70400 | Xcel Owned | ALLI-SODA-115.0-1 | FACILITY |  | 950 | 1045 | 950 | 1045 | 189 | 208 | 189 | 208
ALLI-SODA-115.0-1 | 8024 | ALLISON SUBSTATION | XCEL | SODA LAKES SUBSTATION | XCEL | 70023 | 70400 | Xcel Owned | ALLI-SODA-115.0-1 | Transmission Line | 8024 | 950 | 1045 | 950 | 1045 | 189 | 208 | 189 | 208
ALMA-BREC-230.0-1 | 5487 | ALMA SUBSTATION | XCEL | BRECKENRIDGE SUBSTATION | XCEL | 70032 | 70064 | Xcel Owned | ALMA-BREC-230.0-1 | FACILITY |  | 1783 | 2000 | 2000 | 2000 | 710 | 797 | 797 | 797
ALMA-BREC-230.0-1 | 5487 | ALMA SUBSTATION | XCEL | BRECKENRIDGE SUBSTATION | XCEL | 70032 | 70064 | Xcel Owned | 2½" (AL 40) | BUSBAR_SECTION | ALMA | 1783 | 2140 | 2174 | 2462 | 710 | 853 | 866 | 981
ALMA-BREC-230.0-1 | 5487 | ALMA SUBSTATION | XCEL | BRECKENRIDGE SUBSTATION | XCEL | 70032 | 70064 | Xcel Owned | 5487-3 | CIRCUIT_SWITCHER | ALMA | 2000 | 2000 | 2000 | 2000 | 797 | 797 | 797 | 797
ALMA-MALT-230.0-1 | 5487 | ALMA SUBSTATION | XCEL | MALTA SUBSTATION | XCEL | 70032 | 70274 | Xcel Owned | ALMA-MALT-230.0-1 | FACILITY |  | 1037 | 1200 | 1200 | 1200 | 413 | 478 | 478 | 478
ALMA-MALT-230.0-1 | 5487 | ALMA SUBSTATION | XCEL | MALTA SUBSTATION | XCEL | 70032 | 70274 | Xcel Owned | Curlew | BUSBAR_SECTION | MALT | 1037 | 1215 | 1244 | 1387 | 413 | 484 | 496 | 553
ALMA-MALT-230.0-1 | 5487 | ALMA SUBSTATION | XCEL | MALTA SUBSTATION | XCEL | 70032 | 70274 | Xcel Owned | 5487 135Y | CURRENT_TRANSFORMER | MALT | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
ALMA-MALT-230.0-1 | 5487 | ALMA SUBSTATION | XCEL | MALTA SUBSTATION | XCEL | 70032 | 70274 | Xcel Owned | 5487 135X | CURRENT_TRANSFORMER | MALT | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
ALMA-MALT-230.0-1 | 5487 | ALMA SUBSTATION | XCEL | MALTA SUBSTATION | XCEL | 70032 | 70274 | Xcel Owned | 5487 246X | CURRENT_TRANSFORMER | MALT | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
ALMA-MALT-230.0-1 | 5487 | ALMA SUBSTATION | XCEL | MALTA SUBSTATION | XCEL | 70032 | 70274 | Xcel Owned | 5487 246Y | CURRENT_TRANSFORMER | MALT | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
ARAP-ARLQ_TP-115.0-1 | 9332 | ARAPAHOE SUBSTATION | XCEL | AIR LIQUIDE TAP | XCEL | 70036 | 70531 | Xcel Owned | ARAP-ARLQ_TP-115.0-1 | FACILITY |  | 600 | 775 | 743 | 890 | 120 | 154 | 148 | 177
ARAP-ARLQ_TP-115.0-1 | 9332 | ARAPAHOE SUBSTATION | XCEL | AIR LIQUIDE TAP | XCEL | 70036 | 70531 | Xcel Owned | 9332M | SWITCH | ARAP | 600 | 775 | 743 | 890 | 120 | 154 | 148 | 177
ARAP-DAKO-230.0-1 | 5623 | ARAPAHOE SUBSTATION | XCEL | DAKOTA SUBSTATION | XCEL | 70038 | 70141 | Xcel Owned | ARAP-DAKO-230.0-1 | FACILITY |  | 1426 | 1568 | 1625 | 1787 | 568 | 625 | 647 | 712
ARAP-DAKO-230.0-1 | 5623 | ARAPAHOE SUBSTATION | XCEL | DAKOTA SUBSTATION | XCEL | 70038 | 70141 | Xcel Owned | Narcissus | BUSBAR_SECTION | DAKO | 1426 | 1568 | 1625 | 1787 | 568 | 625 | 647 | 712
ARAP-DTER-230.0-1 | 5449 | ARAPAHOE SUBSTATION | XCEL | DENVER TERMINAL SUBSTATION | XCEL | 70038 | 70149 | Xcel Owned | ARAP-DTER-230.0-1 | FACILITY |  | 1444 | 1588 | 1645 | 1810 | 575 | 633 | 655 | 721
ARAP-DTER-230.0-1 | 5449 | ARAPAHOE SUBSTATION | XCEL | DENVER TERMINAL SUBSTATION | XCEL | 70038 | 70149 | Xcel Owned | ARAP-DTER-230.0-1 | Transmission Line | 5449 | 1444 | 1588 | 1645 | 1810 | 575 | 633 | 655 | 721
ARAP-ENGL-115.0-1 | 9336 | ARAPAHOE SUBSTATION | XCEL | ENGLEWOOD SUBSTATION | XCEL | 70037 | 70167 | Xcel Owned | ARAP-ENGL-115.0-1 | FACILITY |  | 799 | 879 | 869 | 956 | 159 | 175 | 173 | 190
ARAP-ENGL-115.0-1 | 9336 | ARAPAHOE SUBSTATION | XCEL | ENGLEWOOD SUBSTATION | XCEL | 70037 | 70167 | Xcel Owned | Hawk | BUSBAR_SECTION | ARAP | 799 | 879 | 909 | 999 | 159 | 175 | 181 | 199
ARAP-ENGL-115.0-1 | 9336 | ARAPAHOE SUBSTATION | XCEL | ENGLEWOOD SUBSTATION | XCEL | 70037 | 70167 | Xcel Owned | ARAP-ENGL-115.0-1 | Transmission Line | 9336 | 803 | 883 | 869 | 956 | 160 | 176 | 173 | 190
ARAP-GREE-230.0-1 | 5709 | ARAPAHOE SUBSTATION | XCEL | GREENWOOD SUBSTATION | XCEL | 70038 | 70189 | Xcel Owned | ARAP-GREE-230.0-1 | FACILITY |  | 1440 | 1584 | 1642 | 1806 | 574 | 631 | 654 | 719
ARAP-GREE-230.0-1 | 5709 | ARAPAHOE SUBSTATION | XCEL | GREENWOOD SUBSTATION | XCEL | 70038 | 70189 | Xcel Owned | ARAP-GREE-230.0-1 | Transmission Line | 5709 | 1440 | 1584 | 1642 | 1806 | 574 | 631 | 654 | 719
ARAP-SANT-230.0-1 | 5107 | ARAPAHOE SUBSTATION | XCEL | SANTA FE SUBSTATION | XCEL | 70038 | 70527 | Xcel Owned | ARAP-SANT-230.0-1 | FACILITY |  | 1266 | 1393 | 1443 | 1587 | 504 | 555 | 575 | 632
ARAP-SANT-230.0-1 | 5107 | ARAPAHOE SUBSTATION | XCEL | SANTA FE SUBSTATION | XCEL | 70038 | 70527 | Xcel Owned | ARAP-SANT-230.0-1 | Transmission Line | 5107 | 1266 | 1393 | 1443 | 1587 | 504 | 555 | 575 | 632
ARAP-SOUT_TP-115.0-1 | 9335 | ARAPAHOE SUBSTATION | XCEL | SOUTH TAP | XCEL | 70037 | 70398 | Xcel Owned | ARAP-SOUT_TP-115.0-1 | FACILITY |  | 798 | 878 | 908 | 998 | 159 | 175 | 181 | 199
ARAP-SOUT_TP-115.0-1 | 9335 | ARAPAHOE SUBSTATION | XCEL | SOUTH TAP | XCEL | 70037 | 70398 | Xcel Owned | ARAP-SOUT_TP-115.0-1 | Transmission Line | 9335 | 798 | 878 | 908 | 998 | 159 | 175 | 181 | 199
ARAP-UNIV-115.0-1 | 9338 | ARAPAHOE SUBSTATION | XCEL | UNIVERSITY SUBSTATION | XCEL | 70036 | 70441 | Xcel Owned | ARAP-UNIV-115.0-1 | FACILITY |  | 773 | 773 | 773 | 773 | 154 | 154 | 154 | 154
ARAP-UNIV-115.0-1 | 9338 | ARAPAHOE SUBSTATION | XCEL | UNIVERSITY SUBSTATION | XCEL | 70036 | 70441 | Xcel Owned | ARAP-UNIV-115.0-1 | Transmission Line | 9338 | 773 | 773 | 773 | 773 | 154 | 154 | 154 | 154
ARGO-CHER-115.0-1 | 9413 | ARGO SUBSTATION | XCEL | CHEROKEE SWITCHYARD SUBSTATION | XCEL | 70039 | 70108 | Xcel Owned | ARGO-CHER-115.0-1 | FACILITY |  | 1200 | 1427 | 1458 | 1600 | 239 | 284 | 290 | 319
ARGO-CHER-115.0-1 | 9413 | ARGO SUBSTATION | XCEL | CHEROKEE SWITCHYARD SUBSTATION | XCEL | 70039 | 70108 | Xcel Owned | 9537N | SWITCH | CHER | 1200 | 1549 | 1486 | 1780 | 239 | 309 | 296 | 355
ARGO-CHER-115.0-1 | 9413 | ARGO SUBSTATION | XCEL | CHEROKEE SWITCHYARD SUBSTATION | XCEL | 70039 | 70108 | Xcel Owned | 9537S | SWITCH | CHER | 1200 | 1549 | 1486 | 1780 | 239 | 309 | 296 | 355
ARGO-CHER-115.0-1 | 9413 | ARGO SUBSTATION | XCEL | CHEROKEE SWITCHYARD SUBSTATION | XCEL | 70039 | 70108 | Xcel Owned | 9556L | SWITCH | CHER | 1200 | 1549 | 1486 | 1780 | 239 | 309 | 296 | 355
ARGO-CHER-115.0-1 | 9413 | ARGO SUBSTATION | XCEL | CHEROKEE SWITCHYARD SUBSTATION | XCEL | 70039 | 70108 | Xcel Owned | 9413W | SWITCH | CHER | 1200 | 1549 | 1486 | 1780 | 239 | 309 | 296 | 355
ARGO-CHER-115.0-1 | 9413 | ARGO SUBSTATION | XCEL | CHEROKEE SWITCHYARD SUBSTATION | XCEL | 70039 | 70108 | Xcel Owned | 9556E | SWITCH | CHER | 1200 | 1549 | 1486 | 1780 | 239 | 309 | 296 | 355
ARGO-CHER-115.0-1 | 9413 | ARGO SUBSTATION | XCEL | CHEROKEE SWITCHYARD SUBSTATION | XCEL | 70039 | 70108 | Xcel Owned | 9413L | SWITCH | CHER | 1200 | 1549 | 1486 | 1780 | 239 | 309 | 296 | 355
ARGO-CHER-115.0-1 | 9413 | ARGO SUBSTATION | XCEL | CHEROKEE SWITCHYARD SUBSTATION | XCEL | 70039 | 70108 | Xcel Owned | Narcissus | BUSBAR_SECTION | CHER | 1220 | 1427 | 1458 | 1626 | 243 | 284 | 290 | 324
ARGO-CHER-115.0-1 | 9413 | ARGO SUBSTATION | XCEL | CHEROKEE SWITCHYARD SUBSTATION | XCEL | 70039 | 70108 | Xcel Owned | 9556 | BREAKER | CHER | 1600 | 1600 | 1600 | 1600 | 319 | 319 | 319 | 319
ARGO-CHER-115.0-1 | 9413 | ARGO SUBSTATION | XCEL | CHEROKEE SWITCHYARD SUBSTATION | XCEL | 70039 | 70108 | Xcel Owned | 9413 | BREAKER | CHER | 1600 | 1600 | 1600 | 1600 | 319 | 319 | 319 | 319
ARGO-DTER-115.0-1 | 9004 | ARGO SUBSTATION | XCEL | DENVER TERMINAL SUBSTATION | XCEL | 70039 | 70148 | Xcel Owned | ARGO-DTER-115.0-1 | FACILITY |  | 2393 | 2400 | 2400 | 2400 | 477 | 478 | 478 | 478
ARGO-DTER-115.0-1 | 9004 | ARGO SUBSTATION | XCEL | DENVER TERMINAL SUBSTATION | XCEL | 70039 | 70148 | Xcel Owned | Magnolia | BUSBAR_SECTION | ARGO | 2393 | 2632 | 2724 | 2996 | 477 | 524 | 543 | 597
ARGO-DTER-115.0-1 | 9004 | ARGO SUBSTATION | XCEL | DENVER TERMINAL SUBSTATION | XCEL | 70039 | 70148 | Xcel Owned | ARGO-DTER-115.0-1 | Transmission Line | 9004 | 2393 | 2632 | 2725 | 2997 | 477 | 524 | 543 | 597
ARGO-DTER-115.0-1 | 9004 | ARGO SUBSTATION | XCEL | DENVER TERMINAL SUBSTATION | XCEL | 70039 | 70148 | Xcel Owned | 9004 135X | CURRENT_TRANSFORMER | ARGO | 2400 | 2400 | 2400 | 2400 | 478 | 478 | 478 | 478
ARGO-DTER-115.0-1 | 9004 | ARGO SUBSTATION | XCEL | DENVER TERMINAL SUBSTATION | XCEL | 70039 | 70148 | Xcel Owned | 9004_135Y_PK | SECONDARY_CURRENT_LIMITATION | ARGO | 2400 | 2400 | 2400 | 2400 | 478 | 478 | 478 | 478
ARGO-DTER-115.0-1 | 9004 | ARGO SUBSTATION | XCEL | DENVER TERMINAL SUBSTATION | XCEL | 70039 | 70148 | Xcel Owned | 9004 246X | CURRENT_TRANSFORMER | DTER | 2400 | 2400 | 2400 | 2400 | 478 | 478 | 478 | 478
ARGO-DTER-115.0-1 | 9004 | ARGO SUBSTATION | XCEL | DENVER TERMINAL SUBSTATION | XCEL | 70039 | 70148 | Xcel Owned | 9004 135Y | CURRENT_TRANSFORMER | ARGO | 2400 | 2400 | 2400 | 2400 | 478 | 478 | 478 | 478
ARGO-DTER-115.0-1 | 9004 | ARGO SUBSTATION | XCEL | DENVER TERMINAL SUBSTATION | XCEL | 70039 | 70148 | Xcel Owned | 9004 246X PK | SECONDARY_CURRENT_LIMITATION | DTER | 2400 | 2400 | 2400 | 2400 | 478 | 478 | 478 | 478
ARGO-DTER-115.0-1 | 9004 | ARGO SUBSTATION | XCEL | DENVER TERMINAL SUBSTATION | XCEL | 70039 | 70148 | Xcel Owned | 9004_135X_PK | SECONDARY_CURRENT_LIMITATION | ARGO | 2400 | 2400 | 2400 | 2400 | 478 | 478 | 478 | 478
ARGO-DTER-115.0-1 | 9004 | ARGO SUBSTATION | XCEL | DENVER TERMINAL SUBSTATION | XCEL | 70039 | 70148 | Xcel Owned | 9004 135Y | CURRENT_TRANSFORMER | DTER | 2400 | 2400 | 2400 | 2400 | 478 | 478 | 478 | 478
ARGO-DTER-115.0-1 | 9004 | ARGO SUBSTATION | XCEL | DENVER TERMINAL SUBSTATION | XCEL | 70039 | 70148 | Xcel Owned | 9004 135Y PK-2 | SECONDARY_CURRENT_LIMITATION | DTER | 2400 | 2400 | 2400 | 2400 | 478 | 478 | 478 | 478
ARGO-DTER-115.0-1 | 9004 | ARGO SUBSTATION | XCEL | DENVER TERMINAL SUBSTATION | XCEL | 70039 | 70148 | Xcel Owned | 9004 135X | CURRENT_TRANSFORMER | DTER | 2400 | 2400 | 2400 | 2400 | 478 | 478 | 478 | 478
ARSE-HAVA-115.0-1 | 9543 | ARSENAL | XCEL | HAVANA SUBSTATION | XCEL | 70040 | 70217 | Xcel Owned | ARSE-HAVA-115.0-1 | FACILITY |  | 799 | 879 | 909 | 999 | 159 | 175 | 181 | 199
ARSE-HAVA-115.0-1 | 9543 | ARSENAL | XCEL | HAVANA SUBSTATION | XCEL | 70040 | 70217 | Xcel Owned | ARSE-HAVA-115.0-1 | Transmission Line | 9543 | 799 | 879 | 909 | 999 | 159 | 175 | 181 | 199
ARSE-HAVA-115.0-1 | 9543 | ARSENAL | XCEL | HAVANA SUBSTATION | XCEL | 70040 | 70217 | Xcel Owned | Hawk | BUSBAR_SECTION | ARSE | 799 | 879 | 909 | 999 | 159 | 175 | 181 | 199
ARVA-CHER-230.0-1 | 5067 | ARVADA SUBSTATION | XCEL | CHEROKEE SWITCHYARD SUBSTATION | XCEL | 70041 | 70107 | Xcel Owned | ARVA-CHER-230.0-1 | FACILITY |  | 1091 | 1271 | 1303 | 1448 | 435 | 506 | 519 | 577
ARVA-CHER-230.0-1 | 5067 | ARVADA SUBSTATION | XCEL | CHEROKEE SWITCHYARD SUBSTATION | XCEL | 70041 | 70107 | Xcel Owned | Curlew | BUSBAR_SECTION | CHER | 1091 | 1271 | 1303 | 1448 | 435 | 506 | 519 | 577
ARVA-RIDG_TP-230.0-1 | 5067 | ARVADA SUBSTATION | XCEL | RIDGE TAP | XCEL | 70041 | 2210 | Xcel Owned | ARVA-RIDG_TP-230.0-1 | FACILITY |  | 1268 | 1395 | 1444 | 1589 | 505 | 556 | 575 | 633
ARVA-RIDG_TP-230.0-1 | 5067 | ARVADA SUBSTATION | XCEL | RIDGE TAP | XCEL | 70041 | 2210 | Xcel Owned | ARVA-RIDG_TP-230.0-1 | Transmission Line | 5067 | 1268 | 1395 | 1444 | 1589 | 505 | 556 | 575 | 633
ATER-BLPK-115.0-1 | 8004 | ALAMOSA TERMINAL SUBSTATION | XCEL | BLANCA PEAK SUBSTATION | XCEL | 70025 | 70937 | Xcel Owned | ATER-BLPK-115.0-1 | FACILITY |  | 815 | 896 | 894 | 983 | 162 | 178 | 178 | 196
ATER-BLPK-115.0-1 | 8004 | ALAMOSA TERMINAL SUBSTATION | XCEL | BLANCA PEAK SUBSTATION | XCEL | 70025 | 70937 | Xcel Owned | ATER-BLPK-115.0-1 | Transmission Line | 8004 | 815 | 896 | 894 | 983 | 162 | 178 | 178 | 196
BANC-GRAY-115.0-1 | 9448 | BANCROFT SUBSTATION | XCEL | GRAY STREET SUBSTATION | XCEL | 70045 | 70208 | Xcel Owned | BANC-GRAY-115.0-1 | FACILITY |  | 797 | 877 | 907 | 997 | 159 | 175 | 181 | 199
BANC-GRAY-115.0-1 | 9448 | BANCROFT SUBSTATION | XCEL | GRAY STREET SUBSTATION | XCEL | 70045 | 70208 | Xcel Owned | BANC-GRAY-115.0-1 | Transmission Line | 9448 | 797 | 877 | 907 | 997 | 159 | 175 | 181 | 199
BANC-KEND-115.0-1 | 8024 | BANCROFT SUBSTATION | XCEL | KENDRICK SUBSTATION | XCEL | 70045 | 70242 | Xcel Owned | BANC-KEND-115.0-1 | FACILITY |  | 795 | 874 | 904 | 994 | 158 | 174 | 180 | 198
BANC-KEND-115.0-1 | 8024 | BANCROFT SUBSTATION | XCEL | KENDRICK SUBSTATION | XCEL | 70045 | 70242 | Xcel Owned | Hawk | BUSBAR_SECTION | KEND | 795 | 874 | 904 | 994 | 158 | 174 | 180 | 198
BANC-SOUT_TP-115.0-1 | 9335 | BANCROFT SUBSTATION | XCEL | SOUTH TAP | XCEL | 70045 | 70398 | Xcel Owned | BANC-SOUT_TP-115.0-1 | FACILITY |  | 797 | 877 | 907 | 997 | 159 | 175 | 181 | 199
BANC-SOUT_TP-115.0-1 | 9335 | BANCROFT SUBSTATION | XCEL | SOUTH TAP | XCEL | 70045 | 70398 | Xcel Owned | BANC-SOUT_TP-115.0-1 | Transmission Line | 9335 | 797 | 877 | 907 | 997 | 159 | 175 | 181 | 199
BARR-GRVL-230.0-1 | 5759 | BARR LAKE SUBSTATION | XCEL | GREEN VALLEY SUBSTATION | XCEL | 70047 | 70048 | Xcel Owned | BARR-GRVL-230.0-1 | FACILITY |  | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
BARR-GRVL-230.0-1 | 5759 | BARR LAKE SUBSTATION | XCEL | GREEN VALLEY SUBSTATION | XCEL | 70047 | 70048 | Xcel Owned | TL5759 XAMP | SECONDARY_CURRENT_LIMITATION | BARR | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
BARR-GRVL-230.0-1 | 5759 | BARR LAKE SUBSTATION | XCEL | GREEN VALLEY SUBSTATION | XCEL | 70047 | 70048 | Xcel Owned | 5759 135Y | CURRENT_TRANSFORMER | BARR | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
BARR-GRVL-230.0-1 | 5759 | BARR LAKE SUBSTATION | XCEL | GREEN VALLEY SUBSTATION | XCEL | 70047 | 70048 | Xcel Owned | TL5759 W/VAR | SECONDARY_CURRENT_LIMITATION | BARR | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
BARR-GRVL-230.0-1 | 5759 | BARR LAKE SUBSTATION | XCEL | GREEN VALLEY SUBSTATION | XCEL | 70047 | 70048 | Xcel Owned | 5759 246Y | CURRENT_TRANSFORMER | BARR | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
BARR-REUN-230.0-1 | 5875 | BARR LAKE SUBSTATION | XCEL | REUNION (TSGT) | FOREIGN | 70047 | 72026 | Xcel Owned | BARR-REUN-230.0-1 | FACILITY |  | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
BARR-REUN-230.0-1 | 5875 | BARR LAKE SUBSTATION | XCEL | REUNION (TSGT) | FOREIGN | 70047 | 72026 | Xcel Owned | 5875 135Y | CURRENT_TRANSFORMER | BARR | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
BARR-REUN-230.0-1 | 5875 | BARR LAKE SUBSTATION | XCEL | REUNION (TSGT) | FOREIGN | 70047 | 72026 | Xcel Owned | TL5875 W/VAR | SECONDARY_CURRENT_LIMITATION | BARR | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
BARR-REUN-230.0-1 | 5875 | BARR LAKE SUBSTATION | XCEL | REUNION (TSGT) | FOREIGN | 70047 | 72026 | Xcel Owned | TL5875 XAMP | SECONDARY_CURRENT_LIMITATION | BARR | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
BARR-REUN-230.0-1 | 5875 | BARR LAKE SUBSTATION | XCEL | REUNION (TSGT) | FOREIGN | 70047 | 72026 | Xcel Owned | 5875 246Y | CURRENT_TRANSFORMER | BARR | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
BASA-HOPK_TP-115.0-1 | 9256 | BASALT SUBSTATION | XCEL | HOPKINS TAP | XCEL | 79003 | 2203 | Xcel Owned | BASA-HOPK_TP-115.0-1 | FACILITY |  | 433 | 476 | 477 | 525 | 86 | 95 | 95 | 105
BASA-HOPK_TP-115.0-1 | 9256 | BASALT SUBSTATION | XCEL | HOPKINS TAP | XCEL | 79003 | 2203 | Xcel Owned | BASA-HOPK_TP-115.0-1 | Transmission Line | 9256 | 433 | 476 | 477 | 525 | 86 | 95 | 95 | 105
BCRK-AVON-115.0-1 | 8424 | BEAVER CREEK WEST SUBSTATION | XCEL | AVON SUBSTATION | XCEL | 79006 | 79092 | Jointly Owned | BCRK-AVON-115.0-1 | FACILITY |  | 600 | 600 | 600 | 600 | 120 | 120 | 120 | 120
BCRK-AVON-115.0-1 | 8424 | BEAVER CREEK WEST SUBSTATION | XCEL | AVON SUBSTATION | XCEL | 79006 | 79092 | Jointly Owned | BC551 135X | CURRENT_TRANSFORMER | BCRK | 600 | 600 | 600 | 600 | 120 | 120 | 120 | 120
BCRK-AVON-115.0-1 | 8424 | BEAVER CREEK WEST SUBSTATION | XCEL | AVON SUBSTATION | XCEL | 79006 | 79092 | Jointly Owned | 514 | SWITCH | AVON | 600 | 775 | 743 | 890 | 120 | 154 | 148 | 177
BCRK-AVON-115.0-1 | 8424 | BEAVER CREEK WEST SUBSTATION | XCEL | AVON SUBSTATION | XCEL | 79006 | 79092 | Jointly Owned | 564 | SWITCH | AVON | 600 | 775 | 743 | 890 | 120 | 154 | 148 | 177
BCRK-AVON-115.0-1 | 8424 | BEAVER CREEK WEST SUBSTATION | XCEL | AVON SUBSTATION | XCEL | 79006 | 79092 | Jointly Owned | 532 | SWITCH | AVON | 600 | 775 | 743 | 890 | 120 | 154 | 148 | 177
BCRK-AVON-115.0-1 | 8424 | BEAVER CREEK WEST SUBSTATION | XCEL | AVON SUBSTATION | XCEL | 79006 | 79092 | Jointly Owned | 512 | SWITCH | AVON | 600 | 775 | 743 | 890 | 120 | 154 | 148 | 177
BCRK-AVON-115.0-1 | 8424 | BEAVER CREEK WEST SUBSTATION | XCEL | AVON SUBSTATION | XCEL | 79006 | 79092 | Jointly Owned | 552 | SWITCH | AVON | 600 | 775 | 743 | 890 | 120 | 154 | 148 | 177
BCRK-AVON-115.0-1 | 8424 | BEAVER CREEK WEST SUBSTATION | XCEL | AVON SUBSTATION | XCEL | 79006 | 79092 | Jointly Owned | BC552 | SWITCH | BCRK | 600 | 775 | 743 | 890 | 120 | 154 | 148 | 177
BCRK-AVON-115.0-1 | 8424 | BEAVER CREEK WEST SUBSTATION | XCEL | AVON SUBSTATION | XCEL | 79006 | 79092 | Jointly Owned | BC554 | SWITCH | BCRK | 600 | 775 | 743 | 890 | 120 | 154 | 148 | 177
BCRK-AVON-115.0-1 | 8424 | BEAVER CREEK WEST SUBSTATION | XCEL | AVON SUBSTATION | XCEL | 79006 | 79092 | Jointly Owned | 534 | SWITCH | AVON | 600 | 775 | 743 | 890 | 120 | 154 | 148 | 177
BCRK-AVON-115.0-1 | 8424 | BEAVER CREEK WEST SUBSTATION | XCEL | AVON SUBSTATION | XCEL | 79006 | 79092 | Jointly Owned | 554 | SWITCH | AVON | 600 | 775 | 743 | 890 | 120 | 154 | 148 | 177
BCRK-WOLC-115.0-1 | 8415 | BEAVER CREEK WEST SUBSTATION | XCEL | WOLCOTT (HCEA) | FOREIGN | 79006 | 77643 | Jointly Owned | BCRK-WOLC-115.0-1 | FACILITY |  | 600 | 600 | 600 | 600 | 120 | 120 | 120 | 120
BCRK-WOLC-115.0-1 | 8415 | BEAVER CREEK WEST SUBSTATION | XCEL | WOLCOTT (HCEA) | FOREIGN | 79006 | 77643 | Jointly Owned | BC541 135X | CURRENT_TRANSFORMER | BCRK | 600 | 600 | 600 | 600 | 120 | 120 | 120 | 120
BCRK-WOLC-115.0-1 | 8415 | BEAVER CREEK WEST SUBSTATION | XCEL | WOLCOTT (HCEA) | FOREIGN | 79006 | 77643 | Jointly Owned | Foreign Ratings | Foreign Ratings | WOLC | 600 | 600 | 743 | 743 | 120 | 120 | 148 | 148
BCRK-WOLC-115.0-1 | 8415 | BEAVER CREEK WEST SUBSTATION | XCEL | WOLCOTT (HCEA) | FOREIGN | 79006 | 77643 | Jointly Owned | BC544 | SWITCH | BCRK | 600 | 775 | 743 | 890 | 120 | 154 | 148 | 177
BEAV-STOR-230.0-1 | 5265 | BEAVER CREEK EAST SUBSTATION | XCEL | STORY SUBSTATION | XCEL | 70399 | 73192 | Jointly Owned | BEAV-STOR-230.0-1 | FACILITY |  | 695 | 695 | 695 | 695 | 277 | 277 | 277 | 277
BEAV-STOR-230.0-1 | 5265 | BEAVER CREEK EAST SUBSTATION | XCEL | STORY SUBSTATION | XCEL | 70399 | 73192 | Jointly Owned | Foreign Ratings | Foreign Ratings | STOR | 695 | 695 | 695 | 695 | 277 | 277 | 277 | 277
BHYD-NCAR-115.0-1 | 9205 | BOULDER CANYON SWYD | XCEL | NCAR SUBSTATION | XCEL | 70058 | 70295 | Xcel Owned | BHYD-NCAR-115.0-1 | FACILITY |  | 912 | 1063 | 1087 | 1200 | 182 | 212 | 217 | 239
BHYD-NCAR-115.0-1 | 9205 | BOULDER CANYON SWYD | XCEL | NCAR SUBSTATION | XCEL | 70058 | 70295 | Xcel Owned | Arbutus | BUSBAR_SECTION | NCAR | 912 | 1063 | 1087 | 1210 | 182 | 212 | 217 | 241
BHYD-NCAR-115.0-1 | 9205 | BOULDER CANYON SWYD | XCEL | NCAR SUBSTATION | XCEL | 70058 | 70295 | Xcel Owned | 9205_246X_PK | SECONDARY_CURRENT_LIMITATION | BHYD | 1200 | 1200 | 1200 | 1200 | 239 | 239 | 239 | 239
BHYD-NCAR-115.0-1 | 9205 | BOULDER CANYON SWYD | XCEL | NCAR SUBSTATION | XCEL | 70058 | 70295 | Xcel Owned | 9200_135X_PK | SECONDARY_CURRENT_LIMITATION | BHYD | 1200 | 1200 | 1200 | 1200 | 239 | 239 | 239 | 239
BHYD-SUNS-115.0-1 | 9216 | BOULDER CANYON SWYD | XCEL | SUNSHINE CANYON SUBSTATION | XCEL | 70058 | 70424 | Xcel Owned | BHYD-SUNS-115.0-1 | FACILITY |  | 627 | 689 | 712 | 783 | 125 | 137 | 142 | 156
BHYD-SUNS-115.0-1 | 9216 | BOULDER CANYON SWYD | XCEL | SUNSHINE CANYON SUBSTATION | XCEL | 70058 | 70424 | Xcel Owned | Merlin | BUSBAR_SECTION | SUNS | 627 | 689 | 712 | 783 | 125 | 137 | 142 | 156
BIGH-COMA-230.0-1 | 55173 | BIGHORN SOLAR | FOREIGN | COMANCHE SUBSTATION | XCEL | 70875 | 70122 | Jointly Owned | BIGH-COMA-230.0-1 | FACILITY |  | 665 | 665 | 665 | 665 | 265 | 265 | 265 | 265
BIGH-COMA-230.0-1 | 55173 | BIGHORN SOLAR | FOREIGN | COMANCHE SUBSTATION | XCEL | 70875 | 70122 | Jointly Owned | Foreign Ratings | Foreign Ratings | BIGH | 665 | 665 | 665 | 665 | 265 | 265 | 265 | 265
BLUE-MILL-115.0-1 | 8055 | BLUE RIVER SUBSTATION | XCEL | MILL SUBSTATION | XCEL | 70052 | 70287 | Jointly Owned | BLUE-MILL-115.0-1 | FACILITY |  | 767 | 792 | 836 | 836 | 153 | 158 | 167 | 167
BLUE-MILL-115.0-1 | 8055 | BLUE RIVER SUBSTATION | XCEL | MILL SUBSTATION | XCEL | 70052 | 70287 | Jointly Owned | Hawk | BUSBAR_SECTION | MILL | 767 | 844 | 874 | 962 | 153 | 168 | 174 | 192
BLUE-MILL-115.0-1 | 8055 | BLUE RIVER SUBSTATION | XCEL | MILL SUBSTATION | XCEL | 70052 | 70287 | Jointly Owned |  | LINE_TRAP | BLUE | 792 | 792 | 836 | 836 | 158 | 158 | 167 | 167
BOON-COMA-230.0-1 | 5415 | BOONE SUBSTATION | XCEL | COMANCHE SUBSTATION | XCEL | 70061 | 70122 | Xcel Owned | BOON-COMA-230.0-1 | FACILITY |  | 800 | 800 | 800 | 800 | 319 | 319 | 319 | 319
BOON-COMA-230.0-1 | 5415 | BOONE SUBSTATION | XCEL | COMANCHE SUBSTATION | XCEL | 70061 | 70122 | Xcel Owned | 5415 246Y | CURRENT_TRANSFORMER | BOON | 800 | 800 | 800 | 800 | 319 | 319 | 319 | 319
BOON-LASS-230.0-1 | 5337 | BOONE SUBSTATION | XCEL | LAMAR 345KV SWITCHING STATION | XCEL | 70061 | 70254 | Jointly Owned | BOON-LASS-230.0-1 | FACILITY |  | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
BOON-LASS-230.0-1 | 5337 | BOONE SUBSTATION | XCEL | LAMAR 345KV SWITCHING STATION | XCEL | 70061 | 70254 | Jointly Owned | TL5337_XDCR WATT | SECONDARY_CURRENT_LIMITATION | BOON | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
BOON-LASS-230.0-1 | 5337 | BOONE SUBSTATION | XCEL | LAMAR 345KV SWITCHING STATION | XCEL | 70061 | 70254 | Jointly Owned | TL5337_XDCR VAR | SECONDARY_CURRENT_LIMITATION | BOON | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
BOON-LASS-230.0-1 | 5337 | BOONE SUBSTATION | XCEL | LAMAR 345KV SWITCHING STATION | XCEL | 70061 | 70254 | Jointly Owned | 230 5337 M C | CURRENT_TRANSFORMER | BOON | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
BOON-LASS-230.0-1 | 5337 | BOONE SUBSTATION | XCEL | LAMAR 345KV SWITCHING STATION | XCEL | 70061 | 70254 | Jointly Owned | 230 5337 M A | CURRENT_TRANSFORMER | BOON | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
BOON-LASS-230.0-1 | 5337 | BOONE SUBSTATION | XCEL | LAMAR 345KV SWITCHING STATION | XCEL | 70061 | 70254 | Jointly Owned | TL5337_METER VAR | SECONDARY_CURRENT_LIMITATION | BOON | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
BOON-LASS-230.0-1 | 5337 | BOONE SUBSTATION | XCEL | LAMAR 345KV SWITCHING STATION | XCEL | 70061 | 70254 | Jointly Owned | TL5337_AMP SW | SECONDARY_CURRENT_LIMITATION | BOON | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
BOON-LASS-230.0-1 | 5337 | BOONE SUBSTATION | XCEL | LAMAR 345KV SWITCHING STATION | XCEL | 70061 | 70254 | Jointly Owned | TL5337_XDCR AMP | SECONDARY_CURRENT_LIMITATION | BOON | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
BOON-LASS-230.0-1 | 5337 | BOONE SUBSTATION | XCEL | LAMAR 345KV SWITCHING STATION | XCEL | 70061 | 70254 | Jointly Owned | TL5337_METER WATT | SECONDARY_CURRENT_LIMITATION | BOON | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
BOON-LASS-230.0-1 | 5337 | BOONE SUBSTATION | XCEL | LAMAR 345KV SWITCHING STATION | XCEL | 70061 | 70254 | Jointly Owned | 230 5337 M B | CURRENT_TRANSFORMER | BOON | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
BOON-LASS-230.0-1 | 5337 | BOONE SUBSTATION | XCEL | LAMAR 345KV SWITCHING STATION | XCEL | 70061 | 70254 | Jointly Owned | TL5337_METER AMP | SECONDARY_CURRENT_LIMITATION | BOON | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
BOON-LASS-230.0-1 | 5337 | BOONE SUBSTATION | XCEL | LAMAR 345KV SWITCHING STATION | XCEL | 70061 | 70254 | Jointly Owned | 5332S | SWITCH | BOON | 1200 | 1549 | 1486 | 1780 | 478 | 617 | 592 | 709
BOON-LASS-230.0-1 | 5337 | BOONE SUBSTATION | XCEL | LAMAR 345KV SWITCHING STATION | XCEL | 70061 | 70254 | Jointly Owned | 5337N | SWITCH | BOON | 1200 | 1549 | 1486 | 1780 | 478 | 617 | 592 | 709
BOON-LASS-230.0-1 | 5337 | BOONE SUBSTATION | XCEL | LAMAR 345KV SWITCHING STATION | XCEL | 70061 | 70254 | Jointly Owned | 5336S | SWITCH | BOON | 1200 | 1549 | 1486 | 1780 | 478 | 617 | 592 | 709
BOON-LASS-230.0-1 | 5337 | BOONE SUBSTATION | XCEL | LAMAR 345KV SWITCHING STATION | XCEL | 70061 | 70254 | Jointly Owned | 5332N | SWITCH | BOON | 1200 | 1549 | 1486 | 1780 | 478 | 617 | 592 | 709
BOON-LASS-230.0-1 | 5337 | BOONE SUBSTATION | XCEL | LAMAR 345KV SWITCHING STATION | XCEL | 70061 | 70254 | Jointly Owned | 5337S | SWITCH | BOON | 1200 | 1549 | 1486 | 1780 | 478 | 617 | 592 | 709
BOON-LASS-230.0-1 | 5337 | BOONE SUBSTATION | XCEL | LAMAR 345KV SWITCHING STATION | XCEL | 70061 | 70254 | Jointly Owned | 5336N | SWITCH | BOON | 1200 | 1549 | 1486 | 1780 | 478 | 617 | 592 | 709
BOON-MIDW-230.0-1 | 5335 | BOONE SUBSTATION | XCEL | MIDWAY SUBSTATION | XCEL | 70061 | 70286 | Xcel Owned | BOON-MIDW-230.0-1 | FACILITY |  | 800 | 800 | 800 | 800 | 319 | 319 | 319 | 319
BOON-MIDW-230.0-1 | 5335 | BOONE SUBSTATION | XCEL | MIDWAY SUBSTATION | XCEL | 70061 | 70286 | Xcel Owned | 5335 246Y | CURRENT_TRANSFORMER | BOON | 800 | 800 | 800 | 800 | 319 | 319 | 319 | 319
BREC-DILL-230.0-1 | 5355 | BRECKENRIDGE SUBSTATION | XCEL | DILLON SUBSTATION | XCEL | 70064 | 70156 | Xcel Owned | BREC-DILL-230.0-1 | FACILITY |  | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
BREC-DILL-230.0-1 | 5355 | BRECKENRIDGE SUBSTATION | XCEL | DILLON SUBSTATION | XCEL | 70064 | 70156 | Xcel Owned | 5356 135Y | CURRENT_TRANSFORMER | DILL | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
BREC-DILL-230.0-1 | 5355 | BRECKENRIDGE SUBSTATION | XCEL | DILLON SUBSTATION | XCEL | 70064 | 70156 | Xcel Owned | 5356 246Y | CURRENT_TRANSFORMER | DILL | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
BROO-FEDE-115.0-1 | 9558 | BROOMFIELD SUBSTATION | XCEL | FEDERAL HEIGHTS SUBSTATION | XCEL | 70065 | 70174 | Xcel Owned | BROO-FEDE-115.0-1 | FACILITY |  | 797 | 876 | 906 | 997 | 159 | 174 | 180 | 199
BROO-FEDE-115.0-1 | 9558 | BROOMFIELD SUBSTATION | XCEL | FEDERAL HEIGHTS SUBSTATION | XCEL | 70065 | 70174 | Xcel Owned | BROO-FEDE-115.0-1 | Transmission Line | 9558 | 797 | 876 | 906 | 997 | 159 | 174 | 180 | 199
BROO-LOUI-115.0-1 | 9052 | BROOMFIELD SUBSTATION | XCEL | LOUISVILLE SUBSTATION | XCEL | 70065 | 70269 | Xcel Owned | BROO-LOUI-115.0-1 | FACILITY |  | 792 | 792 | 836 | 836 | 158 | 158 | 167 | 167
BROO-LOUI-115.0-1 | 9052 | BROOMFIELD SUBSTATION | XCEL | LOUISVILLE SUBSTATION | XCEL | 70065 | 70269 | Xcel Owned |  | LINE_TRAP | BROO | 792 | 792 | 836 | 836 | 158 | 158 | 167 | 167
BROO-SEMP-115.0-1 | 9464 | BROOMFIELD SUBSTATION | XCEL | SEMPER SUBSTATION | XCEL | 70065 | 70382 | Xcel Owned | BROO-SEMP-115.0-1 | FACILITY |  | 797 | 877 | 900 | 900 | 159 | 175 | 179 | 179
BROO-SEMP-115.0-1 | 9464 | BROOMFIELD SUBSTATION | XCEL | SEMPER SUBSTATION | XCEL | 70065 | 70382 | Xcel Owned | BROO-SEMP-115.0-1 | Transmission Line | 9464 | 797 | 877 | 907 | 998 | 159 | 175 | 181 | 199
BROO-SEMP-115.0-1 | 9464 | BROOMFIELD SUBSTATION | XCEL | SEMPER SUBSTATION | XCEL | 70065 | 70382 | Xcel Owned | 9464_135X_XDCR_AMP | SECONDARY_CURRENT_LIMITATION | SEMP | 900 | 900 | 900 | 900 | 179 | 179 | 179 | 179
BROO-VALM-115.0-1 | 9068 | BROOMFIELD SUBSTATION | XCEL | VALMONT SWITCHYARD SUBSTATION | XCEL | 70065 | 70440 | Xcel Owned | BROO-VALM-115.0-1 | FACILITY |  | 1440 | 1584 | 1642 | 1673 | 287 | 316 | 327 | 333
BROO-VALM-115.0-1 | 9068 | BROOMFIELD SUBSTATION | XCEL | VALMONT SWITCHYARD SUBSTATION | XCEL | 70065 | 70440 | Xcel Owned | BROO-VALM-115.0-1 | Transmission Line | 9068 | 1440 | 1584 | 1642 | 1806 | 287 | 316 | 327 | 360
BROO-VALM-115.0-1 | 9068 | BROOMFIELD SUBSTATION | XCEL | VALMONT SWITCHYARD SUBSTATION | XCEL | 70065 | 70440 | Xcel Owned |  | LINE_TRAP | VALM | 1584 | 1584 | 1673 | 1673 | 316 | 316 | 333 | 333
BRSS-BCP-115.0-1 | 9153 | BRUSH SWITCHING STATION | XCEL | Brush4 | FOREIGN | 2003 | 2004 | Xcel Owned | BRSS-BCP-115.0-1 | FACILITY |  | 402 | 402 | 402 | 402 | 80 | 80 | 80 | 80
BRSS-BCP-115.0-1 | 9153 | BRUSH SWITCHING STATION | XCEL | Brush4 | FOREIGN | 2003 | 2004 | Xcel Owned | Foreign Ratings | Foreign Ratings | BCP | 402 | 402 | 402 | 402 | 80 | 80 | 80 | 80
BRSS-BEAV-115.0-1 | 9406 | BRUSH SWITCHING STATION | XCEL | BEAVER CREEK EAST SUBSTATION | XCEL | 70005 | 70397 | Xcel Owned | BRSS-BEAV-115.0-1 | FACILITY |  | 1200 | 1200 | 1200 | 1200 | 239 | 239 | 239 | 239
BRSS-BEAV-115.0-1 | 9406 | BRUSH SWITCHING STATION | XCEL | BEAVER CREEK EAST SUBSTATION | XCEL | 70005 | 70397 | Xcel Owned | 9400 135Y | CURRENT_TRANSFORMER | BEAV | 1200 | 1200 | 1200 | 1200 | 239 | 239 | 239 | 239
BRSS-BEAV-115.0-1 | 9406 | BRUSH SWITCHING STATION | XCEL | BEAVER CREEK EAST SUBSTATION | XCEL | 70005 | 70397 | Xcel Owned | 9400 135X | CURRENT_TRANSFORMER | BEAV | 1200 | 1200 | 1200 | 1200 | 239 | 239 | 239 | 239
BRSS-BEAV-115.0-1 | 9406 | BRUSH SWITCHING STATION | XCEL | BEAVER CREEK EAST SUBSTATION | XCEL | 70005 | 70397 | Xcel Owned | 9400 246Y | CURRENT_TRANSFORMER | BEAV | 1200 | 1200 | 1200 | 1200 | 239 | 239 | 239 | 239
BRSS-BEAV-115.0-1 | 9406 | BRUSH SWITCHING STATION | XCEL | BEAVER CREEK EAST SUBSTATION | XCEL | 70005 | 70397 | Xcel Owned | 9400 246X | CURRENT_TRANSFORMER | BEAV | 1200 | 1200 | 1200 | 1200 | 239 | 239 | 239 | 239
BRSS-BEAV-115.0-2 | 9407 | BRUSH SWITCHING STATION | XCEL | BEAVER CREEK EAST SUBSTATION | XCEL | 70005 | 70397 | Xcel Owned | BRSS-BEAV-115.0-2 | FACILITY |  | 1200 | 1200 | 1200 | 1200 | 239 | 239 | 239 | 239
BRSS-BEAV-115.0-2 | 9407 | BRUSH SWITCHING STATION | XCEL | BEAVER CREEK EAST SUBSTATION | XCEL | 70005 | 70397 | Xcel Owned | 9407 XDCR W/VAR | SECONDARY_CURRENT_LIMITATION | BEAV | 1200 | 1200 | 1200 | 1200 | 239 | 239 | 239 | 239
BRSS-BEAV-115.0-2 | 9407 | BRUSH SWITCHING STATION | XCEL | BEAVER CREEK EAST SUBSTATION | XCEL | 70005 | 70397 | Xcel Owned | 9400 135X | CURRENT_TRANSFORMER | BEAV | 1200 | 1200 | 1200 | 1200 | 239 | 239 | 239 | 239
BRSS-BEAV-115.0-2 | 9407 | BRUSH SWITCHING STATION | XCEL | BEAVER CREEK EAST SUBSTATION | XCEL | 70005 | 70397 | Xcel Owned | 9400 246Y | CURRENT_TRANSFORMER | BEAV | 1200 | 1200 | 1200 | 1200 | 239 | 239 | 239 | 239
BRSS-BEAV-115.0-2 | 9407 | BRUSH SWITCHING STATION | XCEL | BEAVER CREEK EAST SUBSTATION | XCEL | 70005 | 70397 | Xcel Owned | 9400 135Y | CURRENT_TRANSFORMER | BEAV | 1200 | 1200 | 1200 | 1200 | 239 | 239 | 239 | 239
BRSS-BEAV-115.0-2 | 9407 | BRUSH SWITCHING STATION | XCEL | BEAVER CREEK EAST SUBSTATION | XCEL | 70005 | 70397 | Xcel Owned | 9400 246X | CURRENT_TRANSFORMER | BEAV | 1200 | 1200 | 1200 | 1200 | 239 | 239 | 239 | 239
BRSS-BRNG-115.0-1 | 9155 | BRUSH SWITCHING STATION | XCEL | BRUSH CO-GEN / CPP SW. YARD | XCEL | 2003 | 2005 | Xcel Owned | BRSS-BRNG-115.0-1 | FACILITY |  | 800 | 800 | 800 | 800 | 159 | 159 | 159 | 159
BRSS-BRNG-115.0-1 | 9155 | BRUSH SWITCHING STATION | XCEL | BRUSH CO-GEN / CPP SW. YARD | XCEL | 2003 | 2005 | Xcel Owned | 115 9155 MU B | CURRENT_TRANSFORMER | BRNG | 800 | 800 | 800 | 800 | 159 | 159 | 159 | 159
BRSS-BRNG-115.0-1 | 9155 | BRUSH SWITCHING STATION | XCEL | BRUSH CO-GEN / CPP SW. YARD | XCEL | 2003 | 2005 | Xcel Owned | 9155_PK-1-3_115KV | SECONDARY_CURRENT_LIMITATION | BRNG | 800 | 800 | 800 | 800 | 159 | 159 | 159 | 159
BRSS-BRNG-115.0-1 | 9155 | BRUSH SWITCHING STATION | XCEL | BRUSH CO-GEN / CPP SW. YARD | XCEL | 2003 | 2005 | Xcel Owned | 115 9155 MU C | CURRENT_TRANSFORMER | BRNG | 800 | 800 | 800 | 800 | 159 | 159 | 159 | 159
BRSS-BRNG-115.0-1 | 9155 | BRUSH SWITCHING STATION | XCEL | BRUSH CO-GEN / CPP SW. YARD | XCEL | 2003 | 2005 | Xcel Owned | 115 9155 MU A | CURRENT_TRANSFORMER | BRNG | 800 | 800 | 800 | 800 | 159 | 159 | 159 | 159
BRSS-BRNG-115.0-1 | 9155 | BRUSH SWITCHING STATION | XCEL | BRUSH CO-GEN / CPP SW. YARD | XCEL | 2003 | 2005 | Xcel Owned | 9155_PK-1-2_115KV | SECONDARY_CURRENT_LIMITATION | BRNG | 800 | 800 | 800 | 800 | 159 | 159 | 159 | 159
BRSS-BRNG-115.0-1 | 9155 | BRUSH SWITCHING STATION | XCEL | BRUSH CO-GEN / CPP SW. YARD | XCEL | 2003 | 2005 | Xcel Owned | 9155_PK-1-1_115KV | SECONDARY_CURRENT_LIMITATION | BRNG | 800 | 800 | 800 | 800 | 159 | 159 | 159 | 159
BRSS-BRNG-115.0-2 | 9156 | BRUSH SWITCHING STATION | XCEL | BRUSH CO-GEN / CPP SW. YARD | XCEL | 2003 | 2150 | Xcel Owned | BRSS-BRNG-115.0-2 | FACILITY |  | 600 | 600 | 600 | 600 | 120 | 120 | 120 | 120
BRSS-BRNG-115.0-2 | 9156 | BRUSH SWITCHING STATION | XCEL | BRUSH CO-GEN / CPP SW. YARD | XCEL | 2003 | 2150 | Xcel Owned | 115 9156 MU C | CURRENT_TRANSFORMER | BRNG | 600 | 600 | 600 | 600 | 120 | 120 | 120 | 120
BRSS-BRNG-115.0-2 | 9156 | BRUSH SWITCHING STATION | XCEL | BRUSH CO-GEN / CPP SW. YARD | XCEL | 2003 | 2150 | Xcel Owned | 115 9156 MU A | CURRENT_TRANSFORMER | BRNG | 600 | 600 | 600 | 600 | 120 | 120 | 120 | 120
BRSS-BRNG-115.0-2 | 9156 | BRUSH SWITCHING STATION | XCEL | BRUSH CO-GEN / CPP SW. YARD | XCEL | 2003 | 2150 | Xcel Owned | 115 9156 MU B | CURRENT_TRANSFORMER | BRNG | 600 | 600 | 600 | 600 | 120 | 120 | 120 | 120
BSVY-CAME-230.0-1 | 55123 | BLUESTONE VALLEY | XCEL | CAMEO SUBSTATION | XCEL | 70264 | 70078 | Xcel Owned | BSVY-CAME-230.0-1 | FACILITY |  | 1095 | 1205 | 1247 | 1372 | 436 | 480 | 497 | 547
BSVY-CAME-230.0-1 | 55123 | BLUESTONE VALLEY | XCEL | CAMEO SUBSTATION | XCEL | 70264 | 70078 | Xcel Owned | BSVY-CAME-230.0-1 | Transmission Line | 55123 | 1095 | 1205 | 1247 | 1372 | 436 | 480 | 497 | 547
BSVY-PARA-230.0-1 | 5509 | BLUESTONE VALLEY | XCEL | PARACHUTE SUBSTATION | XCEL | 70264 | 70309 | Xcel Owned | BSVY-PARA-230.0-1 | FACILITY |  | 996 | 996 | 996 | 996 | 397 | 397 | 397 | 397
BSVY-PARA-230.0-1 | 5509 | BLUESTONE VALLEY | XCEL | PARACHUTE SUBSTATION | XCEL | 70264 | 70309 | Xcel Owned | 5508 246Y | CURRENT_TRANSFORMER | PARA | 996 | 996 | 996 | 996 | 397 | 397 | 397 | 397
BSVY-PARA-230.0-1 | 5509 | BLUESTONE VALLEY | XCEL | PARACHUTE SUBSTATION | XCEL | 70264 | 70309 | Xcel Owned | 5508 246X | CURRENT_TRANSFORMER | PARA | 996 | 996 | 996 | 996 | 397 | 397 | 397 | 397
BTER-SUNS-115.0-1 | 9216 | BOULDER TERMINAL SUBSTATION | XCEL | SUNSHINE CANYON SUBSTATION | XCEL | 70059 | 70424 | Xcel Owned | BTER-SUNS-115.0-1 | FACILITY |  | 627 | 689 | 712 | 783 | 125 | 137 | 142 | 156
BTER-SUNS-115.0-1 | 9216 | BOULDER TERMINAL SUBSTATION | XCEL | SUNSHINE CANYON SUBSTATION | XCEL | 70059 | 70424 | Xcel Owned | Merlin | BUSBAR_SECTION | SUNS | 627 | 689 | 712 | 783 | 125 | 137 | 142 | 156
BTER-VALM-115.0-1 | 9065 | BOULDER TERMINAL SUBSTATION | XCEL | VALMONT SWITCHYARD SUBSTATION | XCEL | 70059 | 70440 | Xcel Owned | BTER-VALM-115.0-1 | FACILITY |  | 799 | 879 | 908 | 999 | 159 | 175 | 181 | 199
BTER-VALM-115.0-1 | 9065 | BOULDER TERMINAL SUBSTATION | XCEL | VALMONT SWITCHYARD SUBSTATION | XCEL | 70059 | 70440 | Xcel Owned | Hawk | BUSBAR_SECTION | BTER | 799 | 879 | 908 | 999 | 159 | 175 | 181 | 199
BTER-VALM-115.0-1 | 9065 | BOULDER TERMINAL SUBSTATION | XCEL | VALMONT SWITCHYARD SUBSTATION | XCEL | 70059 | 70440 | Xcel Owned | BTER-VALM-115.0-1 | Transmission Line | 9065 | 799 | 879 | 908 | 999 | 159 | 175 | 181 | 199
BTER-VALM-115.0-2 | 9067 | BOULDER TERMINAL SUBSTATION | XCEL | VALMONT SWITCHYARD SUBSTATION | XCEL | 70059 | 70444 | Xcel Owned | BTER-VALM-115.0-2 | FACILITY |  | 750 | 750 | 750 | 750 | 149 | 149 | 149 | 149
BTER-VALM-115.0-2 | 9067 | BOULDER TERMINAL SUBSTATION | XCEL | VALMONT SWITCHYARD SUBSTATION | XCEL | 70059 | 70444 | Xcel Owned | 9220 246X | CURRENT_TRANSFORMER | BTER | 750 | 750 | 750 | 750 | 149 | 149 | 149 | 149
BUCK-JEWE-230.0-1 | 5167 | BUCKLEY SUBSTATION | XCEL | JEWELL SUBSTATION | XCEL | 70067 | 70512 | Xcel Owned | BUCK-JEWE-230.0-1 | FACILITY |  | 1265 | 1391 | 1441 | 1585 | 504 | 554 | 574 | 631
BUCK-JEWE-230.0-1 | 5167 | BUCKLEY SUBSTATION | XCEL | JEWELL SUBSTATION | XCEL | 70067 | 70512 | Xcel Owned | BUCK-JEWE-230.0-1 | Transmission Line | 5167 | 1265 | 1391 | 1441 | 1585 | 504 | 554 | 574 | 631
BUCK-SMOK-230.0-1 | 5285 | BUCKLEY SUBSTATION | XCEL | SMOKY HILL SUBSTATION | XCEL | 70067 | 70396 | Xcel Owned | BUCK-SMOK-230.0-1 | FACILITY |  | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
BUCK-SMOK-230.0-1 | 5285 | BUCKLEY SUBSTATION | XCEL | SMOKY HILL SUBSTATION | XCEL | 70067 | 70396 | Xcel Owned | TL5285 CNP11A 67GP | SECONDARY_CURRENT_LIMITATION | SMOK | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
BUCK-SMOK-230.0-1 | 5285 | BUCKLEY SUBSTATION | XCEL | SMOKY HILL SUBSTATION | XCEL | 70067 | 70396 | Xcel Owned | TL5285 CEY52A PH21ZP | SECONDARY_CURRENT_LIMITATION | SMOK | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
BUCK-SMOK-230.0-2 | 5167 | BUCKLEY SUBSTATION | XCEL | SMOKY HILL SUBSTATION | XCEL | 70046 | 70396 | Xcel Owned | BUCK-SMOK-230.0-2 | FACILITY |  | 1262 | 1388 | 1438 | 1581 | 503 | 553 | 573 | 630
BUCK-SMOK-230.0-2 | 5167 | BUCKLEY SUBSTATION | XCEL | SMOKY HILL SUBSTATION | XCEL | 70046 | 70396 | Xcel Owned | BUCK-SMOK-230.0-2 | Transmission Line | 5167 | 1262 | 1388 | 1438 | 1581 | 503 | 553 | 573 | 630
BUCK-TOLL-230.0-1 | 5285 | BUCKLEY SUBSTATION | XCEL | TOLLGATE SUBSTATION | XCEL | 70046 | 70491 | Xcel Owned | BUCK-TOLL-230.0-1 | FACILITY |  | 1214 | 1392 | 1442 | 1586 | 484 | 555 | 574 | 632
BUCK-TOLL-230.0-1 | 5285 | BUCKLEY SUBSTATION | XCEL | TOLLGATE SUBSTATION | XCEL | 70046 | 70491 | Xcel Owned | Narcissus | BUSBAR_SECTION | TOLL | 1214 | 1421 | 1450 | 1619 | 484 | 566 | 578 | 645
BUCK-TOLL-230.0-1 | 5285 | BUCKLEY SUBSTATION | XCEL | TOLLGATE SUBSTATION | XCEL | 70046 | 70491 | Xcel Owned | BUCK-TOLL-230.0-1 | Transmission Line | 5285 | 1265 | 1392 | 1442 | 1586 | 504 | 555 | 574 | 632
BUVI_TP-RAYL-115.0-1 | 9255 | BUENA VISTA TAP | XCEL | RAY LEWIS | XCEL | 70056 | 70312 | Xcel Owned | BUVI_TP-RAYL-115.0-1 | FACILITY | [9 empty] | See Ambient Adjusted Ratings Section
CABI-DILL-230.0-1 | 5007 | CABIN CREEK HYDRO SUBSTATION | XCEL | DILLON SUBSTATION | XCEL | 70072 | 70156 | Xcel Owned | CABI-DILL-230.0-1 | FACILITY |  | 1584 | 1584 | 1673 | 1673 | 631 | 631 | 666 | 666
CABI-DILL-230.0-1 | 5007 | CABIN CREEK HYDRO SUBSTATION | XCEL | DILLON SUBSTATION | XCEL | 70072 | 70156 | Xcel Owned |  | LINE_TRAP | DILL | 1584 | 1584 | 1673 | 1673 | 631 | 631 | 666 | 666
CABI-GEOR-115.0-1 | 9665 | CABIN CREEK HYDRO SUBSTATION | XCEL | GEORGETOWN HYDRO SUBSTATION | XCEL | 70071 | 70197 | Xcel Owned | CABI-GEOR-115.0-1 | FACILITY |  | 600 | 775 | 743 | 890 | 120 | 154 | 148 | 177
CABI-GEOR-115.0-1 | 9665 | CABIN CREEK HYDRO SUBSTATION | XCEL | GEORGETOWN HYDRO SUBSTATION | XCEL | 70071 | 70197 | Xcel Owned | 9665-1 | SWITCH | GEOR | 600 | 775 | 743 | 890 | 120 | 154 | 148 | 177
CABI-IDAH-230.0-1 | 5005 | CABIN CREEK HYDRO SUBSTATION | XCEL | IDAHO SPRINGS SUBSTATION | XCEL | 70072 | 70237 | Xcel Owned | CABI-IDAH-230.0-1 | FACILITY |  | 1188 | 1394 | 1415 | 1556 | 473 | 555 | 564 | 620
CABI-IDAH-230.0-1 | 5005 | CABIN CREEK HYDRO SUBSTATION | XCEL | IDAHO SPRINGS SUBSTATION | XCEL | 70072 | 70237 | Xcel Owned | Narcissus | BUSBAR_SECTION | IDAH | 1188 | 1394 | 1422 | 1590 | 473 | 555 | 567 | 633
CABI-IDAH-230.0-1 | 5005 | CABIN CREEK HYDRO SUBSTATION | XCEL | IDAHO SPRINGS SUBSTATION | XCEL | 70072 | 70237 | Xcel Owned | CABI-IDAH-230.0-1 | Transmission Line | 5005 | 1285 | 1414 | 1415 | 1556 | 512 | 563 | 564 | 620
CABI-LOOK-230.0-1 | 5003 | CABIN CREEK HYDRO SUBSTATION | XCEL | LOOKOUT SUBSTATION | XCEL | 70072 | 70266 | Xcel Owned | CABI-LOOK-230.0-1 | FACILITY |  | 1188 | 1188 | 1255 | 1255 | 473 | 473 | 500 | 500
CABI-LOOK-230.0-1 | 5003 | CABIN CREEK HYDRO SUBSTATION | XCEL | LOOKOUT SUBSTATION | XCEL | 70072 | 70266 | Xcel Owned |  | LINE_TRAP | LOOK | 1188 | 1188 | 1255 | 1255 | 473 | 473 | 500 | 500
CACR-GOOS-345.0-1 | 7251 | CANAL CROSSING | XCEL | GOOSE CREEK | XCEL | 70915 | 70918 | Xcel Owned | CACR-GOOS-345.0-1 | FACILITY |  | 2897 | 2970 | 3000 | 3000 | 1731 | 1775 | 1793 | 1793
CACR-GOOS-345.0-1 | 7251 | CANAL CROSSING | XCEL | GOOSE CREEK | XCEL | 70915 | 70918 | Xcel Owned | CACR-GOOS-345.0-1 | Transmission Line | 7251 | 2897 | 3187 | 3302 | 3633 | 1731 | 1904 | 1973 | 2171
CACR-GOOS-345.0-1 | 7251 | CANAL CROSSING | XCEL | GOOSE CREEK | XCEL | 70915 | 70918 | Xcel Owned |  | LINE_TRAP | GOOS | 2970 | 2970 | 3136 | 3136 | 1775 | 1775 | 1874 | 1874
CACR-GOOS-345.0-1 | 7251 | CANAL CROSSING | XCEL | GOOSE CREEK | XCEL | 70915 | 70918 | Xcel Owned |  | LINE_TRAP | CACR | 2970 | 2970 | 3136 | 3136 | 1775 | 1775 | 1874 | 1874
CACR-GOOS-345.0-1 | 7251 | CANAL CROSSING | XCEL | GOOSE CREEK | XCEL | 70915 | 70918 | Xcel Owned | 7252 | BREAKER | GOOS | 3000 | 3000 | 3000 | 3000 | 1793 | 1793 | 1793 | 1793
CACR-GOOS-345.0-1 | 7251 | CANAL CROSSING | XCEL | GOOSE CREEK | XCEL | 70915 | 70918 | Xcel Owned | 7294 | BREAKER | CACR | 3000 | 3000 | 3000 | 3000 | 1793 | 1793 | 1793 | 1793
CACR-GOOS-345.0-1 | 7251 | CANAL CROSSING | XCEL | GOOSE CREEK | XCEL | 70915 | 70918 | Xcel Owned | 7251 | BREAKER | CACR | 3000 | 3000 | 3000 | 3000 | 1793 | 1793 | 1793 | 1793
CACR-GOOS-345.0-1 | 7251 | CANAL CROSSING | XCEL | GOOSE CREEK | XCEL | 70915 | 70918 | Xcel Owned | 7251 | BREAKER | GOOS | 3000 | 3000 | 3000 | 3000 | 1793 | 1793 | 1793 | 1793
CACR-GOOS-345.0-2 | 7295 | CANAL CROSSING | XCEL | GOOSE CREEK | XCEL | 70915 | 70918 | Xcel Owned | CACR-GOOS-345.0-2 | FACILITY |  | 2897 | 2970 | 3000 | 3000 | 1731 | 1775 | 1793 | 1793
CACR-GOOS-345.0-2 | 7295 | CANAL CROSSING | XCEL | GOOSE CREEK | XCEL | 70915 | 70918 | Xcel Owned | CACR-GOOS-345.0-2 | Transmission Line | 7295 | 2897 | 3187 | 3302 | 3633 | 1731 | 1904 | 1973 | 2171
CACR-GOOS-345.0-2 | 7295 | CANAL CROSSING | XCEL | GOOSE CREEK | XCEL | 70915 | 70918 | Xcel Owned |  | LINE_TRAP | CACR | 2970 | 2970 | 3136 | 3136 | 1775 | 1775 | 1874 | 1874
CACR-GOOS-345.0-2 | 7295 | CANAL CROSSING | XCEL | GOOSE CREEK | XCEL | 70915 | 70918 | Xcel Owned |  | LINE_TRAP | GOOS | 2970 | 2970 | 3136 | 3136 | 1775 | 1775 | 1874 | 1874
CACR-GOOS-345.0-2 | 7295 | CANAL CROSSING | XCEL | GOOSE CREEK | XCEL | 70915 | 70918 | Xcel Owned | 7254 | BREAKER | GOOS | 3000 | 3000 | 3000 | 3000 | 1793 | 1793 | 1793 | 1793
CACR-GOOS-345.0-2 | 7295 | CANAL CROSSING | XCEL | GOOSE CREEK | XCEL | 70915 | 70918 | Xcel Owned | 7295 | BREAKER | GOOS | 3000 | 3000 | 3000 | 3000 | 1793 | 1793 | 1793 | 1793
CACR-GOOS-345.0-2 | 7295 | CANAL CROSSING | XCEL | GOOSE CREEK | XCEL | 70915 | 70918 | Xcel Owned | 7296 | BREAKER | CACR | 3000 | 3000 | 3000 | 3000 | 1793 | 1793 | 1793 | 1793
CACR-GOOS-345.0-2 | 7295 | CANAL CROSSING | XCEL | GOOSE CREEK | XCEL | 70915 | 70918 | Xcel Owned | 7295 | BREAKER | CACR | 3000 | 3000 | 3000 | 3000 | 1793 | 1793 | 1793 | 1793
CACR-MSST-345.0-1 | 7111 | CANAL CROSSING | XCEL | MISSILE SITE | XCEL | 70915 | 70624 | Xcel Owned | CACR-MSST-345.0-1 | FACILITY |  | 2425 | 2838 | 2897 | 3000 | 1449 | 1696 | 1731 | 1793
CACR-MSST-345.0-1 | 7111 | CANAL CROSSING | XCEL | MISSILE SITE | XCEL | 70915 | 70624 | Xcel Owned | Narcissus | BUSBAR_SECTION | MSST | 2425 | 2838 | 2897 | 3233 | 1449 | 1696 | 1731 | 1932
CACR-MSST-345.0-1 | 7111 | CANAL CROSSING | XCEL | MISSILE SITE | XCEL | 70915 | 70624 | Xcel Owned | 7290 | BREAKER | CACR | 3000 | 3000 | 3000 | 3000 | 1793 | 1793 | 1793 | 1793
CACR-MSST-345.0-1 | 7111 | CANAL CROSSING | XCEL | MISSILE SITE | XCEL | 70915 | 70624 | Xcel Owned | 7108 | BREAKER | MSST | 3000 | 3000 | 3000 | 3000 | 1793 | 1793 | 1793 | 1793
CACR-MSST-345.0-1 | 7111 | CANAL CROSSING | XCEL | MISSILE SITE | XCEL | 70915 | 70624 | Xcel Owned | 7111 | BREAKER | MSST | 3000 | 3000 | 3000 | 3000 | 1793 | 1793 | 1793 | 1793
CACR-MSST-345.0-1 | 7111 | CANAL CROSSING | XCEL | MISSILE SITE | XCEL | 70915 | 70624 | Xcel Owned | 7111 | BREAKER | CACR | 3000 | 3000 | 3000 | 3000 | 1793 | 1793 | 1793 | 1793
CACR-MSST-345.0-2 | 7293 | CANAL CROSSING | XCEL | MISSILE SITE | XCEL | 70915 | 70624 | Xcel Owned | CACR-MSST-345.0-2 | FACILITY |  | 2821 | 2970 | 3000 | 3000 | 1686 | 1775 | 1793 | 1793
CACR-MSST-345.0-2 | 7293 | CANAL CROSSING | XCEL | MISSILE SITE | XCEL | 70915 | 70624 | Xcel Owned | Narcissus | BUSBAR_SECTION | MSST | 2821 | 3103 | 3214 | 3536 | 1686 | 1854 | 1921 | 2113
CACR-MSST-345.0-2 | 7293 | CANAL CROSSING | XCEL | MISSILE SITE | XCEL | 70915 | 70624 | Xcel Owned |  | LINE_TRAP | MSST | 2970 | 2970 | 3136 | 3136 | 1775 | 1775 | 1874 | 1874
CACR-MSST-345.0-2 | 7293 | CANAL CROSSING | XCEL | MISSILE SITE | XCEL | 70915 | 70624 | Xcel Owned |  | LINE_TRAP | CACR | 2970 | 2970 | 3136 | 3136 | 1775 | 1775 | 1874 | 1874
CACR-MSST-345.0-2 | 7293 | CANAL CROSSING | XCEL | MISSILE SITE | XCEL | 70915 | 70624 | Xcel Owned | 7292 | BREAKER | CACR | 3000 | 3000 | 3000 | 3000 | 1793 | 1793 | 1793 | 1793
CACR-MSST-345.0-2 | 7293 | CANAL CROSSING | XCEL | MISSILE SITE | XCEL | 70915 | 70624 | Xcel Owned | 7293 | BREAKER | CACR | 3000 | 3000 | 3000 | 3000 | 1793 | 1793 | 1793 | 1793
CACR-PAWN-345.0-1 | 7091 | CANAL CROSSING | XCEL | PAWNEE 345KV | XCEL | 70915 | 70598 | Xcel Owned | CACR-PAWN-345.0-1 | FACILITY |  | 2867 | 2970 | 3000 | 3000 | 1713 | 1775 | 1793 | 1793
CACR-PAWN-345.0-1 | 7091 | CANAL CROSSING | XCEL | PAWNEE 345KV | XCEL | 70915 | 70598 | Xcel Owned | Narcissus | BUSBAR_SECTION | PAWN | 2867 | 3154 | 3265 | 3592 | 1713 | 1885 | 1951 | 2146
CACR-PAWN-345.0-1 | 7091 | CANAL CROSSING | XCEL | PAWNEE 345KV | XCEL | 70915 | 70598 | Xcel Owned |  | LINE_TRAP | CACR | 2970 | 2970 | 3136 | 3136 | 1775 | 1775 | 1874 | 1874
CACR-PAWN-345.0-1 | 7091 | CANAL CROSSING | XCEL | PAWNEE 345KV | XCEL | 70915 | 70598 | Xcel Owned | 7092 | BREAKER | PAWN | 3000 | 3000 | 3000 | 3000 | 1793 | 1793 | 1793 | 1793
CACR-PAWN-345.0-1 | 7091 | CANAL CROSSING | XCEL | PAWNEE 345KV | XCEL | 70915 | 70598 | Xcel Owned | 7304 | BREAKER | CACR | 3000 | 3000 | 3000 | 3000 | 1793 | 1793 | 1793 | 1793
CACR-PAWN-345.0-1 | 7091 | CANAL CROSSING | XCEL | PAWNEE 345KV | XCEL | 70915 | 70598 | Xcel Owned | 7091 | BREAKER | CACR | 3000 | 3000 | 3000 | 3000 | 1793 | 1793 | 1793 | 1793
CACR-PAWN-345.0-2 | 7307 | CANAL CROSSING | XCEL | PAWNEE 345KV | XCEL | 70915 | 70598 | Xcel Owned | CACR-PAWN-345.0-2 | FACILITY |  | 2867 | 2970 | 3000 | 3000 | 1713 | 1775 | 1793 | 1793
CACR-PAWN-345.0-2 | 7307 | CANAL CROSSING | XCEL | PAWNEE 345KV | XCEL | 70915 | 70598 | Xcel Owned | Narcissus | BUSBAR_SECTION | PAWN | 2867 | 3154 | 3265 | 3592 | 1713 | 1885 | 1951 | 2146
CACR-PAWN-345.0-2 | 7307 | CANAL CROSSING | XCEL | PAWNEE 345KV | XCEL | 70915 | 70598 | Xcel Owned |  | LINE_TRAP | CACR | 2970 | 2970 | 3136 | 3136 | 1775 | 1775 | 1874 | 1874
CACR-PAWN-345.0-2 | 7307 | CANAL CROSSING | XCEL | PAWNEE 345KV | XCEL | 70915 | 70598 | Xcel Owned | 7298 | BREAKER | CACR | 3000 | 3000 | 3000 | 3000 | 1793 | 1793 | 1793 | 1793
CACR-PAWN-345.0-2 | 7307 | CANAL CROSSING | XCEL | PAWNEE 345KV | XCEL | 70915 | 70598 | Xcel Owned | 7307 | BREAKER | CACR | 3000 | 3000 | 3000 | 3000 | 1793 | 1793 | 1793 | 1793
CALI-CHER-115.0-1 | 9542 | CALIFORNIA SUBSTATION | XCEL | CHEROKEE SWITCHYARD SUBSTATION | XCEL | 70073 | 70108 | Xcel Owned | CALI-CHER-115.0-1 | FACILITY |  | 770 | 908 | 925 | 1037 | 153 | 181 | 184 | 207
CALI-CHER-115.0-1 | 9542 | CALIFORNIA SUBSTATION | XCEL | CHEROKEE SWITCHYARD SUBSTATION | XCEL | 70073 | 70108 | Xcel Owned | Arbutus | BUSBAR_SECTION | CALI | 770 | 908 | 925 | 1037 | 153 | 181 | 184 | 207
CALI-HARR-115.0-1 | 9542 | CALIFORNIA SUBSTATION | XCEL | HARRISON SUBSTATION | XCEL | 70073 | 70182 | Xcel Owned | CALI-HARR-115.0-1 | FACILITY |  | 728 | 801 | 728 | 801 | 145 | 160 | 145 | 160
CALI-HARR-115.0-1 | 9542 | CALIFORNIA SUBSTATION | XCEL | HARRISON SUBSTATION | XCEL | 70073 | 70182 | Xcel Owned | CALI-HARR-115.0-1 | Transmission Line | 9542 | 728 | 801 | 728 | 801 | 145 | 160 | 145 | 160
CAME-UINT-230.0-1 | 5607 | CAMEO SUBSTATION | XCEL | UINTAH SUBSTATION | XCEL | 70078 | 70438 | Xcel Owned | CAME-UINT-230.0-1 | FACILITY |  | 800 | 800 | 800 | 800 | 319 | 319 | 319 | 319 | Railroad Documentation
CAME-UINT-230.0-1 | 5607 | CAMEO SUBSTATION | XCEL | UINTAH SUBSTATION | XCEL | 70078 | 70438 | Xcel Owned | CAME-UINT-230.0-1 | Transmission Line | 5607 | 800 | 800 | 800 | 800 | 319 | 319 | 319 | 319
CAPI-CALI_TP-115.0-1 | 9547 | CAPITOL HILL SUBSTATION | XCEL | CALIFORNIA TAP | XCEL | 70087 | 2050 | Xcel Owned | CAPI-CALI_TP-115.0-1 | FACILITY |  | 914 | 1005 | 914 | 1005 | 182 | 200 | 182 | 200
CAPI-CALI_TP-115.0-1 | 9547 | CAPITOL HILL SUBSTATION | XCEL | CALIFORNIA TAP | XCEL | 70087 | 2050 | Xcel Owned | CAPI-CALI_TP-115.0-1 | Transmission Line | 9547 | 914 | 1005 | 914 | 1005 | 182 | 200 | 182 | 200
CAPI-CALI_TP-115.0-1 | 9547 | CAPITOL HILL SUBSTATION | XCEL | CALIFORNIA TAP | XCEL | 70087 | 2050 | Xcel Owned |  | CABLE_TERMINATOR | CAPI | 914 | 1006 | 914 | 1006 | 182 | 200 | 182 | 200
CAPI-DTER-115.0-1 | 9007 | CAPITOL HILL SUBSTATION | XCEL | DENVER TERMINAL SUBSTATION | XCEL | 70087 | 70148 | Xcel Owned | CAPI-DTER-115.0-1 | FACILITY |  | 660 | 726 | 660 | 726 | 131 | 145 | 131 | 145
CAPI-DTER-115.0-1 | 9007 | CAPITOL HILL SUBSTATION | XCEL | DENVER TERMINAL SUBSTATION | XCEL | 70087 | 70148 | Xcel Owned | CAPI-DTER-115.0-1 | Transmission Line | 9007 | 660 | 726 | 660 | 726 | 131 | 145 | 131 | 145
CAPI-HARR-115.0-1 | 9956 | CAPITOL HILL SUBSTATION | XCEL | HARRISON SUBSTATION | XCEL | 70087 | 70182 | Xcel Owned | CAPI-HARR-115.0-1 | FACILITY |  | 1022 | 1213 | 1233 | 1260 | 204 | 242 | 246 | 251
CAPI-HARR-115.0-1 | 9956 | CAPITOL HILL SUBSTATION | XCEL | HARRISON SUBSTATION | XCEL | 70087 | 70182 | Xcel Owned | Narcissus | BUSBAR_SECTION | HARR | 1022 | 1213 | 1233 | 1388 | 204 | 242 | 246 | 276
CAPI-HARR-115.0-1 | 9956 | CAPITOL HILL SUBSTATION | XCEL | HARRISON SUBSTATION | XCEL | 70087 | 70182 | Xcel Owned | CAPI-HARR-115.0-1 | Transmission Line | 9956 | 1260 | 1260 | 1260 | 1260 | 251 | 251 | 251 | 251
CAST_TP1-CAST-115.0-1 | 9603 | CASTLE ROCK TAP 1 | XCEL | CASTLE ROCK SUBSTATION | XCEL | 70020 | 70091 | Xcel Owned | CAST_TP1-CAST-115.0-1 | FACILITY |  | 900 | 900 | 900 | 900 | 179 | 179 | 179 | 179
CAST_TP1-CAST-115.0-1 | 9603 | CASTLE ROCK TAP 1 | XCEL | CASTLE ROCK SUBSTATION | XCEL | 70020 | 70091 | Xcel Owned | 9603_246X_A1_115KV | SECONDARY_CURRENT_LIMITATION | CAST | 900 | 900 | 900 | 900 | 179 | 179 | 179 | 179
CAST_TP1-PALM-115.0-1 | 9603 | CASTLE ROCK TAP 1 | XCEL | PALMER LAKE SUBSTATION | XCEL | 70020 | 70308 | Xcel Owned | CAST_TP1-PALM-115.0-1 | FACILITY |  | 783 | 861 | 891 | 900 | 156 | 172 | 178 | 179
CAST_TP1-PALM-115.0-1 | 9603 | CASTLE ROCK TAP 1 | XCEL | PALMER LAKE SUBSTATION | XCEL | 70020 | 70308 | Xcel Owned | Hawk | BUSBAR_SECTION | PALM | 783 | 861 | 891 | 980 | 156 | 172 | 178 | 195
CAST_TP1-PALM-115.0-1 | 9603 | CASTLE ROCK TAP 1 | XCEL | PALMER LAKE SUBSTATION | XCEL | 70020 | 70308 | Xcel Owned | 9603 135Y | CURRENT_TRANSFORMER | PALM | 900 | 900 | 900 | 900 | 179 | 179 | 179 | 179
CAST_TP1-PALM-115.0-1 | 9603 | CASTLE ROCK TAP 1 | XCEL | PALMER LAKE SUBSTATION | XCEL | 70020 | 70308 | Xcel Owned | 9603 135X | CURRENT_TRANSFORMER | PALM | 900 | 900 | 900 | 900 | 179 | 179 | 179 | 179
CAST_TP2-CAST-115.0-1 | 9606 | CASTLE ROCK TAP 2 | XCEL | CASTLE ROCK SUBSTATION | XCEL | 70021 | 70091 | Xcel Owned | CAST_TP2-CAST-115.0-1 | FACILITY |  | 800 | 880 | 900 | 900 | 159 | 175 | 179 | 179
CAST_TP2-CAST-115.0-1 | 9606 | CASTLE ROCK TAP 2 | XCEL | CASTLE ROCK SUBSTATION | XCEL | 70021 | 70091 | Xcel Owned | CAST_TP2-CAST-115.0-1 | Transmission Line | 9606 | 800 | 880 | 910 | 1001 | 159 | 175 | 181 | 199
CAST_TP2-CAST-115.0-1 | 9606 | CASTLE ROCK TAP 2 | XCEL | CASTLE ROCK SUBSTATION | XCEL | 70021 | 70091 | Xcel Owned | 9606_246X_A1 | SECONDARY_CURRENT_LIMITATION | CAST | 900 | 900 | 900 | 900 | 179 | 179 | 179 | 179
CAST_TP2-CROV-115.0-1 | 9606 | CASTLE ROCK TAP 2 | XCEL | CROWFOOT VALLEY | XCEL | 70021 | 70117 | Xcel Owned | CAST_TP2-CROV-115.0-1 | FACILITY |  | 1246 | 1395 | 1298 | 1436 | 248 | 278 | 259 | 286
CAST_TP2-CROV-115.0-1 | 9606 | CASTLE ROCK TAP 2 | XCEL | CROWFOOT VALLEY | XCEL | 70021 | 70117 | Xcel Owned | CAST_TP2-CROV-115.0-1 | Transmission Line | 9606 | 1246 | 1395 | 1298 | 1436 | 248 | 278 | 259 | 286
CCCB_TP-CCCB-230.0-1 | 5967 | CEDAR CREEK CAP BANK | FOREIGN | CEDAR CREEK CAP BANK | FOREIGN | 70821 | 2123 | Jointly Owned | CCCB_TP-CCCB-230.0-1 | FACILITY |  | 2412 | 2654 | 2750 | 3026 | 961 | 1057 | 1096 | 1205
CCCB_TP-CCCB-230.0-1 | 5967 | CEDAR CREEK CAP BANK | FOREIGN | CEDAR CREEK CAP BANK | FOREIGN | 70821 | 2123 | Jointly Owned | CCCB_TP-CCCB-230.0-1 | Transmission Line | 5967 | 2412 | 2654 | 2750 | 3026 | 961 | 1057 | 1096 | 1205
CCCB_TP-CDSY-230.0-1 | 5967 | CEDAR CREEK CAP BANK | FOREIGN | CEDAR CREEK SWITCHYARD | FOREIGN | 70821 | 2121 | Jointly Owned | CCCB_TP-CDSY-230.0-1 | FACILITY |  | 2412 | 2654 | 2750 | 3026 | 961 | 1057 | 1096 | 1205
CCCB_TP-CDSY-230.0-1 | 5967 | CEDAR CREEK CAP BANK | FOREIGN | CEDAR CREEK SWITCHYARD | FOREIGN | 70821 | 2121 | Jointly Owned | CCCB_TP-CDSY-230.0-1 | Transmission Line | 5967 | 2412 | 2654 | 2750 | 3026 | 961 | 1057 | 1096 | 1205
CCCB_TP-KEEN-230.0-1 | 5967 | CEDAR CREEK CAP BANK | FOREIGN | KEENESBURG SUBSTATION | XCEL | 70821 | 70820 | Jointly Owned | CCCB_TP-KEEN-230.0-1 | FACILITY |  | 1980 | 1980 | 2091 | 2091 | 789 | 789 | 833 | 833
CCCB_TP-KEEN-230.0-1 | 5967 | CEDAR CREEK CAP BANK | FOREIGN | KEENESBURG SUBSTATION | XCEL | 70821 | 70820 | Jointly Owned |  | LINE_TRAP | KEEN | 1980 | 1980 | 2091 | 2091 | 789 | 789 | 833 | 833
CHAT-WATE-230.0-1 | 5023 | CHATFIELD SUBSTATION | XCEL | WATERTON SUBSTATION | XCEL | 70100 | 70464 | Xcel Owned | CHAT-WATE-230.0-1 | FACILITY |  | 1200 | 1387 | 1437 | 1581 | 478 | 553 | 572 | 630
CHAT-WATE-230.0-1 | 5023 | CHATFIELD SUBSTATION | XCEL | WATERTON SUBSTATION | XCEL | 70100 | 70464 | Xcel Owned | 5023E | SWITCH | WATE | 1200 | 1549 | 1486 | 1780 | 478 | 617 | 592 | 709
CHAT-WATE-230.0-1 | 5023 | CHATFIELD SUBSTATION | XCEL | WATERTON SUBSTATION | XCEL | 70100 | 70464 | Xcel Owned | CHAT-WATE-230.0-1 | Transmission Line | 5023 | 1261 | 1387 | 1437 | 1581 | 502 | 553 | 572 | 630
CHER-CONS-115.0-1 | 9549 | CHEROKEE SWITCHYARD SUBSTATION | XCEL | CONOCO SOUTH SUBSTATION | XCEL | 70110 | 70126 | Xcel Owned | CHER-CONS-115.0-1 | FACILITY |  | 918 | 1069 | 1093 | 1154 | 183 | 213 | 218 | 230
CHER-CONS-115.0-1 | 9549 | CHEROKEE SWITCHYARD SUBSTATION | XCEL | CONOCO SOUTH SUBSTATION | XCEL | 70110 | 70126 | Xcel Owned | Arbutus | BUSBAR_SECTION | CONS | 918 | 1069 | 1093 | 1216 | 183 | 213 | 218 | 242
CHER-CONS-115.0-1 | 9549 | CHEROKEE SWITCHYARD SUBSTATION | XCEL | CONOCO SOUTH SUBSTATION | XCEL | 70110 | 70126 | Xcel Owned | CHER-CONS-115.0-1 | Transmission Line | 9549 | 1081 | 1081 | 1154 | 1154 | 215 | 215 | 230 | 230
CHER-DERB_TP-115.0-1 | 9543 | CHEROKEE SWITCHYARD SUBSTATION | XCEL | DERBY TAP | XCEL | 70110 | 70153 | Xcel Owned | CHER-DERB_TP-115.0-1 | FACILITY |  | 800 | 880 | 909 | 1000 | 159 | 175 | 181 | 199
CHER-DERB_TP-115.0-1 | 9543 | CHEROKEE SWITCHYARD SUBSTATION | XCEL | DERBY TAP | XCEL | 70110 | 70153 | Xcel Owned | CHER-DERB_TP-115.0-1 | Transmission Line | 9543 | 800 | 880 | 909 | 1000 | 159 | 175 | 181 | 199
CHER-DERB-115.0-1 | 9544 | CHEROKEE SWITCHYARD SUBSTATION | XCEL | DERBY SUBSTATION | XCEL | 70110 | 70154 | Xcel Owned | CHER-DERB-115.0-1 | FACILITY |  | 800 | 880 | 909 | 1000 | 159 | 175 | 181 | 199
CHER-DERB-115.0-1 | 9544 | CHEROKEE SWITCHYARD SUBSTATION | XCEL | DERBY SUBSTATION | XCEL | 70110 | 70154 | Xcel Owned | CHER-DERB-115.0-1 | Transmission Line | 9544 | 800 | 880 | 909 | 1000 | 159 | 175 | 181 | 199
CHER-FEDE-115.0-1 | 9558 | CHEROKEE SWITCHYARD SUBSTATION | XCEL | FEDERAL HEIGHTS SUBSTATION | XCEL | 70110 | 70174 | Xcel Owned | CHER-FEDE-115.0-1 | FACILITY |  | 1030 | 1133 | 1107 | 1217 | 205 | 226 | 220 | 242
CHER-FEDE-115.0-1 | 9558 | CHEROKEE SWITCHYARD SUBSTATION | XCEL | FEDERAL HEIGHTS SUBSTATION | XCEL | 70110 | 70174 | Xcel Owned | CHER-FEDE-115.0-1 | Transmission Line | 9558 | 1030 | 1133 | 1107 | 1217 | 205 | 226 | 220 | 242
CHER-FEDE-115.0-2 | 9055 | CHEROKEE SWITCHYARD SUBSTATION | XCEL | FEDERAL HEIGHTS SUBSTATION | XCEL | 70110 | 70175 | Xcel Owned | CHER-FEDE-115.0-2 | FACILITY |  | 1030 | 1133 | 1107 | 1217 | 205 | 226 | 220 | 242
CHER-FEDE-115.0-2 | 9055 | CHEROKEE SWITCHYARD SUBSTATION | XCEL | FEDERAL HEIGHTS SUBSTATION | XCEL | 70110 | 70175 | Xcel Owned | CHER-FEDE-115.0-2 | Transmission Line | 9055 | 1030 | 1133 | 1107 | 1217 | 205 | 226 | 220 | 242
CHER-GLEN-230.0-1 | 5527 | CHEROKEE SWITCHYARD SUBSTATION | XCEL | GLENN SUBSTATION | XCEL | 70107 | 70200 | Xcel Owned | CHER-GLEN-230.0-1 | FACILITY |  | 1091 | 1271 | 1303 | 1448 | 435 | 506 | 519 | 577
CHER-GLEN-230.0-1 | 5527 | CHEROKEE SWITCHYARD SUBSTATION | XCEL | GLENN SUBSTATION | XCEL | 70107 | 70200 | Xcel Owned | Curlew | BUSBAR_SECTION | CHER | 1091 | 1271 | 1303 | 1448 | 435 | 506 | 519 | 577
CHER-LACO-230.0-1 | 5057 | CHEROKEE SWITCHYARD SUBSTATION | XCEL | LACOMBE SUBSTATION | XCEL | 70107 | 70324 | Xcel Owned | CHER-LACO-230.0-1 | FACILITY |  | 1091 | 1271 | 1303 | 1392 | 435 | 506 | 519 | 555
CHER-LACO-230.0-1 | 5057 | CHEROKEE SWITCHYARD SUBSTATION | XCEL | LACOMBE SUBSTATION | XCEL | 70107 | 70324 | Xcel Owned | Curlew | BUSBAR_SECTION | CHER | 1091 | 1271 | 1303 | 1448 | 435 | 506 | 519 | 577
CHER-LACO-230.0-1 | 5057 | CHEROKEE SWITCHYARD SUBSTATION | XCEL | LACOMBE SUBSTATION | XCEL | 70107 | 70324 | Xcel Owned | CHER-LACO-230.0-1 | Transmission Line | 5057 | 1392 | 1392 | 1392 | 1392 | 555 | 555 | 555 | 555
CHER-MAPL-115.0-1 | 9546 | CHEROKEE SWITCHYARD SUBSTATION | XCEL | MAPLETON SUBSTATION | XCEL | 70108 | 70276 | Xcel Owned | CHER-MAPL-115.0-1 | FACILITY |  | 800 | 880 | 909 | 1000 | 159 | 175 | 181 | 199
CHER-MAPL-115.0-1 | 9546 | CHEROKEE SWITCHYARD SUBSTATION | XCEL | MAPLETON SUBSTATION | XCEL | 70108 | 70276 | Xcel Owned | Hawk | BUSBAR_SECTION | CHER | 800 | 880 | 909 | 1000 | 159 | 175 | 181 | 199
CHER-MAPL-115.0-2 | 9547 | CHEROKEE SWITCHYARD SUBSTATION | XCEL | MAPLETON SUBSTATION | XCEL | 70108 | 70277 | Xcel Owned | CHER-MAPL-115.0-2 | FACILITY |  | 1200 | 1200 | 1200 | 1200 | 239 | 239 | 239 | 239
CHER-MAPL-115.0-2 | 9547 | CHEROKEE SWITCHYARD SUBSTATION | XCEL | MAPLETON SUBSTATION | XCEL | 70108 | 70277 | Xcel Owned | 9547-2 | CIRCUIT_SWITCHER | MAPL | 1200 | 1200 | 1200 | 1200 | 239 | 239 | 239 | 239
CHER-MAPL-115.0-2 | 9547 | CHEROKEE SWITCHYARD SUBSTATION | XCEL | MAPLETON SUBSTATION | XCEL | 70108 | 70277 | Xcel Owned | 9547E | SWITCH | CHER | 1200 | 1549 | 1486 | 1780 | 239 | 309 | 296 | 355
CHER-MAPL-115.0-2 | 9547 | CHEROKEE SWITCHYARD SUBSTATION | XCEL | MAPLETON SUBSTATION | XCEL | 70108 | 70277 | Xcel Owned | 9536N | SWITCH | CHER | 1200 | 1549 | 1486 | 1780 | 239 | 309 | 296 | 355
CHER-METO-115.0-1 | 9548 | CHEROKEE SWITCHYARD SUBSTATION | XCEL | METRO | XCEL | 70110 | 70494 | Xcel Owned | CHER-METO-115.0-1 | FACILITY |  | 800 | 880 | 909 | 1000 | 159 | 175 | 181 | 199
CHER-METO-115.0-1 | 9548 | CHEROKEE SWITCHYARD SUBSTATION | XCEL | METRO | XCEL | 70110 | 70494 | Xcel Owned | CHER-METO-115.0-1 | Transmission Line | 9548 | 800 | 880 | 909 | 1000 | 159 | 175 | 181 | 199
CHER-METO-115.0-1 | 9548 | CHEROKEE SWITCHYARD SUBSTATION | XCEL | METRO | XCEL | 70110 | 70494 | Xcel Owned | Hawk | BUSBAR_SECTION | CHER | 800 | 880 | 909 | 1000 | 159 | 175 | 181 | 199
CHER-RIVE-230.0-1 | 5309 | CHEROKEE SWITCHYARD SUBSTATION | XCEL | RIVERDALE SUBSTATION | XCEL | 70107 | 70362 | Xcel Owned | CHER-RIVE-230.0-1 | FACILITY |  | 1220 | 1398 | 1448 | 1593 | 486 | 557 | 577 | 635
CHER-RIVE-230.0-1 | 5309 | CHEROKEE SWITCHYARD SUBSTATION | XCEL | RIVERDALE SUBSTATION | XCEL | 70107 | 70362 | Xcel Owned | Narcissus | BUSBAR_SECTION | CHER | 1220 | 1427 | 1458 | 1626 | 486 | 569 | 581 | 648
CHER-RIVE-230.0-1 | 5309 | CHEROKEE SWITCHYARD SUBSTATION | XCEL | RIVERDALE SUBSTATION | XCEL | 70107 | 70362 | Xcel Owned | CHER-RIVE-230.0-1 | Transmission Line | 5309 | 1271 | 1398 | 1448 | 1593 | 506 | 557 | 577 | 635
CHER-SISA-230.0-1 | 5055 | CHEROKEE SWITCHYARD SUBSTATION | XCEL | SILVER SADDLE SUBSTATION | XCEL | 70107 | 70609 | Xcel Owned | CHER-SISA-230.0-1 | FACILITY |  | 1220 | 1398 | 1448 | 1593 | 486 | 557 | 577 | 635
CHER-SISA-230.0-1 | 5055 | CHEROKEE SWITCHYARD SUBSTATION | XCEL | SILVER SADDLE SUBSTATION | XCEL | 70107 | 70609 | Xcel Owned | Narcissus | BUSBAR_SECTION | CHER | 1220 | 1427 | 1458 | 1626 | 486 | 569 | 581 | 648
CHER-SISA-230.0-1 | 5055 | CHEROKEE SWITCHYARD SUBSTATION | XCEL | SILVER SADDLE SUBSTATION | XCEL | 70107 | 70609 | Xcel Owned | CHER-SISA-230.0-1 | Transmission Line | 5055 | 1271 | 1398 | 1448 | 1593 | 506 | 557 | 577 | 635
CHER-SISA-230.0-1 | 5055 | CHEROKEE SWITCHYARD SUBSTATION | XCEL | SILVER SADDLE SUBSTATION | XCEL | 70107 | 70609 | Xcel Owned | Orchid | BUSBAR_SECTION | SISA | 1271 | 1398 | 1448 | 1593 | 506 | 557 | 577 | 635
CHYW-GOOS-345.0-1 | 7261 | CHEYENNE RIDGE WEST (ES) | FOREIGN | GOOSE CREEK | XCEL | 70632 | 70918 | Jointly Owned | CHYW-GOOS-345.0-1 | FACILITY |  | 1200 | 1200 | 1200 | 1200 | 717 | 717 | 717 | 717
CHYW-GOOS-345.0-1 | 7261 | CHEYENNE RIDGE WEST (ES) | FOREIGN | GOOSE CREEK | XCEL | 70632 | 70918 | Jointly Owned | 7261C | CURRENT_TRANSFORMER | GOOS | 1200 | 1200 | 1200 | 1200 | 717 | 717 | 717 | 717
CHYW-GOOS-345.0-1 | 7261 | CHEYENNE RIDGE WEST (ES) | FOREIGN | GOOSE CREEK | XCEL | 70632 | 70918 | Jointly Owned | 7261A | CURRENT_TRANSFORMER | GOOS | 1200 | 1200 | 1200 | 1200 | 717 | 717 | 717 | 717
CHYW-GOOS-345.0-1 | 7261 | CHEYENNE RIDGE WEST (ES) | FOREIGN | GOOSE CREEK | XCEL | 70632 | 70918 | Jointly Owned | 7261B | CURRENT_TRANSFORMER | GOOS | 1200 | 1200 | 1200 | 1200 | 717 | 717 | 717 | 717
CLAR-GREE-230.0-1 | 5435 | CLARK SUBSTATION | XCEL | GREENWOOD SUBSTATION | XCEL | 70112 | 70212 | Xcel Owned | CLAR-GREE-230.0-1 | FACILITY |  | 920 | 1012 | 920 | 1012 | 367 | 403 | 367 | 403
CLAR-GREE-230.0-1 | 5435 | CLARK SUBSTATION | XCEL | GREENWOOD SUBSTATION | XCEL | 70112 | 70212 | Xcel Owned | CLAR-GREE-230.0-1 | Transmission Line | 5435 | 920 | 1012 | 920 | 1012 | 367 | 403 | 367 | 403
CLAR-JORD-230.0-1 | 5435 | CLARK SUBSTATION | XCEL | JORDAN ROAD SUBSTATION | XCEL | 70112 | 70241 | Xcel Owned | CLAR-JORD-230.0-1 | FACILITY |  | 830 | 913 | 830 | 913 | 331 | 364 | 331 | 364
CLAR-JORD-230.0-1 | 5435 | CLARK SUBSTATION | XCEL | JORDAN ROAD SUBSTATION | XCEL | 70112 | 70241 | Xcel Owned | CLAR-JORD-230.0-1 | Transmission Line | 5435 | 830 | 913 | 830 | 913 | 331 | 364 | 331 | 364
CLIF-GJCT-230.0-1 | 5557 | CLIFTON SUBSTATION | XCEL | GRAND JUNCTION SUBSTATION (PSCO) | XCEL | 70113 | 70206 | Xcel Owned | CLIF-GJCT-230.0-1 | FACILITY |  | 1200 | 1435 | 1466 | 1600 | 478 | 571 | 584 | 637
CLIF-GJCT-230.0-1 | 5557 | CLIFTON SUBSTATION | XCEL | GRAND JUNCTION SUBSTATION (PSCO) | XCEL | 70113 | 70206 | Xcel Owned | 5580 | SWITCH | CLIF | 1200 | 1549 | 1486 | 1780 | 478 | 617 | 592 | 709
CLIF-GJCT-230.0-1 | 5557 | CLIFTON SUBSTATION | XCEL | GRAND JUNCTION SUBSTATION (PSCO) | XCEL | 70113 | 70206 | Xcel Owned | Narcissus | BUSBAR_SECTION | CLIF | 1227 | 1435 | 1466 | 1634 | 489 | 571 | 584 | 651
CLIF-GJCT-230.0-1 | 5557 | CLIFTON SUBSTATION | XCEL | GRAND JUNCTION SUBSTATION (PSCO) | XCEL | 70113 | 70206 | Xcel Owned | 5557-1 | CIRCUIT_SWITCHER | CLIF | 1600 | 1600 | 1600 | 1600 | 637 | 637 | 637 | 637
CLIF-UTEG-230.0-1 | 5557 | CLIFTON SUBSTATION | XCEL | UTE GRAND JUNCTION SUBSTATION | XCEL | 70113 | 70205 | Xcel Owned | CLIF-UTEG-230.0-1 | FACILITY |  | 1200 | 1431 | 1462 | 1600 | 478 | 570 | 583 | 637
CLIF-UTEG-230.0-1 | 5557 | CLIFTON SUBSTATION | XCEL | UTE GRAND JUNCTION SUBSTATION | XCEL | 70113 | 70205 | Xcel Owned | 5557M | SWITCH | UTEG | 1200 | 1549 | 1486 | 1780 | 478 | 617 | 592 | 709
CLIF-UTEG-230.0-1 | 5557 | CLIFTON SUBSTATION | XCEL | UTE GRAND JUNCTION SUBSTATION | XCEL | 70113 | 70205 | Xcel Owned | 5580 | SWITCH | CLIF | 1200 | 1549 | 1486 | 1780 | 478 | 617 | 592 | 709
CLIF-UTEG-230.0-1 | 5557 | CLIFTON SUBSTATION | XCEL | UTE GRAND JUNCTION SUBSTATION | XCEL | 70113 | 70205 | Xcel Owned | Narcissus | BUSBAR_SECTION | UTEG | 1224 | 1431 | 1462 | 1630 | 488 | 570 | 583 | 649
CLIF-UTEG-230.0-1 | 5557 | CLIFTON SUBSTATION | XCEL | UTE GRAND JUNCTION SUBSTATION | XCEL | 70113 | 70205 | Xcel Owned | 5557-2 | CIRCUIT_SWITCHER | CLIF | 1600 | 1600 | 1600 | 1600 | 637 | 637 | 637 | 637
CLIM-LEAD_TP1-115.0-1 | 9254 | CLIMAX SUBSTATION | XCEL | LEADVILLE TAP 1 | XCEL | 70114 | 2114 | Xcel Owned | CLIM-LEAD_TP1-115.0-1 | FACILITY |  | 386 | 425 | 417 | 459 | 77 | 85 | 83 | 91
CLIM-LEAD_TP1-115.0-1 | 9254 | CLIMAX SUBSTATION | XCEL | LEADVILLE TAP 1 | XCEL | 70114 | 2114 | Xcel Owned | CLIM-LEAD_TP1-115.0-1 | Transmission Line | 9254 | 386 | 425 | 417 | 459 | 77 | 85 | 83 | 91
CLIM-MAYF-115.0-1 | 8174 | CLIMAX SUBSTATION | XCEL | MAYFLOWER SUBSTATION | XCEL | 70114 | 70281 | Xcel Owned | CLIM-MAYF-115.0-1 | FACILITY |  | 442 | 480 | 477 | 500 | 88 | 96 | 95 | 100
CLIM-MAYF-115.0-1 | 8174 | CLIMAX SUBSTATION | XCEL | MAYFLOWER SUBSTATION | XCEL | 70114 | 70281 | Xcel Owned | CLIM-MAYF-115.0-1 | Transmission Line | 8174 | 442 | 480 | 477 | 525 | 88 | 96 | 95 | 105
CLIM-MAYF-115.0-1 | 8174 | CLIMAX SUBSTATION | XCEL | MAYFLOWER SUBSTATION | XCEL | 70114 | 70281 | Xcel Owned | 8174 METER AMPSW | SECONDARY_CURRENT_LIMITATION | CLIM | 500 | 500 | 500 | 500 | 100 | 100 | 100 | 100
CLIM-MAYF-115.0-1 | 8174 | CLIMAX SUBSTATION | XCEL | MAYFLOWER SUBSTATION | XCEL | 70114 | 70281 | Xcel Owned | 8174 246X W XDCR | SECONDARY_CURRENT_LIMITATION | CLIM | 500 | 500 | 500 | 500 | 100 | 100 | 100 | 100
CLIM-MAYF-115.0-1 | 8174 | CLIMAX SUBSTATION | XCEL | MAYFLOWER SUBSTATION | XCEL | 70114 | 70281 | Xcel Owned | 8174 246X VAR XDCR | SECONDARY_CURRENT_LIMITATION | CLIM | 500 | 500 | 500 | 500 | 100 | 100 | 100 | 100
CLIM-MAYF-115.0-1 | 8174 | CLIMAX SUBSTATION | XCEL | MAYFLOWER SUBSTATION | XCEL | 70114 | 70281 | Xcel Owned | 8174 METER W | SECONDARY_CURRENT_LIMITATION | CLIM | 500 | 500 | 500 | 500 | 100 | 100 | 100 | 100
CLIM-MAYF-115.0-1 | 8174 | CLIMAX SUBSTATION | XCEL | MAYFLOWER SUBSTATION | XCEL | 70114 | 70281 | Xcel Owned | 8174 METER VAR | SECONDARY_CURRENT_LIMITATION | CLIM | 500 | 500 | 500 | 500 | 100 | 100 | 100 | 100
CLIM-ROBI-115.0-1 | 9257 | CLIMAX SUBSTATION | XCEL | ROBINSON RACK | XCEL | 70114 | 70389 | Xcel Owned | CLIM-ROBI-115.0-1 | FACILITY |  | 370 | 400 | 400 | 400 | 74 | 80 | 80 | 80
CLIM-ROBI-115.0-1 | 9257 | CLIMAX SUBSTATION | XCEL | ROBINSON RACK | XCEL | 70114 | 70389 | Xcel Owned | CLIM-ROBI-115.0-1 | Transmission Line | 9257 | 370 | 407 | 420 | 462 | 74 | 81 | 84 | 92
CLIM-ROBI-115.0-1 | 9257 | CLIMAX SUBSTATION | XCEL | ROBINSON RACK | XCEL | 70114 | 70389 | Xcel Owned | 9257 METER W | SECONDARY_CURRENT_LIMITATION | CLIM | 400 | 400 | 400 | 400 | 80 | 80 | 80 | 80
CLIM-ROBI-115.0-1 | 9257 | CLIMAX SUBSTATION | XCEL | ROBINSON RACK | XCEL | 70114 | 70389 | Xcel Owned | 9257 METER AMPSW | SECONDARY_CURRENT_LIMITATION | CLIM | 400 | 400 | 400 | 400 | 80 | 80 | 80 | 80
CLIM-ROBI-115.0-1 | 9257 | CLIMAX SUBSTATION | XCEL | ROBINSON RACK | XCEL | 70114 | 70389 | Xcel Owned | 9257 135X VAR XDCR | SECONDARY_CURRENT_LIMITATION | CLIM | 400 | 400 | 400 | 400 | 80 | 80 | 80 | 80
CLIM-ROBI-115.0-1 | 9257 | CLIMAX SUBSTATION | XCEL | ROBINSON RACK | XCEL | 70114 | 70389 | Xcel Owned | 9257 METER VAR | SECONDARY_CURRENT_LIMITATION | CLIM | 400 | 400 | 400 | 400 | 80 | 80 | 80 | 80
CLIM-ROBI-115.0-1 | 9257 | CLIMAX SUBSTATION | XCEL | ROBINSON RACK | XCEL | 70114 | 70389 | Xcel Owned | 9257 135X W XDCR | SECONDARY_CURRENT_LIMITATION | CLIM | 400 | 400 | 400 | 400 | 80 | 80 | 80 | 80
CLVR-DCPL_TP-115.0-1 | 8266 | CLOVERLY SUBSTATION | XCEL | DCP LUCERNE | FOREIGN | 70903 | 2133 | Xcel Owned | CLVR-DCPL_TP-115.0-1 | FACILITY |  | 1110 | 1221 | 1263 | 1390 | 221 | 243 | 252 | 277
CLVR-DCPL_TP-115.0-1 | 8266 | CLOVERLY SUBSTATION | XCEL | DCP LUCERNE | FOREIGN | 70903 | 2133 | Xcel Owned | CLVR-DCPL_TP-115.0-1 | Transmission Line | 8266 | 1110 | 1221 | 1263 | 1390 | 221 | 243 | 252 | 277
COLL-UTER-138.0-1 | 3014 | COLLBRAN SUBSTATION | XCEL | RIFLE UTE 230/345KV SUBSTATION | XCEL | 79047 | 79056 | Jointly Owned | COLL-UTER-138.0-1 | FACILITY |  | 400 | 400 | 400 | 400 | 96 | 96 | 96 | 96
COLL-UTER-138.0-1 | 3014 | COLLBRAN SUBSTATION | XCEL | RIFLE UTE 230/345KV SUBSTATION | XCEL | 79047 | 79056 | Jointly Owned | R821 135X | CURRENT_TRANSFORMER | UTER | 400 | 400 | 400 | 400 | 96 | 96 | 96 | 96
COLL-UTER-138.0-1 | 3014 | COLLBRAN SUBSTATION | XCEL | RIFLE UTE 230/345KV SUBSTATION | XCEL | 79047 | 79056 | Jointly Owned | 3014 GCX17 B 21Z1 | SECONDARY_CURRENT_LIMITATION | UTER | 400 | 400 | 400 | 400 | 96 | 96 | 96 | 96
COLL-UTER-138.0-1 | 3014 | COLLBRAN SUBSTATION | XCEL | RIFLE UTE 230/345KV SUBSTATION | XCEL | 79047 | 79056 | Jointly Owned | 3014 GCX17 C 21Z1 | SECONDARY_CURRENT_LIMITATION | UTER | 400 | 400 | 400 | 400 | 96 | 96 | 96 | 96
COLL-UTER-138.0-1 | 3014 | COLLBRAN SUBSTATION | XCEL | RIFLE UTE 230/345KV SUBSTATION | XCEL | 79047 | 79056 | Jointly Owned | 3014 GCX17 A 21Z1 | SECONDARY_CURRENT_LIMITATION | UTER | 400 | 400 | 400 | 400 | 96 | 96 | 96 | 96
COLL-UTER-138.0-1 | 3014 | COLLBRAN SUBSTATION | XCEL | RIFLE UTE 230/345KV SUBSTATION | XCEL | 79047 | 79056 | Jointly Owned | COLL-UTER-138.0-1 | Transmission Line | 3014 | 400 | 440 | 400 | 440 | 96 | 105 | 96 | 105
COMA-CALU-230.0-1 | 5408 | COMANCHE SUBSTATION | XCEL | WALSENBURG (TSGT) | FOREIGN | 70122 | 70459 | Jointly Owned | COMA-CALU-230.0-1 | FACILITY |  | 900 | 900 | 900 | 900 | 359 | 359 | 359 | 359
COMA-CALU-230.0-1 | 5408 | COMANCHE SUBSTATION | XCEL | WALSENBURG (TSGT) | FOREIGN | 70122 | 70459 | Jointly Owned | TL5408XDCRAMP | SECONDARY_CURRENT_LIMITATION | COMA | 900 | 900 | 900 | 900 | 359 | 359 | 359 | 359
COMA-MIDW-230.0-1 | 5411 | COMANCHE SUBSTATION | XCEL | MIDWAY SUBSTATION | XCEL | 70122 | 70286 | Xcel Owned | COMA-MIDW-230.0-1 | FACILITY |  | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
COMA-MIDW-230.0-1 | 5411 | COMANCHE SUBSTATION | XCEL | MIDWAY SUBSTATION | XCEL | 70122 | 70286 | Xcel Owned | TL5411XDCRAMP | SECONDARY_CURRENT_LIMITATION | COMA | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
COMA-MIDW-230.0-1 | 5411 | COMANCHE SUBSTATION | XCEL | MIDWAY SUBSTATION | XCEL | 70122 | 70286 | Xcel Owned | 5411 135X | CURRENT_TRANSFORMER | MIDW | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
COMA-MIDW-230.0-1 | 5411 | COMANCHE SUBSTATION | XCEL | MIDWAY SUBSTATION | XCEL | 70122 | 70286 | Xcel Owned | 5411_VAR_230KV | SECONDARY_CURRENT_LIMITATION | MIDW | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
COMA-MIDW-230.0-1 | 5411 | COMANCHE SUBSTATION | XCEL | MIDWAY SUBSTATION | XCEL | 70122 | 70286 | Xcel Owned | 5411_AM_230KV | SECONDARY_CURRENT_LIMITATION | MIDW | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
COMA-MIDW-230.0-1 | 5411 | COMANCHE SUBSTATION | XCEL | MIDWAY SUBSTATION | XCEL | 70122 | 70286 | Xcel Owned | 5117 135Y | CURRENT_TRANSFORMER | MIDW | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
COMA-MIDW-230.0-1 | 5411 | COMANCHE SUBSTATION | XCEL | MIDWAY SUBSTATION | XCEL | 70122 | 70286 | Xcel Owned | 5411_AM_SWITCH_230KV | SECONDARY_CURRENT_LIMITATION | MIDW | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
COMA-MIDW-230.0-1 | 5411 | COMANCHE SUBSTATION | XCEL | MIDWAY SUBSTATION | XCEL | 70122 | 70286 | Xcel Owned | 5411_W_XDCR_230KV | SECONDARY_CURRENT_LIMITATION | MIDW | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
COMA-MIDW-230.0-1 | 5411 | COMANCHE SUBSTATION | XCEL | MIDWAY SUBSTATION | XCEL | 70122 | 70286 | Xcel Owned | TL5411XDCRW/VAR | SECONDARY_CURRENT_LIMITATION | COMA | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
COMA-MIDW-230.0-1 | 5411 | COMANCHE SUBSTATION | XCEL | MIDWAY SUBSTATION | XCEL | 70122 | 70286 | Xcel Owned | 5124 246X | CURRENT_TRANSFORMER | MIDW | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
COMA-MIDW-230.0-1 | 5411 | COMANCHE SUBSTATION | XCEL | MIDWAY SUBSTATION | XCEL | 70122 | 70286 | Xcel Owned | 5124 135Y | CURRENT_TRANSFORMER | MIDW | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
COMA-MIDW-230.0-1 | 5411 | COMANCHE SUBSTATION | XCEL | MIDWAY SUBSTATION | XCEL | 70122 | 70286 | Xcel Owned | 5411_A_XDCR_B_230KV | SECONDARY_CURRENT_LIMITATION | MIDW | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
COMA-MIDW-230.0-1 | 5411 | COMANCHE SUBSTATION | XCEL | MIDWAY SUBSTATION | XCEL | 70122 | 70286 | Xcel Owned | 5411_A_XDCR_A_230KV | SECONDARY_CURRENT_LIMITATION | MIDW | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
COMA-MIDW-230.0-1 | 5411 | COMANCHE SUBSTATION | XCEL | MIDWAY SUBSTATION | XCEL | 70122 | 70286 | Xcel Owned | 5410 246Y | CURRENT_TRANSFORMER | COMA | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
COMA-MIDW-230.0-1 | 5411 | COMANCHE SUBSTATION | XCEL | MIDWAY SUBSTATION | XCEL | 70122 | 70286 | Xcel Owned | 5411_21Z1/2-A | SECONDARY_CURRENT_LIMITATION | COMA | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
COMA-MIDW-230.0-1 | 5411 | COMANCHE SUBSTATION | XCEL | MIDWAY SUBSTATION | XCEL | 70122 | 70286 | Xcel Owned | 5411_21Z1/2-C | SECONDARY_CURRENT_LIMITATION | COMA | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
COMA-MIDW-230.0-1 | 5411 | COMANCHE SUBSTATION | XCEL | MIDWAY SUBSTATION | XCEL | 70122 | 70286 | Xcel Owned | 5124 135X | CURRENT_TRANSFORMER | MIDW | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
COMA-MIDW-230.0-1 | 5411 | COMANCHE SUBSTATION | XCEL | MIDWAY SUBSTATION | XCEL | 70122 | 70286 | Xcel Owned | 5117 246Y | CURRENT_TRANSFORMER | MIDW | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
COMA-MIDW-230.0-1 | 5411 | COMANCHE SUBSTATION | XCEL | MIDWAY SUBSTATION | XCEL | 70122 | 70286 | Xcel Owned | 5411_67GP | SECONDARY_CURRENT_LIMITATION | COMA | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
COMA-MIDW-230.0-1 | 5411 | COMANCHE SUBSTATION | XCEL | MIDWAY SUBSTATION | XCEL | 70122 | 70286 | Xcel Owned | 5411_21Z1/2-B | SECONDARY_CURRENT_LIMITATION | COMA | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
COMA-MIDW-230.0-1 | 5411 | COMANCHE SUBSTATION | XCEL | MIDWAY SUBSTATION | XCEL | 70122 | 70286 | Xcel Owned | 5411_VAR_XDCR_230KV | SECONDARY_CURRENT_LIMITATION | MIDW | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
COMA-MIDW-230.0-1 | 5411 | COMANCHE SUBSTATION | XCEL | MIDWAY SUBSTATION | XCEL | 70122 | 70286 | Xcel Owned | 5410 246X | CURRENT_TRANSFORMER | COMA | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
COMA-MIDW-230.0-1 | 5411 | COMANCHE SUBSTATION | XCEL | MIDWAY SUBSTATION | XCEL | 70122 | 70286 | Xcel Owned | 5411_21ZP | SECONDARY_CURRENT_LIMITATION | COMA | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
COMA-MIDW-230.0-1 | 5411 | COMANCHE SUBSTATION | XCEL | MIDWAY SUBSTATION | XCEL | 70122 | 70286 | Xcel Owned | 5411 246X | CURRENT_TRANSFORMER | MIDW | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
COMA-MIDW-230.0-1 | 5411 | COMANCHE SUBSTATION | XCEL | MIDWAY SUBSTATION | XCEL | 70122 | 70286 | Xcel Owned | 5117 246X | CURRENT_TRANSFORMER | MIDW | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
COMA-MIDW-230.0-1 | 5411 | COMANCHE SUBSTATION | XCEL | MIDWAY SUBSTATION | XCEL | 70122 | 70286 | Xcel Owned | 5124 246Y | CURRENT_TRANSFORMER | MIDW | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
COMA-MIDW-230.0-1 | 5411 | COMANCHE SUBSTATION | XCEL | MIDWAY SUBSTATION | XCEL | 70122 | 70286 | Xcel Owned | 5411 246Y | CURRENT_TRANSFORMER | MIDW | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
COMA-MIDW-230.0-1 | 5411 | COMANCHE SUBSTATION | XCEL | MIDWAY SUBSTATION | XCEL | 70122 | 70286 | Xcel Owned | 5411_W_230KV | SECONDARY_CURRENT_LIMITATION | MIDW | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
COMA-MIDW-230.0-1 | 5411 | COMANCHE SUBSTATION | XCEL | MIDWAY SUBSTATION | XCEL | 70122 | 70286 | Xcel Owned | 5117 135X | CURRENT_TRANSFORMER | MIDW | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
COMA-MIDW-230.0-1 | 5411 | COMANCHE SUBSTATION | XCEL | MIDWAY SUBSTATION | XCEL | 70122 | 70286 | Xcel Owned | 5411 135Y | CURRENT_TRANSFORMER | MIDW | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
COMA-MIDW-230.0-1 | 5411 | COMANCHE SUBSTATION | XCEL | MIDWAY SUBSTATION | XCEL | 70122 | 70286 | Xcel Owned | 5411_A_XDCR_C_230KV | SECONDARY_CURRENT_LIMITATION | MIDW | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
COMA-MIDW-230.0-1 | 5411 | COMANCHE SUBSTATION | XCEL | MIDWAY SUBSTATION | XCEL | 70122 | 70286 | Xcel Owned | 5411N | SWITCH | MIDW | 1200 | 1549 | 1486 | 1780 | 478 | 617 | 592 | 709
COMA-MIDW-230.0-1 | 5411 | COMANCHE SUBSTATION | XCEL | MIDWAY SUBSTATION | XCEL | 70122 | 70286 | Xcel Owned | 5117N | SWITCH | MIDW | 1200 | 1549 | 1486 | 1780 | 478 | 617 | 592 | 709
COMA-MIDW-230.0-1 | 5411 | COMANCHE SUBSTATION | XCEL | MIDWAY SUBSTATION | XCEL | 70122 | 70286 | Xcel Owned | 5411S | SWITCH | COMA | 1200 | 1549 | 1486 | 1780 | 478 | 617 | 592 | 709
COMA-MIDW-230.0-1 | 5411 | COMANCHE SUBSTATION | XCEL | MIDWAY SUBSTATION | XCEL | 70122 | 70286 | Xcel Owned | 5410N | SWITCH | COMA | 1200 | 1549 | 1486 | 1780 | 478 | 617 | 592 | 709
COMA-MIDW-230.0-1 | 5411 | COMANCHE SUBSTATION | XCEL | MIDWAY SUBSTATION | XCEL | 70122 | 70286 | Xcel Owned | 5410S | SWITCH | COMA | 1200 | 1549 | 1486 | 1780 | 478 | 617 | 592 | 709
COMA-MIDW-230.0-1 | 5411 | COMANCHE SUBSTATION | XCEL | MIDWAY SUBSTATION | XCEL | 70122 | 70286 | Xcel Owned | 5411S | SWITCH | MIDW | 1200 | 1549 | 1486 | 1780 | 478 | 617 | 592 | 709
COMA-MIDW-230.0-1 | 5411 | COMANCHE SUBSTATION | XCEL | MIDWAY SUBSTATION | XCEL | 70122 | 70286 | Xcel Owned | 5411N | SWITCH | COMA | 1200 | 1549 | 1486 | 1780 | 478 | 617 | 592 | 709
COMA-MIDW-230.0-1 | 5411 | COMANCHE SUBSTATION | XCEL | MIDWAY SUBSTATION | XCEL | 70122 | 70286 | Xcel Owned | 5124N | SWITCH | MIDW | 1200 | 1549 | 1486 | 1780 | 478 | 617 | 592 | 709
COMA-MIDW-230.0-1 | 5411 | COMANCHE SUBSTATION | XCEL | MIDWAY SUBSTATION | XCEL | 70122 | 70286 | Xcel Owned | 5117S | SWITCH | MIDW | 1200 | 1549 | 1486 | 1780 | 478 | 617 | 592 | 709
COMA-MIDW-230.0-1 | 5411 | COMANCHE SUBSTATION | XCEL | MIDWAY SUBSTATION | XCEL | 70122 | 70286 | Xcel Owned | 5124S | SWITCH | MIDW | 1200 | 1549 | 1486 | 1780 | 478 | 617 | 592 | 709
COMA-MSOL-230.0-1 | 5413 | COMANCHE SUBSTATION | XCEL | MIRASOL SUBSTATION | XCEL | 70122 | 70652 | Xcel Owned | COMA-MSOL-230.0-1 | FACILITY |  | 1200 | 1403 | 1200 | 1546 | 478 | 559 | 478 | 616
COMA-MSOL-230.0-1 | 5413 | COMANCHE SUBSTATION | XCEL | MIRASOL SUBSTATION | XCEL | 70122 | 70652 | Xcel Owned | Foreign Ratings | Foreign Ratings | COMA | 1200 | 1546 | 1200 | 1546 | 478 | 616 | 478 | 616
COMA-MSOL-230.0-1 | 5413 | COMANCHE SUBSTATION | XCEL | MIRASOL SUBSTATION | XCEL | 70122 | 70652 | Xcel Owned | COMA-MSOL-230.0-1 | Transmission Line | 5413 | 1276 | 1403 | 1452 | 1597 | 508 | 559 | 578 | 636
COMA-READ-115.0-1 | 9986 | COMANCHE SUBSTATION | XCEL | Reader | FOREIGN | 70121 | 70352 | Jointly Owned | COMA-READ-115.0-1 | FACILITY |  | 1900 | 1900 | 1900 | 1900 | 378 | 378 | 378 | 378
COMA-READ-115.0-1 | 9986 | COMANCHE SUBSTATION | XCEL | Reader | FOREIGN | 70121 | 70352 | Jointly Owned | COMA-READ-115.0-1 | Transmission Line | 9986 | 1900 | 1900 | 1900 | 1900 | 378 | 378 | 378 | 378
COMA-READ-115.0-2 | 9984 | COMANCHE SUBSTATION | XCEL | Reader | FOREIGN | 70123 | 70352 | Jointly Owned | COMA-READ-115.0-2 | FACILITY |  | 1600 | 1600 | 1600 | 1600 | 319 | 319 | 319 | 319
COMA-READ-115.0-2 | 9984 | COMANCHE SUBSTATION | XCEL | Reader | FOREIGN | 70123 | 70352 | Jointly Owned | 9984 | BREAKER | COMA | 1600 | 1600 | 1600 | 1600 | 319 | 319 | 319 | 319
COMA-TUND-345.0-1 | 7015 | COMANCHE SUBSTATION | XCEL | TUNDRA SUBSTATION | XCEL | 70654 | 70653 | Xcel Owned | COMA-TUND-345.0-1 | FACILITY |  | 2000 | 2000 | 2112 | 2112 | 1195 | 1195 | 1262 | 1262
COMA-TUND-345.0-1 | 7015 | COMANCHE SUBSTATION | XCEL | TUNDRA SUBSTATION | XCEL | 70654 | 70653 | Xcel Owned |  | LINE_TRAP | COMA | 2000 | 2000 | 2112 | 2112 | 1195 | 1195 | 1262 | 1262
CONS-SAND-115.0-1 | 9549 | CONOCO SOUTH SUBSTATION | XCEL | SANDOWN SUBSTATION | XCEL | 70126 | 70377 | Xcel Owned | CONS-SAND-115.0-1 | FACILITY |  | 799 | 879 | 909 | 999 | 159 | 175 | 181 | 199
CONS-SAND-115.0-1 | 9549 | CONOCO SOUTH SUBSTATION | XCEL | SANDOWN SUBSTATION | XCEL | 70126 | 70377 | Xcel Owned | CONS-SAND-115.0-1 | Transmission Line | 9549 | 799 | 879 | 909 | 999 | 159 | 175 | 181 | 199
COOL-BASA-230.0-1 | 5787 | COOLEY MESA (HOLY CROSS) | FOREIGN | BASALT SUBSTATION | XCEL | 70535 | 79004 | Jointly Owned | COOL-BASA-230.0-1 | FACILITY |  | 1422 | 1564 | 1600 | 1600 | 566 | 623 | 637 | 637
COOL-BASA-230.0-1 | 5787 | COOLEY MESA (HOLY CROSS) | FOREIGN | BASALT SUBSTATION | XCEL | 70535 | 79004 | Jointly Owned | Bittern | BUSBAR_SECTION | BASA | 1422 | 1564 | 1622 | 1784 | 566 | 623 | 646 | 711
COOL-BASA-230.0-1 | 5787 | COOLEY MESA (HOLY CROSS) | FOREIGN | BASALT SUBSTATION | XCEL | 70535 | 79004 | Jointly Owned | B241 135X | CURRENT_TRANSFORMER | BASA | 1600 | 1600 | 1600 | 1600 | 637 | 637 | 637 | 637
COOL-BASA-230.0-1 | 5787 | COOLEY MESA (HOLY CROSS) | FOREIGN | BASALT SUBSTATION | XCEL | 70535 | 79004 | Jointly Owned | B241 135Y | CURRENT_TRANSFORMER | BASA | 1600 | 1600 | 1600 | 1600 | 637 | 637 | 637 | 637
COOL-BASA-230.0-1 | 5787 | COOLEY MESA (HOLY CROSS) | FOREIGN | BASALT SUBSTATION | XCEL | 70535 | 79004 | Jointly Owned | Foreign Ratings | Foreign Ratings | COOL | 1600 | 1600 | 1600 | 1600 | 637 | 637 | 637 | 637
COOL-BASA-230.0-1 | 5787 | COOLEY MESA (HOLY CROSS) | FOREIGN | BASALT SUBSTATION | XCEL | 70535 | 79004 | Jointly Owned | B231 246Y | CURRENT_TRANSFORMER | BASA | 1600 | 1600 | 1600 | 1600 | 637 | 637 | 637 | 637
COST-CLVR-115.0-1 | 9787 | COLLINS ST SUBSTATION | XCEL | CLOVERLY SUBSTATION | XCEL | 70902 | 70903 | Xcel Owned | COST-CLVR-115.0-1 | FACILITY |  | 1109 | 1220 | 1262 | 1388 | 221 | 243 | 251 | 276
COST-CLVR-115.0-1 | 9787 | COLLINS ST SUBSTATION | XCEL | CLOVERLY SUBSTATION | XCEL | 70902 | 70903 | Xcel Owned | COST-CLVR-115.0-1 | Transmission Line | 9787 | 1109 | 1220 | 1262 | 1388 | 221 | 243 | 251 | 276
COST-HSKY-115.0-1 | 9787 | COLLINS ST SUBSTATION | XCEL | HUSKY SUBSTATION | XCEL | 70902 | 70901 | Xcel Owned | COST-HSKY-115.0-1 | FACILITY |  | 1107 | 1218 | 1260 | 1386 | 220 | 243 | 251 | 276
COST-HSKY-115.0-1 | 9787 | COLLINS ST SUBSTATION | XCEL | HUSKY SUBSTATION | XCEL | 70902 | 70901 | Xcel Owned | COST-HSKY-115.0-1 | Transmission Line | 9787 | 1107 | 1218 | 1260 | 1386 | 220 | 243 | 251 | 276
CRAT-CRAI-230.0-1 | 5831 | CRAIG TRANSFER | XCEL | CRAIG SW YARD | XCEL | 79013 | 70009 | Xcel Owned | CRAT-CRAI-230.0-1 | FACILITY |  | 231 | 231 | 231 | 231 | 92 | 92 | 92 | 92
CRAT-CRAI-230.0-1 | 5831 | CRAIG TRANSFER | XCEL | CRAIG SW YARD | XCEL | 79013 | 70009 | Xcel Owned | 5831_135X_PK | SECONDARY_CURRENT_LIMITATION | CRAT | 231 | 231 | 231 | 231 | 92 | 92 | 92 | 92
CROV-HACA-115.0-1 | 9652 | CROWFOOT VALLEY | XCEL | HAPPY CANYON SUBSTATION | XCEL | 70117 | 70115 | Xcel Owned | CROV-HACA-115.0-1 | FACILITY |  | 1246 | 1395 | 1298 | 1436 | 248 | 278 | 259 | 286
CROV-HACA-115.0-1 | 9652 | CROWFOOT VALLEY | XCEL | HAPPY CANYON SUBSTATION | XCEL | 70117 | 70115 | Xcel Owned | CROV-HACA-115.0-1 | Transmission Line | 9652 | 1246 | 1395 | 1298 | 1436 | 248 | 278 | 259 | 286
DAKO-DTER-230.0-1 | 5623 | DAKOTA SUBSTATION | XCEL | DENVER TERMINAL SUBSTATION | XCEL | 70141 | 70149 | Xcel Owned | DAKO-DTER-230.0-1 | FACILITY |  | 1188 | 1188 | 1379 | 1379 | 473 | 473 | 549 | 549
DAKO-DTER-230.0-1 | 5623 | DAKOTA SUBSTATION | XCEL | DENVER TERMINAL SUBSTATION | XCEL | 70141 | 70149 | Xcel Owned | DAKO-DTER-230.0-1 | Transmission Line | 5623 | 1188 | 1188 | 1379 | 1379 | 473 | 473 | 549 | 549
DANI-COMA-345.0-2 | 7017 | DANIELS PARK 115 & 230KV SUBSTATION | XCEL | COMANCHE SUBSTATION | XCEL | 70601 | 70654 | Xcel Owned | DANI-COMA-345.0-2 | FACILITY |  | 1980 | 1980 | 2091 | 2091 | 1183 | 1183 | 1249 | 1249
DANI-COMA-345.0-2 | 7017 | DANIELS PARK 115 & 230KV SUBSTATION | XCEL | COMANCHE SUBSTATION | XCEL | 70601 | 70654 | Xcel Owned |  | LINE_TRAP | DANI | 1980 | 1980 | 2091 | 2091 | 1183 | 1183 | 1249 | 1249
DANI-HACA-115.0-1 | 9674 | DANIELS PARK 115 & 230KV SUBSTATION | XCEL | HAPPY CANYON SUBSTATION | XCEL | 70138 | 70115 | Xcel Owned | DANI-HACA-115.0-1 | FACILITY |  | 950 | 1045 | 1094 | 1200 | 189 | 208 | 218 | 239
DANI-HACA-115.0-1 | 9674 | DANIELS PARK 115 & 230KV SUBSTATION | XCEL | HAPPY CANYON SUBSTATION | XCEL | 70138 | 70115 | Xcel Owned | 500 - 37 | BUSBAR_SECTION | DANI | 950 | 1045 | 1094 | 1203 | 189 | 208 | 218 | 240
DANI-HACA-115.0-1 | 9674 | DANIELS PARK 115 & 230KV SUBSTATION | XCEL | HAPPY CANYON SUBSTATION | XCEL | 70138 | 70115 | Xcel Owned | 9674 246Y | CURRENT_TRANSFORMER | DANI | 1200 | 1200 | 1200 | 1200 | 239 | 239 | 239 | 239
DANI-HACA-115.0-1 | 9674 | DANIELS PARK 115 & 230KV SUBSTATION | XCEL | HAPPY CANYON SUBSTATION | XCEL | 70138 | 70115 | Xcel Owned | 9674 135Y | CURRENT_TRANSFORMER | DANI | 1200 | 1200 | 1200 | 1200 | 239 | 239 | 239 | 239
DANI-HACA-115.0-1 | 9674 | DANIELS PARK 115 & 230KV SUBSTATION | XCEL | HAPPY CANYON SUBSTATION | XCEL | 70138 | 70115 | Xcel Owned | 9674 246X | CURRENT_TRANSFORMER | DANI | 1200 | 1200 | 1200 | 1200 | 239 | 239 | 239 | 239
DANI-HACA-115.0-1 | 9674 | DANIELS PARK 115 & 230KV SUBSTATION | XCEL | HAPPY CANYON SUBSTATION | XCEL | 70138 | 70115 | Xcel Owned | 9674 | BREAKER | DANI | 1200 | 1200 | 1200 | 1200 | 239 | 239 | 239 | 239
DANI-HACA-115.0-1 | 9674 | DANIELS PARK 115 & 230KV SUBSTATION | XCEL | HAPPY CANYON SUBSTATION | XCEL | 70138 | 70115 | Xcel Owned | 9674 135X | CURRENT_TRANSFORMER | DANI | 1200 | 1200 | 1200 | 1200 | 239 | 239 | 239 | 239
DANI-HMIL-345.0-1 | 7153 | DANIELS PARK 115 & 230KV SUBSTATION | XCEL | HARVEST MILE | XCEL | 70601 | 70597 | Xcel Owned | DANI-HMIL-345.0-1 | FACILITY |  | 2716 | 2970 | 3000 | 3000 | 1623 | 1775 | 1793 | 1793
DANI-HMIL-345.0-1 | 7153 | DANIELS PARK 115 & 230KV SUBSTATION | XCEL | HARVEST MILE | XCEL | 70601 | 70597 | Xcel Owned | Narcissus | BUSBAR_SECTION | HMIL | 2716 | 2988 | 3096 | 3405 | 1623 | 1785 | 1850 | 2035
DANI-HMIL-345.0-1 | 7153 | DANIELS PARK 115 & 230KV SUBSTATION | XCEL | HARVEST MILE | XCEL | 70601 | 70597 | Xcel Owned |  | LINE_TRAP | DANI | 2970 | 2970 | 3136 | 3136 | 1775 | 1775 | 1874 | 1874
DANI-HMIL-345.0-1 | 7153 | DANIELS PARK 115 & 230KV SUBSTATION | XCEL | HARVEST MILE | XCEL | 70601 | 70597 | Xcel Owned |  | LINE_TRAP | HMIL | 2970 | 2970 | 3136 | 3136 | 1775 | 1775 | 1874 | 1874
DANI-HMIL-345.0-1 | 7153 | DANIELS PARK 115 & 230KV SUBSTATION | XCEL | HARVEST MILE | XCEL | 70601 | 70597 | Xcel Owned | 7153 | BREAKER | DANI | 3000 | 3000 | 3000 | 3000 | 1793 | 1793 | 1793 | 1793
DANI-HMIL-345.0-1 | 7153 | DANIELS PARK 115 & 230KV SUBSTATION | XCEL | HARVEST MILE | XCEL | 70601 | 70597 | Xcel Owned | 7036 | BREAKER | DANI | 3000 | 3000 | 3000 | 3000 | 1793 | 1793 | 1793 | 1793
DANI-HMIL-345.0-1 | 7153 | DANIELS PARK 115 & 230KV SUBSTATION | XCEL | HARVEST MILE | XCEL | 70601 | 70597 | Xcel Owned | 7153 | BREAKER | HMIL | 3000 | 3000 | 3000 | 3000 | 1793 | 1793 | 1793 | 1793
DANI-HMIL-345.0-1 | 7153 | DANIELS PARK 115 & 230KV SUBSTATION | XCEL | HARVEST MILE | XCEL | 70601 | 70597 | Xcel Owned | 7150 | BREAKER | HMIL | 3000 | 3000 | 3000 | 3000 | 1793 | 1793 | 1793 | 1793
DANI-JFUL-230.0-1 | 5119 | DANIELS PARK 115 & 230KV SUBSTATION | XCEL | JACKSON FULLER SUBSTATION | XCEL | 70139 | 73477 | Xcel Owned | DANI-JFUL-230.0-1 | FACILITY |  | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
DANI-JFUL-230.0-1 | 5119 | DANIELS PARK 115 & 230KV SUBSTATION | XCEL | JACKSON FULLER SUBSTATION | XCEL | 70139 | 73477 | Xcel Owned | 5102 135Y | CURRENT_TRANSFORMER | DANI | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
DANI-JFUL-230.0-1 | 5119 | DANIELS PARK 115 & 230KV SUBSTATION | XCEL | JACKSON FULLER SUBSTATION | XCEL | 70139 | 73477 | Xcel Owned | 5119 246X | CURRENT_TRANSFORMER | DANI | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
DANI-JFUL-230.0-1 | 5119 | DANIELS PARK 115 & 230KV SUBSTATION | XCEL | JACKSON FULLER SUBSTATION | XCEL | 70139 | 73477 | Xcel Owned | 5119 135Y | CURRENT_TRANSFORMER | DANI | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
DANI-JFUL-230.0-1 | 5119 | DANIELS PARK 115 & 230KV SUBSTATION | XCEL | JACKSON FULLER SUBSTATION | XCEL | 70139 | 73477 | Xcel Owned | 5102 246Y | CURRENT_TRANSFORMER | DANI | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
DANI-JFUL-230.0-1 | 5119 | DANIELS PARK 115 & 230KV SUBSTATION | XCEL | JACKSON FULLER SUBSTATION | XCEL | 70139 | 73477 | Xcel Owned | 5102 246X | CURRENT_TRANSFORMER | DANI | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
DANI-JFUL-230.0-1 | 5119 | DANIELS PARK 115 & 230KV SUBSTATION | XCEL | JACKSON FULLER SUBSTATION | XCEL | 70139 | 73477 | Xcel Owned | 5102 135X | CURRENT_TRANSFORMER | DANI | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
DANI-JFUL-230.0-1 | 5119 | DANIELS PARK 115 & 230KV SUBSTATION | XCEL | JACKSON FULLER SUBSTATION | XCEL | 70139 | 73477 | Xcel Owned | 5119 246Y | CURRENT_TRANSFORMER | DANI | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
DANI-JFUL-230.0-1 | 5119 | DANIELS PARK 115 & 230KV SUBSTATION | XCEL | JACKSON FULLER SUBSTATION | XCEL | 70139 | 73477 | Xcel Owned | 5119 135X | CURRENT_TRANSFORMER | DANI | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
DANI-JFUL-230.0-1 | 5119 | DANIELS PARK 115 & 230KV SUBSTATION | XCEL | JACKSON FULLER SUBSTATION | XCEL | 70139 | 73477 | Xcel Owned | 5102N | SWITCH | DANI | 1200 | 1549 | 1486 | 1780 | 478 | 617 | 592 | 709
DANI-JFUL-230.0-1 | 5119 | DANIELS PARK 115 & 230KV SUBSTATION | XCEL | JACKSON FULLER SUBSTATION | XCEL | 70139 | 73477 | Xcel Owned | 5102S | SWITCH | DANI | 1200 | 1549 | 1486 | 1780 | 478 | 617 | 592 | 709
DANI-JFUL-230.0-1 | 5119 | DANIELS PARK 115 & 230KV SUBSTATION | XCEL | JACKSON FULLER SUBSTATION | XCEL | 70139 | 73477 | Xcel Owned | 5119N | SWITCH | DANI | 1200 | 1549 | 1486 | 1780 | 478 | 617 | 592 | 709
DANI-MARC-230.0-1 | 5085 | DANIELS PARK 115 & 230KV SUBSTATION | XCEL | MARCY SUBSTATION | XCEL | 70139 | 70278 | Xcel Owned | DANI-MARC-230.0-1 | FACILITY |  | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
DANI-MARC-230.0-1 | 5085 | DANIELS PARK 115 & 230KV SUBSTATION | XCEL | MARCY SUBSTATION | XCEL | 70139 | 70278 | Xcel Owned | 5102 135Y | CURRENT_TRANSFORMER | DANI | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
DANI-MARC-230.0-1 | 5085 | DANIELS PARK 115 & 230KV SUBSTATION | XCEL | MARCY SUBSTATION | XCEL | 70139 | 70278 | Xcel Owned | 5085 135X | CURRENT_TRANSFORMER | DANI | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
DANI-MARC-230.0-1 | 5085 | DANIELS PARK 115 & 230KV SUBSTATION | XCEL | MARCY SUBSTATION | XCEL | 70139 | 70278 | Xcel Owned | 5102 135X | CURRENT_TRANSFORMER | DANI | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
DANI-MARC-230.0-1 | 5085 | DANIELS PARK 115 & 230KV SUBSTATION | XCEL | MARCY SUBSTATION | XCEL | 70139 | 70278 | Xcel Owned | 5085 21Z1/2-B | SECONDARY_CURRENT_LIMITATION | DANI | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
DANI-MARC-230.0-1 | 5085 | DANIELS PARK 115 & 230KV SUBSTATION | XCEL | MARCY SUBSTATION | XCEL | 70139 | 70278 | Xcel Owned | 5085 GRD DIR 67GS | SECONDARY_CURRENT_LIMITATION | DANI | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
DANI-MARC-230.0-1 | 5085 | DANIELS PARK 115 & 230KV SUBSTATION | XCEL | MARCY SUBSTATION | XCEL | 70139 | 70278 | Xcel Owned | 5085 246X | CURRENT_TRANSFORMER | DANI | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
DANI-MARC-230.0-1 | 5085 | DANIELS PARK 115 & 230KV SUBSTATION | XCEL | MARCY SUBSTATION | XCEL | 70139 | 70278 | Xcel Owned | 5085 135Y | CURRENT_TRANSFORMER | DANI | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
DANI-MARC-230.0-1 | 5085 | DANIELS PARK 115 & 230KV SUBSTATION | XCEL | MARCY SUBSTATION | XCEL | 70139 | 70278 | Xcel Owned | 5102 246Y | CURRENT_TRANSFORMER | DANI | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
DANI-MARC-230.0-1 | 5085 | DANIELS PARK 115 & 230KV SUBSTATION | XCEL | MARCY SUBSTATION | XCEL | 70139 | 70278 | Xcel Owned | 5085 21Z1/2-A | SECONDARY_CURRENT_LIMITATION | DANI | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
DANI-MARC-230.0-1 | 5085 | DANIELS PARK 115 & 230KV SUBSTATION | XCEL | MARCY SUBSTATION | XCEL | 70139 | 70278 | Xcel Owned | 5102 246X | CURRENT_TRANSFORMER | DANI | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
DANI-MARC-230.0-1 | 5085 | DANIELS PARK 115 & 230KV SUBSTATION | XCEL | MARCY SUBSTATION | XCEL | 70139 | 70278 | Xcel Owned | 5085 21Z1/2-C | SECONDARY_CURRENT_LIMITATION | DANI | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
DANI-MARC-230.0-1 | 5085 | DANIELS PARK 115 & 230KV SUBSTATION | XCEL | MARCY SUBSTATION | XCEL | 70139 | 70278 | Xcel Owned | 5085 GRD DIR 67GP | SECONDARY_CURRENT_LIMITATION | DANI | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
DANI-MARC-230.0-1 | 5085 | DANIELS PARK 115 & 230KV SUBSTATION | XCEL | MARCY SUBSTATION | XCEL | 70139 | 70278 | Xcel Owned | 5085 21ZP | SECONDARY_CURRENT_LIMITATION | DANI | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
DANI-MARC-230.0-1 | 5085 | DANIELS PARK 115 & 230KV SUBSTATION | XCEL | MARCY SUBSTATION | XCEL | 70139 | 70278 | Xcel Owned | 5085 246Y | CURRENT_TRANSFORMER | DANI | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
DANI-MARC-230.0-1 | 5085 | DANIELS PARK 115 & 230KV SUBSTATION | XCEL | MARCY SUBSTATION | XCEL | 70139 | 70278 | Xcel Owned | 5102N | SWITCH | DANI | 1200 | 1549 | 1486 | 1780 | 478 | 617 | 592 | 709
DANI-MARC-230.0-1 | 5085 | DANIELS PARK 115 & 230KV SUBSTATION | XCEL | MARCY SUBSTATION | XCEL | 70139 | 70278 | Xcel Owned | 5102S | SWITCH | DANI | 1200 | 1549 | 1486 | 1780 | 478 | 617 | 592 | 709
DANI-MARC-230.0-1 | 5085 | DANIELS PARK 115 & 230KV SUBSTATION | XCEL | MARCY SUBSTATION | XCEL | 70139 | 70278 | Xcel Owned | 5085S | SWITCH | DANI | 1200 | 1549 | 1486 | 1780 | 478 | 617 | 592 | 709
DANI-MARC-230.0-1 | 5085 | DANIELS PARK 115 & 230KV SUBSTATION | XCEL | MARCY SUBSTATION | XCEL | 70139 | 70278 | Xcel Owned | 5085N | SWITCH | DANI | 1200 | 1549 | 1486 | 1780 | 478 | 617 | 592 | 709
DANI-MSST-230.0-1 | 5113 | DANIELS PARK 115 & 230KV SUBSTATION | XCEL | MISSILE SITE | XCEL | 70139 | 70623 | Xcel Owned | DANI-MSST-230.0-1 | FACILITY |  | 1854 | 1980 | 2091 | 2091 | 739 | 789 | 833 | 833
DANI-MSST-230.0-1 | 5113 | DANIELS PARK 115 & 230KV SUBSTATION | XCEL | MISSILE SITE | XCEL | 70139 | 70623 | Xcel Owned | DANI-MSST-230.0-1 | Transmission Line | 5113 | 1854 | 2039 | 2101 | 2311 | 739 | 812 | 837 | 921
DANI-MSST-230.0-1 | 5113 | DANIELS PARK 115 & 230KV SUBSTATION | XCEL | MISSILE SITE | XCEL | 70139 | 70623 | Xcel Owned |  | LINE_TRAP | DANI | 1980 | 1980 | 2091 | 2091 | 789 | 789 | 833 | 833
DANI-MSST-230.0-1 | 5113 | DANIELS PARK 115 & 230KV SUBSTATION | XCEL | MISSILE SITE | XCEL | 70139 | 70623 | Xcel Owned |  | LINE_TRAP | MSST | 1980 | 1980 | 2091 | 2091 | 789 | 789 | 833 | 833
DANI-MSST-345.0-1 | 7109 | DANIELS PARK 115 & 230KV SUBSTATION | XCEL | MISSILE SITE | XCEL | 70601 | 70624 | Xcel Owned | DANI-MSST-345.0-1 | FACILITY |  | 2425 | 2838 | 2897 | 3000 | 1449 | 1696 | 1731 | 1793
DANI-MSST-345.0-1 | 7109 | DANIELS PARK 115 & 230KV SUBSTATION | XCEL | MISSILE SITE | XCEL | 70601 | 70624 | Xcel Owned | Narcissus | BUSBAR_SECTION | MSST | 2425 | 2838 | 2897 | 3233 | 1449 | 1696 | 1731 | 1932
DANI-MSST-345.0-1 | 7109 | DANIELS PARK 115 & 230KV SUBSTATION | XCEL | MISSILE SITE | XCEL | 70601 | 70624 | Xcel Owned | 7109 | BREAKER | MSST | 3000 | 3000 | 3000 | 3000 | 1793 | 1793 | 1793 | 1793
DANI-MSST-345.0-1 | 7109 | DANIELS PARK 115 & 230KV SUBSTATION | XCEL | MISSILE SITE | XCEL | 70601 | 70624 | Xcel Owned | 7038 | BREAKER | DANI | 3000 | 3000 | 3000 | 3000 | 1793 | 1793 | 1793 | 1793
DANI-MSST-345.0-1 | 7109 | DANIELS PARK 115 & 230KV SUBSTATION | XCEL | MISSILE SITE | XCEL | 70601 | 70624 | Xcel Owned | 7108 | BREAKER | MSST | 3000 | 3000 | 3000 | 3000 | 1793 | 1793 | 1793 | 1793
DANI-MSST-345.0-1 | 7109 | DANIELS PARK 115 & 230KV SUBSTATION | XCEL | MISSILE SITE | XCEL | 70601 | 70624 | Xcel Owned | 7109 | BREAKER | DANI | 3000 | 3000 | 3000 | 3000 | 1793 | 1793 | 1793 | 1793
DANI-PRAI-230.0-1 | 5111 | DANIELS PARK 115 & 230KV SUBSTATION | XCEL | PRAIRIE SUBSTATION | XCEL | 70139 | 70323 | Xcel Owned | DANI-PRAI-230.0-1 | FACILITY |  | 1434 | 1578 | 1600 | 1600 | 571 | 629 | 637 | 637
DANI-PRAI-230.0-1 | 5111 | DANIELS PARK 115 & 230KV SUBSTATION | XCEL | PRAIRIE SUBSTATION | XCEL | 70139 | 70323 | Xcel Owned | DANI-PRAI-230.0-1 | Transmission Line | 5111 | 1434 | 1578 | 1629 | 1792 | 571 | 629 | 649 | 714
DANI-PRAI-230.0-1 | 5111 | DANIELS PARK 115 & 230KV SUBSTATION | XCEL | PRAIRIE SUBSTATION | XCEL | 70139 | 70323 | Xcel Owned | 5111-1 | CIRCUIT_SWITCHER | PRAI | 1600 | 1600 | 1600 | 1600 | 637 | 637 | 637 | 637
DANI-PRAI-230.0-2 | 5707 | DANIELS PARK 115 & 230KV SUBSTATION | XCEL | PRAIRIE SUBSTATION | XCEL | 70139 | 70331 | Xcel Owned | DANI-PRAI-230.0-2 | FACILITY |  | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
DANI-PRAI-230.0-2 | 5707 | DANIELS PARK 115 & 230KV SUBSTATION | XCEL | PRAIRIE SUBSTATION | XCEL | 70139 | 70331 | Xcel Owned | 5106 135Y | CURRENT_TRANSFORMER | DANI | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
DANI-PRAI-230.0-2 | 5707 | DANIELS PARK 115 & 230KV SUBSTATION | XCEL | PRAIRIE SUBSTATION | XCEL | 70139 | 70331 | Xcel Owned | 5106 246Y | CURRENT_TRANSFORMER | DANI | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
DANI-PRAI-230.0-2 | 5707 | DANIELS PARK 115 & 230KV SUBSTATION | XCEL | PRAIRIE SUBSTATION | XCEL | 70139 | 70331 | Xcel Owned | 5106 135X | CURRENT_TRANSFORMER | DANI | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
DANI-PRAI-230.0-2 | 5707 | DANIELS PARK 115 & 230KV SUBSTATION | XCEL | PRAIRIE SUBSTATION | XCEL | 70139 | 70331 | Xcel Owned | 5106 246X | CURRENT_TRANSFORMER | DANI | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
DANI-PRAI-230.0-2 | 5707 | DANIELS PARK 115 & 230KV SUBSTATION | XCEL | PRAIRIE SUBSTATION | XCEL | 70139 | 70331 | Xcel Owned | 5707S | SWITCH | DANI | 1200 | 1549 | 1486 | 1780 | 478 | 617 | 592 | 709
DANI-PRAI-230.0-2 | 5707 | DANIELS PARK 115 & 230KV SUBSTATION | XCEL | PRAIRIE SUBSTATION | XCEL | 70139 | 70331 | Xcel Owned | 5707N | SWITCH | DANI | 1200 | 1549 | 1486 | 1780 | 478 | 617 | 592 | 709
DANI-PRAI-230.0-2 | 5707 | DANIELS PARK 115 & 230KV SUBSTATION | XCEL | PRAIRIE SUBSTATION | XCEL | 70139 | 70331 | Xcel Owned | 5106S | SWITCH | DANI | 1200 | 1549 | 1486 | 1780 | 478 | 617 | 592 | 709
DANI-PRAI-230.0-2 | 5707 | DANIELS PARK 115 & 230KV SUBSTATION | XCEL | PRAIRIE SUBSTATION | XCEL | 70139 | 70331 | Xcel Owned | 5106N | SWITCH | DANI | 1200 | 1549 | 1486 | 1780 | 478 | 617 | 592 | 709
DANI-PRAI-230.0-2 | 5707 | DANIELS PARK 115 & 230KV SUBSTATION | XCEL | PRAIRIE SUBSTATION | XCEL | 70139 | 70331 | Xcel Owned | 5117S | SWITCH | DANI | 1200 | 1549 | 1486 | 1780 | 478 | 617 | 592 | 709
DANI-PRAI-230.0-2 | 5707 | DANIELS PARK 115 & 230KV SUBSTATION | XCEL | PRAIRIE SUBSTATION | XCEL | 70139 | 70331 | Xcel Owned | 5117N | SWITCH | DANI | 1200 | 1549 | 1486 | 1780 | 478 | 617 | 592 | 709
DANI-SANT-230.0-1 | 5107 | DANIELS PARK 115 & 230KV SUBSTATION | XCEL | SANTA FE SUBSTATION | XCEL | 70139 | 70527 | Xcel Owned | DANI-SANT-230.0-1 | FACILITY |  | 1261 | 1387 | 1430 | 1573 | 502 | 553 | 570 | 627
DANI-SANT-230.0-1 | 5107 | DANIELS PARK 115 & 230KV SUBSTATION | XCEL | SANTA FE SUBSTATION | XCEL | 70139 | 70527 | Xcel Owned | DANI-SANT-230.0-1 | Transmission Line | 5107 | 1261 | 1387 | 1430 | 1573 | 502 | 553 | 570 | 627
DANI-SRDG-230.0-1 | 5115 | DANIELS PARK 115 & 230KV SUBSTATION | XCEL | SURREY RIDGE | XCEL | 70139 | 70284 | Xcel Owned | DANI-SRDG-230.0-1 | FACILITY |  | 1849 | 2000 | 2000 | 2000 | 737 | 797 | 797 | 797
DANI-SRDG-230.0-1 | 5115 | DANIELS PARK 115 & 230KV SUBSTATION | XCEL | SURREY RIDGE | XCEL | 70139 | 70284 | Xcel Owned | Narcissus | BUSBAR_SECTION | DANI | 1849 | 2034 | 2086 | 2294 | 737 | 810 | 831 | 914
DANI-SRDG-230.0-1 | 5115 | DANIELS PARK 115 & 230KV SUBSTATION | XCEL | SURREY RIDGE | XCEL | 70139 | 70284 | Xcel Owned | 5115-4 | CIRCUIT_SWITCHER | SRDG | 2000 | 2000 | 2000 | 2000 | 797 | 797 | 797 | 797
DANI-TUND-345.0-1 | 7235 | DANIELS PARK 115 & 230KV SUBSTATION | XCEL | TUNDRA SUBSTATION | XCEL | 70601 | 70653 | Xcel Owned | DANI-TUND-345.0-1 | FACILITY |  | 1980 | 1980 | 2091 | 2091 | 1183 | 1183 | 1249 | 1249
DANI-TUND-345.0-1 | 7235 | DANIELS PARK 115 & 230KV SUBSTATION | XCEL | TUNDRA SUBSTATION | XCEL | 70601 | 70653 | Xcel Owned |  | LINE_TRAP | DANI | 1980 | 1980 | 2091 | 2091 | 1183 | 1183 | 1249 | 1249
DANI-WATE-230.0-1 | 5109 | DANIELS PARK 115 & 230KV SUBSTATION | XCEL | WATERTON SUBSTATION | XCEL | 70139 | 70464 | Xcel Owned | DANI-WATE-230.0-1 | FACILITY |  | 1409 | 1550 | 1607 | 1673 | 561 | 618 | 640 | 666
DANI-WATE-230.0-1 | 5109 | DANIELS PARK 115 & 230KV SUBSTATION | XCEL | WATERTON SUBSTATION | XCEL | 70139 | 70464 | Xcel Owned | Narcissus | BUSBAR_SECTION | DANI | 1409 | 1550 | 1607 | 1768 | 561 | 618 | 640 | 704
DANI-WATE-230.0-1 | 5109 | DANIELS PARK 115 & 230KV SUBSTATION | XCEL | WATERTON SUBSTATION | XCEL | 70139 | 70464 | Xcel Owned |  | LINE_TRAP | DANI | 1584 | 1584 | 1673 | 1673 | 631 | 631 | 666 | 666
DEER-MART_TP-115.0-1 | 9337 | DEER CREEK SUBSTATION | XCEL | MARTIN TAP | XCEL | 70142 | 70484 | Xcel Owned | DEER-MART_TP-115.0-1 | FACILITY |  | 1200 | 1200 | 1200 | 1200 | 239 | 239 | 239 | 239
DEER-MART_TP-115.0-1 | 9337 | DEER CREEK SUBSTATION | XCEL | MARTIN TAP | XCEL | 70142 | 70484 | Xcel Owned | 9337-3 | CIRCUIT_SWITCHER | DEER | 1200 | 1200 | 1200 | 1200 | 239 | 239 | 239 | 239
DEER-MART_TP-115.0-1 | 9337 | DEER CREEK SUBSTATION | XCEL | MARTIN TAP | XCEL | 70142 | 70484 | Xcel Owned | 8160 | SWITCH | DEER | 1200 | 1549 | 1486 | 1780 | 239 | 309 | 296 | 355
DEER-SODA-115.0-1 | 9337 | DEER CREEK SUBSTATION | XCEL | SODA LAKES SUBSTATION | XCEL | 70142 | 70400 | Xcel Owned | DEER-SODA-115.0-1 | FACILITY |  | 600 | 775 | 743 | 800 | 120 | 154 | 148 | 159
DEER-SODA-115.0-1 | 9337 | DEER CREEK SUBSTATION | XCEL | SODA LAKES SUBSTATION | XCEL | 70142 | 70400 | Xcel Owned | 9337L | SWITCH | SODA | 600 | 775 | 743 | 890 | 120 | 154 | 148 | 177
DEER-SODA-115.0-1 | 9337 | DEER CREEK SUBSTATION | XCEL | SODA LAKES SUBSTATION | XCEL | 70142 | 70400 | Xcel Owned | 9337_246Y_21Z1/2/3-C | SECONDARY_CURRENT_LIMITATION | SODA | 800 | 800 | 800 | 800 | 159 | 159 | 159 | 159
DEER-SODA-115.0-1 | 9337 | DEER CREEK SUBSTATION | XCEL | SODA LAKES SUBSTATION | XCEL | 70142 | 70400 | Xcel Owned | 9337_246Y_21Z1/2/3-B | SECONDARY_CURRENT_LIMITATION | SODA | 800 | 800 | 800 | 800 | 159 | 159 | 159 | 159
DEER-SODA-115.0-1 | 9337 | DEER CREEK SUBSTATION | XCEL | SODA LAKES SUBSTATION | XCEL | 70142 | 70400 | Xcel Owned | 9337_246Y_21Z1/2/3-A | SECONDARY_CURRENT_LIMITATION | SODA | 800 | 800 | 800 | 800 | 159 | 159 | 159 | 159
DERB_TP-ARSE-115.0-1 | 9543 | DERBY TAP | XCEL | ARSENAL | XCEL | 70153 | 70040 | Xcel Owned | DERB_TP-ARSE-115.0-1 | FACILITY |  | 799 | 879 | 909 | 999 | 159 | 175 | 181 | 199
DERB_TP-ARSE-115.0-1 | 9543 | DERBY TAP | XCEL | ARSENAL | XCEL | 70153 | 70040 | Xcel Owned | Hawk | BUSBAR_SECTION | ARSE | 799 | 879 | 909 | 999 | 159 | 175 | 181 | 199
DERB_TP-ARSE-115.0-1 | 9543 | DERBY TAP | XCEL | ARSENAL | XCEL | 70153 | 70040 | Xcel Owned | DERB_TP-ARSE-115.0-1 | Transmission Line | 9543 | 799 | 879 | 909 | 999 | 159 | 175 | 181 | 199
DERB-HAVA-115.0-1 | 9544 | DERBY SUBSTATION | XCEL | HAVANA SUBSTATION | XCEL | 70154 | 70216 | Xcel Owned | DERB-HAVA-115.0-1 | FACILITY |  | 799 | 879 | 909 | 999 | 159 | 175 | 181 | 199
DERB-HAVA-115.0-1 | 9544 | DERBY SUBSTATION | XCEL | HAVANA SUBSTATION | XCEL | 70154 | 70216 | Xcel Owned | DERB-HAVA-115.0-1 | Transmission Line | 9544 | 799 | 879 | 909 | 999 | 159 | 175 | 181 | 199
DILL-PTAR-230.0-1 | 5359 | DILLON SUBSTATION | XCEL | PTARMIGAN | XCEL | 70156 | 70057 | Xcel Owned | DILL-PTAR-230.0-1 | FACILITY |  | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
DILL-PTAR-230.0-1 | 5359 | DILLON SUBSTATION | XCEL | PTARMIGAN | XCEL | 70156 | 70057 | Xcel Owned | 5352 246Y | CURRENT_TRANSFORMER | DILL | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
DILL-PTAR-230.0-1 | 5359 | DILLON SUBSTATION | XCEL | PTARMIGAN | XCEL | 70156 | 70057 | Xcel Owned | 5352 135Y | CURRENT_TRANSFORMER | DILL | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
DILL-PTAR-230.0-1 | 5359 | DILLON SUBSTATION | XCEL | PTARMIGAN | XCEL | 70156 | 70057 | Xcel Owned | 5359 246X | CURRENT_TRANSFORMER | DILL | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
DILL-PTAR-230.0-1 | 5359 | DILLON SUBSTATION | XCEL | PTARMIGAN | XCEL | 70156 | 70057 | Xcel Owned | 5352_135Y_50/62BF | SECONDARY_CURRENT_LIMITATION | DILL | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
DILL-SUMM-115.0-1 | 8189 | DILLON SUBSTATION | XCEL | SUMMIT SUBSTATION | XCEL | 70155 | 70421 | Xcel Owned | DILL-SUMM-115.0-1 | FACILITY |  | 440 | 484 | 481 | 529 | 88 | 96 | 96 | 105
DILL-SUMM-115.0-1 | 8189 | DILLON SUBSTATION | XCEL | SUMMIT SUBSTATION | XCEL | 70155 | 70421 | Xcel Owned | DILL-SUMM-115.0-1 | Transmission Line | 8189 | 440 | 484 | 481 | 529 | 88 | 96 | 96 | 105
DIVI-LKGE-115.0-1 | 8384 | DIVIDE SUBSTATION | XCEL | LAKE GEORGE | XCEL | 70157 | 70419 | Xcel Owned | DIVI-LKGE-115.0-1 | FACILITY |  | 1060 | 1166 | 1200 | 1200 | 211 | 232 | 239 | 239
DIVI-LKGE-115.0-1 | 8384 | DIVIDE SUBSTATION | XCEL | LAKE GEORGE | XCEL | 70157 | 70419 | Xcel Owned | Drake | BUSBAR_SECTION | DIVI | 1060 | 1166 | 1210 | 1331 | 211 | 232 | 241 | 265
DIVI-LKGE-115.0-1 | 8384 | DIVIDE SUBSTATION | XCEL | LAKE GEORGE | XCEL | 70157 | 70419 | Xcel Owned | 8384_246Y_A_XDCR | SECONDARY_CURRENT_LIMITATION | DIVI | 1200 | 1200 | 1200 | 1200 | 239 | 239 | 239 | 239
DIVI-LKGE-115.0-1 | 8384 | DIVIDE SUBSTATION | XCEL | LAKE GEORGE | XCEL | 70157 | 70419 | Xcel Owned | 8384N | CIRCUIT_SWITCHER | DIVI | 1200 | 1200 | 1200 | 1200 | 239 | 239 | 239 | 239
DIVI-LKGE-115.0-1 | 8384 | DIVIDE SUBSTATION | XCEL | LAKE GEORGE | XCEL | 70157 | 70419 | Xcel Owned | 8459 | BREAKER | DIVI | 1200 | 1200 | 1200 | 1200 | 239 | 239 | 239 | 239
DIVI-LKGE-115.0-1 | 8384 | DIVIDE SUBSTATION | XCEL | LAKE GEORGE | XCEL | 70157 | 70419 | Xcel Owned | 8384 | BREAKER | DIVI | 1200 | 1200 | 1200 | 1200 | 239 | 239 | 239 | 239
DIVI-LKGE-115.0-1 | 8384 | DIVIDE SUBSTATION | XCEL | LAKE GEORGE | XCEL | 70157 | 70419 | Xcel Owned | 8384_246Y_W/VAR_XDCR | SECONDARY_CURRENT_LIMITATION | DIVI | 1200 | 1200 | 1200 | 1200 | 239 | 239 | 239 | 239
DTER-ELAT-230.0-1 | 5625 | DENVER TERMINAL SUBSTATION | XCEL | ELATI SUBSTATION | XCEL | 70149 | 70163 | Xcel Owned | DTER-ELAT-230.0-1 | FACILITY |  | 770 | 1105 | 770 | 1105 | 307 | 440 | 307 | 440
DTER-ELAT-230.0-1 | 5625 | DENVER TERMINAL SUBSTATION | XCEL | ELATI SUBSTATION | XCEL | 70149 | 70163 | Xcel Owned | DTER-ELAT-230.0-1 | Transmission Line | 5625 | 770 | 1105 | 770 | 1105 | 307 | 440 | 307 | 440
DTER-FEDC_TP-115.0-1 | 9122 | DENVER TERMINAL SUBSTATION | XCEL | FEDERAL CENTER TAP | XCEL | 70144 | 70173 | Xcel Owned | DTER-FEDC_TP-115.0-1 | FACILITY |  | 1200 | 1200 | 1200 | 1200 | 239 | 239 | 239 | 239
DTER-FEDC_TP-115.0-1 | 9122 | DENVER TERMINAL SUBSTATION | XCEL | FEDERAL CENTER TAP | XCEL | 70144 | 70173 | Xcel Owned | 9122 246Y 21Z1 | SECONDARY_CURRENT_LIMITATION | DTER | 1200 | 1200 | 1200 | 1200 | 239 | 239 | 239 | 239
DTER-FEDC_TP-115.0-1 | 9122 | DENVER TERMINAL SUBSTATION | XCEL | FEDERAL CENTER TAP | XCEL | 70144 | 70173 | Xcel Owned | 9122 246Y 21Z2 | SECONDARY_CURRENT_LIMITATION | DTER | 1200 | 1200 | 1200 | 1200 | 239 | 239 | 239 | 239
DTER-FEDC_TP-115.0-1 | 9122 | DENVER TERMINAL SUBSTATION | XCEL | FEDERAL CENTER TAP | XCEL | 70144 | 70173 | Xcel Owned | 9122 246X 67GP | SECONDARY_CURRENT_LIMITATION | DTER | 1200 | 1200 | 1200 | 1200 | 239 | 239 | 239 | 239
DTER-FEDC_TP-115.0-1 | 9122 | DENVER TERMINAL SUBSTATION | XCEL | FEDERAL CENTER TAP | XCEL | 70144 | 70173 | Xcel Owned | 9122 246X 21ZP | SECONDARY_CURRENT_LIMITATION | DTER | 1200 | 1200 | 1200 | 1200 | 239 | 239 | 239 | 239
DTER-FEDC_TP-115.0-1 | 9122 | DENVER TERMINAL SUBSTATION | XCEL | FEDERAL CENTER TAP | XCEL | 70144 | 70173 | Xcel Owned | DTER-FEDC_TP-115.0-1 | Transmission Line | 9122 | 1200 | 1392 | 1442 | 1586 | 239 | 277 | 287 | 316
DTER-FEDC_TP-115.0-1 | 9122 | DENVER TERMINAL SUBSTATION | XCEL | FEDERAL CENTER TAP | XCEL | 70144 | 70173 | Xcel Owned | Curlew | BUSBAR_SECTION | DTER | 1200 | 1392 | 1442 | 1586 | 239 | 277 | 287 | 316
DTER-FEDC_TP-115.0-1 | 9122 | DENVER TERMINAL SUBSTATION | XCEL | FEDERAL CENTER TAP | XCEL | 70144 | 70173 | Xcel Owned | 9122M | SWITCH | DTER | 1200 | 1549 | 1486 | 1780 | 239 | 309 | 296 | 355
DTER-FEDC_TP-115.0-1 | 9122 | DENVER TERMINAL SUBSTATION | XCEL | FEDERAL CENTER TAP | XCEL | 70144 | 70173 | Xcel Owned | 9122L | SWITCH | DTER | 1200 | 1549 | 1486 | 1780 | 239 | 309 | 296 | 355
DTER-GRAY-115.0-1 | 9008 | DENVER TERMINAL SUBSTATION | XCEL | GRAY STREET SUBSTATION | XCEL | 70148 | 70208 | Xcel Owned | DTER-GRAY-115.0-1 | FACILITY |  | 1200 | 1200 | 1200 | 1200 | 239 | 239 | 239 | 239
DTER-GRAY-115.0-1 | 9008 | DENVER TERMINAL SUBSTATION | XCEL | GRAY STREET SUBSTATION | XCEL | 70148 | 70208 | Xcel Owned | 9008_246Y_METER_AMPSW | SECONDARY_CURRENT_LIMITATION | GRAY | 1200 | 1200 | 1200 | 1200 | 239 | 239 | 239 | 239
DTER-GRAY-115.0-1 | 9008 | DENVER TERMINAL SUBSTATION | XCEL | GRAY STREET SUBSTATION | XCEL | 70148 | 70208 | Xcel Owned | 9008 135X | CURRENT_TRANSFORMER | DTER | 1200 | 1200 | 1200 | 1200 | 239 | 239 | 239 | 239
DTER-GRAY-115.0-1 | 9008 | DENVER TERMINAL SUBSTATION | XCEL | GRAY STREET SUBSTATION | XCEL | 70148 | 70208 | Xcel Owned | 9008 135Y | CURRENT_TRANSFORMER | DTER | 1200 | 1200 | 1200 | 1200 | 239 | 239 | 239 | 239
DTER-GRAY-115.0-1 | 9008 | DENVER TERMINAL SUBSTATION | XCEL | GRAY STREET SUBSTATION | XCEL | 70148 | 70208 | Xcel Owned | 9008_246Y_METER_VAR | SECONDARY_CURRENT_LIMITATION | GRAY | 1200 | 1200 | 1200 | 1200 | 239 | 239 | 239 | 239
DTER-GRAY-115.0-1 | 9008 | DENVER TERMINAL SUBSTATION | XCEL | GRAY STREET SUBSTATION | XCEL | 70148 | 70208 | Xcel Owned | 9008 135Y 21Z1/2 | SECONDARY_CURRENT_LIMITATION | DTER | 1200 | 1200 | 1200 | 1200 | 239 | 239 | 239 | 239
DTER-GRAY-115.0-1 | 9008 | DENVER TERMINAL SUBSTATION | XCEL | GRAY STREET SUBSTATION | XCEL | 70148 | 70208 | Xcel Owned | 9008 246Y | CURRENT_TRANSFORMER | DTER | 1200 | 1200 | 1200 | 1200 | 239 | 239 | 239 | 239
DTER-GRAY-115.0-1 | 9008 | DENVER TERMINAL SUBSTATION | XCEL | GRAY STREET SUBSTATION | XCEL | 70148 | 70208 | Xcel Owned | 9008 246X | CURRENT_TRANSFORMER | DTER | 1200 | 1200 | 1200 | 1200 | 239 | 239 | 239 | 239
DTER-GRAY-115.0-1 | 9008 | DENVER TERMINAL SUBSTATION | XCEL | GRAY STREET SUBSTATION | XCEL | 70148 | 70208 | Xcel Owned | 9008_135Y_67GS | SECONDARY_CURRENT_LIMITATION | GRAY | 1200 | 1200 | 1200 | 1200 | 239 | 239 | 239 | 239
DTER-GRAY-115.0-1 | 9008 | DENVER TERMINAL SUBSTATION | XCEL | GRAY STREET SUBSTATION | XCEL | 70148 | 70208 | Xcel Owned | 9008_246Y_METER_W | SECONDARY_CURRENT_LIMITATION | GRAY | 1200 | 1200 | 1200 | 1200 | 239 | 239 | 239 | 239
DTER-GRAY-115.0-1 | 9008 | DENVER TERMINAL SUBSTATION | XCEL | GRAY STREET SUBSTATION | XCEL | 70148 | 70208 | Xcel Owned | 9008_246Y_XDCR_VAR | SECONDARY_CURRENT_LIMITATION | GRAY | 1200 | 1200 | 1200 | 1200 | 239 | 239 | 239 | 239
DTER-GRAY-115.0-1 | 9008 | DENVER TERMINAL SUBSTATION | XCEL | GRAY STREET SUBSTATION | XCEL | 70148 | 70208 | Xcel Owned | 9008_246Y_XDCR_W | SECONDARY_CURRENT_LIMITATION | GRAY | 1200 | 1200 | 1200 | 1200 | 239 | 239 | 239 | 239
DTER-GRAY-115.0-1 | 9008 | DENVER TERMINAL SUBSTATION | XCEL | GRAY STREET SUBSTATION | XCEL | 70148 | 70208 | Xcel Owned | 9008L | SWITCH | GRAY | 1200 | 1549 | 1486 | 1780 | 239 | 309 | 296 | 355
DTER-GRAY-115.0-1 | 9008 | DENVER TERMINAL SUBSTATION | XCEL | GRAY STREET SUBSTATION | XCEL | 70148 | 70208 | Xcel Owned | 9008M | SWITCH | GRAY | 1200 | 1549 | 1486 | 1780 | 239 | 309 | 296 | 355
DTER-GRAY-115.0-1 | 9008 | DENVER TERMINAL SUBSTATION | XCEL | GRAY STREET SUBSTATION | XCEL | 70148 | 70208 | Xcel Owned | 9008M | SWITCH | DTER | 1200 | 1549 | 1486 | 1780 | 239 | 309 | 296 | 355
DTER-LACO-230.0-1 | 5627 | DENVER TERMINAL SUBSTATION | XCEL | LACOMBE SUBSTATION | XCEL | 70149 | 70324 | Xcel Owned | DTER-LACO-230.0-1 | FACILITY |  | 1220 | 1427 | 1457 | 1626 | 486 | 568 | 580 | 648
DTER-LACO-230.0-1 | 5627 | DENVER TERMINAL SUBSTATION | XCEL | LACOMBE SUBSTATION | XCEL | 70149 | 70324 | Xcel Owned | Narcissus | BUSBAR_SECTION | DTER | 1220 | 1427 | 1457 | 1626 | 486 | 568 | 580 | 648
DTER-WEST-230.0-1 | 5629 | DENVER TERMINAL SUBSTATION | XCEL | WEST SUBSTATION | XCEL | 70149 | 70480 | Xcel Owned | DTER-WEST-230.0-1 | FACILITY |  | 1263 | 1389 | 1439 | 1583 | 503 | 553 | 573 | 631
DTER-WEST-230.0-1 | 5629 | DENVER TERMINAL SUBSTATION | XCEL | WEST SUBSTATION | XCEL | 70149 | 70480 | Xcel Owned | DTER-WEST-230.0-1 | Transmission Line | 5629 | 1263 | 1389 | 1439 | 1583 | 503 | 553 | 573 | 631
EAST-CHAM-115.0-1 | 9175 | EAST SUBSTATION | XCEL | CHAMBERS SUBSTATION | XCEL | 70162 | 70538 | Xcel Owned | EAST-CHAM-115.0-1 | FACILITY |  | 798 | 800 | 800 | 800 | 159 | 159 | 159 | 159
EAST-CHAM-115.0-1 | 9175 | EAST SUBSTATION | XCEL | CHAMBERS SUBSTATION | XCEL | 70162 | 70538 | Xcel Owned | EAST-CHAM-115.0-1 | Transmission Line | 9175 | 798 | 878 | 908 | 998 | 159 | 175 | 181 | 199
EAST-CHAM-115.0-1 | 9175 | EAST SUBSTATION | XCEL | CHAMBERS SUBSTATION | XCEL | 70162 | 70538 | Xcel Owned | 9175_135X_XDCR_W | SECONDARY_CURRENT_LIMITATION | EAST | 800 | 800 | 800 | 800 | 159 | 159 | 159 | 159
EAST-CHAM-115.0-1 | 9175 | EAST SUBSTATION | XCEL | CHAMBERS SUBSTATION | XCEL | 70162 | 70538 | Xcel Owned | 9175_135X_METER_W | SECONDARY_CURRENT_LIMITATION | EAST | 800 | 800 | 800 | 800 | 159 | 159 | 159 | 159
EAST-CHAM-115.0-1 | 9175 | EAST SUBSTATION | XCEL | CHAMBERS SUBSTATION | XCEL | 70162 | 70538 | Xcel Owned | 9175_135X_METER_AMPSW | SECONDARY_CURRENT_LIMITATION | EAST | 800 | 800 | 800 | 800 | 159 | 159 | 159 | 159
EAST-CHAM-115.0-1 | 9175 | EAST SUBSTATION | XCEL | CHAMBERS SUBSTATION | XCEL | 70162 | 70538 | Xcel Owned | 9175_135X_XDCR_VAR | SECONDARY_CURRENT_LIMITATION | EAST | 800 | 800 | 800 | 800 | 159 | 159 | 159 | 159
EAST-CHAM-115.0-1 | 9175 | EAST SUBSTATION | XCEL | CHAMBERS SUBSTATION | XCEL | 70162 | 70538 | Xcel Owned | 9175 246X | CURRENT_TRANSFORMER | EAST | 800 | 800 | 800 | 800 | 159 | 159 | 159 | 159
EAST-CHAM-115.0-1 | 9175 | EAST SUBSTATION | XCEL | CHAMBERS SUBSTATION | XCEL | 70162 | 70538 | Xcel Owned | 9175 135X | CURRENT_TRANSFORMER | EAST | 800 | 800 | 800 | 800 | 159 | 159 | 159 | 159
EAST-CHAM-115.0-1 | 9175 | EAST SUBSTATION | XCEL | CHAMBERS SUBSTATION | XCEL | 70162 | 70538 | Xcel Owned | 9175_135X_XDCR_AMP | SECONDARY_CURRENT_LIMITATION | EAST | 800 | 800 | 800 | 800 | 159 | 159 | 159 | 159
EAST-FITZ-115.0-1 | 9178 | EAST SUBSTATION | XCEL | FITZSIMONS SUBSTATION | XCEL | 70162 | 70537 | Xcel Owned | EAST-FITZ-115.0-1 | FACILITY |  | 600 | 600 | 600 | 600 | 120 | 120 | 120 | 120
EAST-FITZ-115.0-1 | 9178 | EAST SUBSTATION | XCEL | FITZSIMONS SUBSTATION | XCEL | 70162 | 70537 | Xcel Owned | 9170_135X_METER_AMPSW | SECONDARY_CURRENT_LIMITATION | EAST | 600 | 600 | 600 | 600 | 120 | 120 | 120 | 120
EAST-FITZ-115.0-1 | 9178 | EAST SUBSTATION | XCEL | FITZSIMONS SUBSTATION | XCEL | 70162 | 70537 | Xcel Owned | 9170 135X | CURRENT_TRANSFORMER | EAST | 600 | 600 | 600 | 600 | 120 | 120 | 120 | 120
EAST-FITZ-115.0-1 | 9178 | EAST SUBSTATION | XCEL | FITZSIMONS SUBSTATION | XCEL | 70162 | 70537 | Xcel Owned | 9170_135X_XDCR_W | SECONDARY_CURRENT_LIMITATION | EAST | 600 | 600 | 600 | 600 | 120 | 120 | 120 | 120
EAST-FITZ-115.0-1 | 9178 | EAST SUBSTATION | XCEL | FITZSIMONS SUBSTATION | XCEL | 70162 | 70537 | Xcel Owned | 9170 246X | CURRENT_TRANSFORMER | EAST | 600 | 600 | 600 | 600 | 120 | 120 | 120 | 120
EAST-FITZ-115.0-1 | 9178 | EAST SUBSTATION | XCEL | FITZSIMONS SUBSTATION | XCEL | 70162 | 70537 | Xcel Owned | 9170_135X_XDCR_VAR | SECONDARY_CURRENT_LIMITATION | EAST | 600 | 600 | 600 | 600 | 120 | 120 | 120 | 120
EAST-FITZ-115.0-1 | 9178 | EAST SUBSTATION | XCEL | FITZSIMONS SUBSTATION | XCEL | 70162 | 70537 | Xcel Owned | 9170_135X_XDCR_AMP | SECONDARY_CURRENT_LIMITATION | EAST | 600 | 600 | 600 | 600 | 120 | 120 | 120 | 120
EAST-FITZ-115.0-1 | 9178 | EAST SUBSTATION | XCEL | FITZSIMONS SUBSTATION | XCEL | 70162 | 70537 | Xcel Owned | 9178L | SWITCH | EAST | 600 | 775 | 743 | 890 | 120 | 154 | 148 | 177
EAST-FITZ-115.0-1 | 9178 | EAST SUBSTATION | XCEL | FITZSIMONS SUBSTATION | XCEL | 70162 | 70537 | Xcel Owned | 9178M | SWITCH | EAST | 600 | 775 | 743 | 890 | 120 | 154 | 148 | 177
EAST-SMOK-115.0-1 | 9174 | EAST SUBSTATION | XCEL | SMOKY HILL SUBSTATION | XCEL | 70171 | 70395 | Xcel Owned | EAST-SMOK-115.0-1 | FACILITY |  | 794 | 873 | 903 | 993 | 158 | 174 | 180 | 198
EAST-SMOK-115.0-1 | 9174 | EAST SUBSTATION | XCEL | SMOKY HILL SUBSTATION | XCEL | 70171 | 70395 | Xcel Owned | EAST-SMOK-115.0-1 | Transmission Line | 9174 | 794 | 873 | 903 | 993 | 158 | 174 | 180 | 198
EAST-SMOK-115.0-2 | 9866 | EAST SUBSTATION | XCEL | SMOKY HILL SUBSTATION | XCEL | 70171 | 70395 | Xcel Owned | EAST-SMOK-115.0-2 | FACILITY |  | 600 | 728 | 743 | 800 | 120 | 145 | 148 | 159
EAST-SMOK-115.0-2 | 9866 | EAST SUBSTATION | XCEL | SMOKY HILL SUBSTATION | XCEL | 70171 | 70395 | Xcel Owned | 9866M | SWITCH | EAST | 600 | 775 | 743 | 890 | 120 | 154 | 148 | 177
EAST-SMOK-115.0-2 | 9866 | EAST SUBSTATION | XCEL | SMOKY HILL SUBSTATION | XCEL | 70171 | 70395 | Xcel Owned | 9866L | SWITCH | EAST | 600 | 775 | 743 | 890 | 120 | 154 | 148 | 177
EAST-SMOK-115.0-2 | 9866 | EAST SUBSTATION | XCEL | SMOKY HILL SUBSTATION | XCEL | 70171 | 70395 | Xcel Owned | 300 - 19 | BUSBAR_SECTION | EAST | 629 | 728 | 745 | 827 | 125 | 145 | 148 | 165
EAST-SMOK-115.0-2 | 9866 | EAST SUBSTATION | XCEL | SMOKY HILL SUBSTATION | XCEL | 70171 | 70395 | Xcel Owned | 9866 135X | CURRENT_TRANSFORMER | EAST | 800 | 800 | 800 | 800 | 159 | 159 | 159 | 159
EAST-SMOK-115.0-2 | 9866 | EAST SUBSTATION | XCEL | SMOKY HILL SUBSTATION | XCEL | 70171 | 70395 | Xcel Owned | 9866_135X_XDCR_VAR | SECONDARY_CURRENT_LIMITATION | EAST | 800 | 800 | 800 | 800 | 159 | 159 | 159 | 159
EAST-SMOK-115.0-2 | 9866 | EAST SUBSTATION | XCEL | SMOKY HILL SUBSTATION | XCEL | 70171 | 70395 | Xcel Owned | 9866_135X_XDCR_W | SECONDARY_CURRENT_LIMITATION | EAST | 800 | 800 | 800 | 800 | 159 | 159 | 159 | 159
EAST-SMOK-115.0-2 | 9866 | EAST SUBSTATION | XCEL | SMOKY HILL SUBSTATION | XCEL | 70171 | 70395 | Xcel Owned | 9866 246X | CURRENT_TRANSFORMER | EAST | 800 | 800 | 800 | 800 | 159 | 159 | 159 | 159
EAST-SMOK-115.0-2 | 9866 | EAST SUBSTATION | XCEL | SMOKY HILL SUBSTATION | XCEL | 70171 | 70395 | Xcel Owned | 9866_135X_XDCR_AMP | SECONDARY_CURRENT_LIMITATION | EAST | 800 | 800 | 800 | 800 | 159 | 159 | 159 | 159
ELAT-MONR-230.0-1 | 5283 | ELATI SUBSTATION | XCEL | MONROE SUBSTATION | XCEL | 70163 | 70291 | Xcel Owned | ELAT-MONR-230.0-1 | FACILITY |  | 800 | 1000 | 1000 | 1000 | 319 | 398 | 398 | 398
ELAT-MONR-230.0-1 | 5283 | ELATI SUBSTATION | XCEL | MONROE SUBSTATION | XCEL | 70163 | 70291 | Xcel Owned | ELAT-MONR-230.0-1 | Transmission Line | 5283 | 800 | 1000 | 1000 | 1000 | 319 | 398 | 398 | 398
ELAT-MONR-230.0-1 | 5283 | ELATI SUBSTATION | XCEL | MONROE SUBSTATION | XCEL | 70163 | 70291 | Xcel Owned | 5283_AMPS_230KV | SECONDARY_CURRENT_LIMITATION | ELAT | 1000 | 1000 | 1000 | 1000 | 398 | 398 | 398 | 398
ELAT-MONR-230.0-1 | 5283 | ELATI SUBSTATION | XCEL | MONROE SUBSTATION | XCEL | 70163 | 70291 | Xcel Owned | 5283_W/VAR_230KV | SECONDARY_CURRENT_LIMITATION | ELAT | 1000 | 1000 | 1000 | 1000 | 398 | 398 | 398 | 398
ELDO-NCAR-115.0-1 | 9205 | ELDORADO SPRINGS SUBSTATION | XCEL | NCAR SUBSTATION | XCEL | 70164 | 70295 | Xcel Owned | ELDO-NCAR-115.0-1 | FACILITY |  | 808 | 889 | 909 | 1000 | 161 | 177 | 181 | 199
ELDO-NCAR-115.0-1 | 9205 | ELDORADO SPRINGS SUBSTATION | XCEL | NCAR SUBSTATION | XCEL | 70164 | 70295 | Xcel Owned | ELDO-NCAR-115.0-1 | Transmission Line | 9205 | 808 | 889 | 909 | 1000 | 161 | 177 | 181 | 199
ELDO-NREL-115.0-1 | 9587 | ELDORADO SPRINGS SUBSTATION | XCEL | NREL | XCEL | 70164 | 70170 | Xcel Owned | ELDO-NREL-115.0-1 | FACILITY |  | 794 | 874 | 900 | 990 | 158 | 174 | 179 | 197
ELDO-NREL-115.0-1 | 9587 | ELDORADO SPRINGS SUBSTATION | XCEL | NREL | XCEL | 70164 | 70170 | Xcel Owned | ELDO-NREL-115.0-1 | Transmission Line | 9587 | 794 | 874 | 900 | 990 | 158 | 174 | 179 | 197
ELDO-RALS-115.0-1 | 9688 | ELDORADO SPRINGS SUBSTATION | XCEL | RALSTON SUBSTATION | XCEL | 70164 | 70346 | Xcel Owned | ELDO-RALS-115.0-1 | FACILITY |  | 644 | 708 | 732 | 805 | 128 | 141 | 146 | 160
ELDO-RALS-115.0-1 | 9688 | ELDORADO SPRINGS SUBSTATION | XCEL | RALSTON SUBSTATION | XCEL | 70164 | 70346 | Xcel Owned | ELDO-RALS-115.0-1 | Transmission Line | 9688 | 644 | 708 | 732 | 805 | 128 | 141 | 146 | 160
ELDO-VALM-115.0-1 | 9046 | ELDORADO SPRINGS SUBSTATION | XCEL | VALMONT SWITCHYARD SUBSTATION | XCEL | 70164 | 70444 | Xcel Owned | ELDO-VALM-115.0-1 | FACILITY |  | 645 | 709 | 733 | 806 | 128 | 141 | 146 | 161
ELDO-VALM-115.0-1 | 9046 | ELDORADO SPRINGS SUBSTATION | XCEL | VALMONT SWITCHYARD SUBSTATION | XCEL | 70164 | 70444 | Xcel Owned | ELDO-VALM-115.0-1 | Transmission Line | 9046 | 645 | 709 | 733 | 806 | 128 | 141 | 146 | 161
ENGL-LITT-115.0-1 | 9336 | ENGLEWOOD SUBSTATION | XCEL | LITTLETON SUBSTATION | XCEL | 70168 | 70263 | Xcel Owned | ENGL-LITT-115.0-1 | FACILITY |  | 797 | 877 | 906 | 997 | 159 | 175 | 180 | 199
ENGL-LITT-115.0-1 | 9336 | ENGLEWOOD SUBSTATION | XCEL | LITTLETON SUBSTATION | XCEL | 70168 | 70263 | Xcel Owned | ENGL-LITT-115.0-1 | Transmission Line | 9336 | 797 | 877 | 906 | 997 | 159 | 175 | 180 | 199
FEDC_TP-QUAK_TP-115.0-1 | 9122 | FEDERAL CENTER TAP | XCEL | QUAKER TAP | XCEL | 70173 | 70342 | Xcel Owned | FEDC_TP-QUAK_TP-115.0-1 | FACILITY |  | 1280 | 1408 | 1280 | 1408 | 255 | 280 | 255 | 280
FEDC_TP-QUAK_TP-115.0-1 | 9122 | FEDERAL CENTER TAP | XCEL | QUAKER TAP | XCEL | 70173 | 70342 | Xcel Owned | FEDC_TP-QUAK_TP-115.0-1 | Transmission Line | 9122 | 1280 | 1408 | 1280 | 1408 | 255 | 280 | 255 | 280
FEDE-SEMP-115.0-1 | 9055 | FEDERAL HEIGHTS SUBSTATION | XCEL | SEMPER SUBSTATION | XCEL | 70175 | 70382 | Xcel Owned | FEDE-SEMP-115.0-1 | FACILITY |  | 797 | 876 | 906 | 997 | 159 | 174 | 180 | 199
FEDE-SEMP-115.0-1 | 9055 | FEDERAL HEIGHTS SUBSTATION | XCEL | SEMPER SUBSTATION | XCEL | 70175 | 70382 | Xcel Owned | FEDE-SEMP-115.0-1 | Transmission Line | 9055 | 797 | 876 | 906 | 997 | 159 | 174 | 180 | 199
FITZ-CHAM-115.0-1 | 9178 | FITZSIMONS SUBSTATION | XCEL | CHAMBERS SUBSTATION | XCEL | 70537 | 70538 | Xcel Owned | FITZ-CHAM-115.0-1 | FACILITY |  | 798 | 878 | 908 | 999 | 159 | 175 | 181 | 199
FITZ-CHAM-115.0-1 | 9178 | FITZSIMONS SUBSTATION | XCEL | CHAMBERS SUBSTATION | XCEL | 70537 | 70538 | Xcel Owned | FITZ-CHAM-115.0-1 | Transmission Line | 9178 | 798 | 878 | 908 | 999 | 159 | 175 | 181 | 199
FLUP-FSVR-230.0-1 | 5311 | FORT LUPTON SUBSTATION | XCEL | FORT SAINT VRAIN SWITCHYARD | XCEL | 70192 | 70410 | Xcel Owned | FLUP-FSVR-230.0-1 | FACILITY |  | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
FLUP-FSVR-230.0-1 | 5311 | FORT LUPTON SUBSTATION | XCEL | FORT SAINT VRAIN SWITCHYARD | XCEL | 70192 | 70410 | Xcel Owned | TL5311 W/VAR XDCR | SECONDARY_CURRENT_LIMITATION | FSVR | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
FLUP-FSVR-230.0-1 | 5311 | FORT LUPTON SUBSTATION | XCEL | FORT SAINT VRAIN SWITCHYARD | XCEL | 70192 | 70410 | Xcel Owned | 5311_21ZP | SECONDARY_CURRENT_LIMITATION | FLUP | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
FLUP-FSVR-230.0-1 | 5311 | FORT LUPTON SUBSTATION | XCEL | FORT SAINT VRAIN SWITCHYARD | XCEL | 70192 | 70410 | Xcel Owned | 5311_67GP | SECONDARY_CURRENT_LIMITATION | FLUP | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
FLUP-FSVR-230.0-1 | 5311 | FORT LUPTON SUBSTATION | XCEL | FORT SAINT VRAIN SWITCHYARD | XCEL | 70192 | 70410 | Xcel Owned | 5311_21Z1 | SECONDARY_CURRENT_LIMITATION | FSVR | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
FLUP-FSVR-230.0-1 | 5311 | FORT LUPTON SUBSTATION | XCEL | FORT SAINT VRAIN SWITCHYARD | XCEL | 70192 | 70410 | Xcel Owned | 5311_21ZP | SECONDARY_CURRENT_LIMITATION | FSVR | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
FLUP-FSVR-230.0-1 | 5311 | FORT LUPTON SUBSTATION | XCEL | FORT SAINT VRAIN SWITCHYARD | XCEL | 70192 | 70410 | Xcel Owned | TL5311 AMP XDCR | SECONDARY_CURRENT_LIMITATION | FSVR | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
FLUP-FSVR-230.0-1 | 5311 | FORT LUPTON SUBSTATION | XCEL | FORT SAINT VRAIN SWITCHYARD | XCEL | 70192 | 70410 | Xcel Owned | 5311_21Z2 | SECONDARY_CURRENT_LIMITATION | FSVR | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
FLUP-FSVR-230.0-2 | 5329 | FORT LUPTON SUBSTATION | XCEL | FORT SAINT VRAIN SWITCHYARD | XCEL | 70192 | 70410 | Xcel Owned | FLUP-FSVR-230.0-2 | FACILITY |  | 1376 | 1514 | 1537 | 1690 | 548 | 603 | 612 | 673
FLUP-FSVR-230.0-2 | 5329 | FORT LUPTON SUBSTATION | XCEL | FORT SAINT VRAIN SWITCHYARD | XCEL | 70192 | 70410 | Xcel Owned | FLUP-FSVR-230.0-2 | Transmission Line | 5329 | 1376 | 1514 | 1537 | 1690 | 548 | 603 | 612 | 673
FLUP-FSVR-230.0-2 | 5329 | FORT LUPTON SUBSTATION | XCEL | FORT SAINT VRAIN SWITCHYARD | XCEL | 70192 | 70410 | Xcel Owned | Narcissus | BUSBAR_SECTION | FSVR | 1376 | 1514 | 1537 | 1690 | 548 | 603 | 612 | 673
FLUP-GRVL-230.0-1 | 5525 | FORT LUPTON SUBSTATION | XCEL | GREEN VALLEY SUBSTATION | XCEL | 70192 | 70048 | Xcel Owned | FLUP-GRVL-230.0-1 | FACILITY |  | 1430 | 1573 | 1629 | 1792 | 570 | 627 | 649 | 714
FLUP-GRVL-230.0-1 | 5525 | FORT LUPTON SUBSTATION | XCEL | GREEN VALLEY SUBSTATION | XCEL | 70192 | 70048 | Xcel Owned | Narcissus | BUSBAR_SECTION | FLUP | 1430 | 1573 | 1629 | 1792 | 570 | 627 | 649 | 714
FLUP-HNLK-230.0-1 | 5047 | FORT LUPTON SUBSTATION | XCEL | HENRY LAKE (Tri State) | FOREIGN | 70192 | 70605 | Xcel Owned | FLUP-HNLK-230.0-1 | FACILITY |  | 1270 | 1397 | 1447 | 1592 | 506 | 557 | 576 | 634
FLUP-HNLK-230.0-1 | 5047 | FORT LUPTON SUBSTATION | XCEL | HENRY LAKE (Tri State) | FOREIGN | 70192 | 70605 | Xcel Owned | FLUP-HNLK-230.0-1 | Transmission Line | 5047 | 1270 | 1397 | 1447 | 1592 | 506 | 557 | 576 | 634
FLUP-JLGR-230.0-1 | 5183 | FORT LUPTON SUBSTATION | XCEL | J. L. Green | FOREIGN | 70192 | 70529 | Jointly Owned | FLUP-JLGR-230.0-1 | FACILITY |  | 1223 | 1430 | 1461 | 1627 | 487 | 570 | 582 | 648
FLUP-JLGR-230.0-1 | 5183 | FORT LUPTON SUBSTATION | XCEL | J. L. Green | FOREIGN | 70192 | 70529 | Jointly Owned | Narcissus | BUSBAR_SECTION | FLUP | 1223 | 1430 | 1461 | 1629 | 487 | 570 | 582 | 649
FLUP-JLGR-230.0-1 | 5183 | FORT LUPTON SUBSTATION | XCEL | J. L. Green | FOREIGN | 70192 | 70529 | Jointly Owned | Foreign Ratings | Foreign Ratings | JLGR | 1599 | 1627 | 1599 | 1627 | 637 | 648 | 637 | 648
FLUP-PAWN-230.0-1 | 5463 | FORT LUPTON SUBSTATION | XCEL | PAWNEE 345KV | XCEL | 70192 | 70311 | Xcel Owned | FLUP-PAWN-230.0-1 | FACILITY |  | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
FLUP-PAWN-230.0-1 | 5463 | FORT LUPTON SUBSTATION | XCEL | PAWNEE 345KV | XCEL | 70192 | 70311 | Xcel Owned | 5463_67GP | SECONDARY_CURRENT_LIMITATION | FLUP | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
FLUP-PAWN-230.0-1 | 5463 | FORT LUPTON SUBSTATION | XCEL | PAWNEE 345KV | XCEL | 70192 | 70311 | Xcel Owned | TL5463_21ZP | SECONDARY_CURRENT_LIMITATION | PAWN | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
FLUP-PAWN-230.0-1 | 5463 | FORT LUPTON SUBSTATION | XCEL | PAWNEE 345KV | XCEL | 70192 | 70311 | Xcel Owned | TL5463_67GP | SECONDARY_CURRENT_LIMITATION | PAWN | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
FLUP-PAWN-230.0-1 | 5463 | FORT LUPTON SUBSTATION | XCEL | PAWNEE 345KV | XCEL | 70192 | 70311 | Xcel Owned | 5463_21ZP | SECONDARY_CURRENT_LIMITATION | FLUP | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
FLUP-PAWN-230.0-1 | 5463 | FORT LUPTON SUBSTATION | XCEL | PAWNEE 345KV | XCEL | 70192 | 70311 | Xcel Owned | TL5463_67GB | SECONDARY_CURRENT_LIMITATION | PAWN | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
FLUP-PAWN-230.0-1 | 5463 | FORT LUPTON SUBSTATION | XCEL | PAWNEE 345KV | XCEL | 70192 | 70311 | Xcel Owned | TL5463_21Z2 | SECONDARY_CURRENT_LIMITATION | PAWN | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
FLUP-PAWN-230.0-1 | 5463 | FORT LUPTON SUBSTATION | XCEL | PAWNEE 345KV | XCEL | 70192 | 70311 | Xcel Owned | TL5463_21Z1 | SECONDARY_CURRENT_LIMITATION | PAWN | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
FLUP-PVAL-115.0-1 | 9499 | FORT LUPTON SUBSTATION | XCEL | PLATTE VALLEY | XCEL | 70090 | 70307 | Xcel Owned | FLUP-PVAL-115.0-1 | FACILITY |  | 1200 | 1330 | 1377 | 1515 | 239 | 265 | 274 | 302
FLUP-PVAL-115.0-1 | 9499 | FORT LUPTON SUBSTATION | XCEL | PLATTE VALLEY | XCEL | 70090 | 70307 | Xcel Owned | 9499-5 | SWITCH | PVAL | 1200 | 1549 | 1486 | 1780 | 239 | 309 | 296 | 355
FLUP-PVAL-115.0-1 | 9499 | FORT LUPTON SUBSTATION | XCEL | PLATTE VALLEY | XCEL | 70090 | 70307 | Xcel Owned | 9499-6 | SWITCH | PVAL | 1200 | 1549 | 1486 | 1780 | 239 | 309 | 296 | 355
FLUP-PVAL-115.0-1 | 9499 | FORT LUPTON SUBSTATION | XCEL | PLATTE VALLEY | XCEL | 70090 | 70307 | Xcel Owned | Cardinal | BUSBAR_SECTION | PVAL | 1209 | 1330 | 1377 | 1515 | 241 | 265 | 274 | 302
FLUP-PVAL-115.0-1 | 9499 | FORT LUPTON SUBSTATION | XCEL | PLATTE VALLEY | XCEL | 70090 | 70307 | Xcel Owned | Cardinal | BUSBAR_SECTION | FLUP | 1209 | 1330 | 1377 | 1515 | 241 | 265 | 274 | 302
FLUP-PVAL-115.0-1 | 9499 | FORT LUPTON SUBSTATION | XCEL | PLATTE VALLEY | XCEL | 70090 | 70307 | Xcel Owned | FLUP-PVAL-115.0-1 | Transmission Line | 9499 | 1210 | 1331 | 1378 | 1515 | 241 | 265 | 274 | 302
FLUP-TCTI-230.0-1 | 5529 | FORT LUPTON SUBSTATION | XCEL | J M SHAFER (TSGT) | FOREIGN | 70192 | 70488 | Jointly Owned | FLUP-TCTI-230.0-1 | FACILITY |  | 1274 | 1401 | 1450 | 1595 | 508 | 558 | 578 | 635
FLUP-TCTI-230.0-1 | 5529 | FORT LUPTON SUBSTATION | XCEL | J M SHAFER (TSGT) | FOREIGN | 70192 | 70488 | Jointly Owned | FLUP-TCTI-230.0-1 | Transmission Line | 5529 | 1274 | 1401 | 1450 | 1595 | 508 | 558 | 578 | 635
FLUP-VASQ-115.0-1 | 9494 | FORT LUPTON SUBSTATION | XCEL | VASQUEZ SUBSTATION | XCEL | 70191 | 70450 | Xcel Owned | FLUP-VASQ-115.0-1 | FACILITY |  | 801 | 881 | 911 | 1002 | 160 | 175 | 181 | 200
FLUP-VASQ-115.0-1 | 9494 | FORT LUPTON SUBSTATION | XCEL | VASQUEZ SUBSTATION | XCEL | 70191 | 70450 | Xcel Owned | FLUP-VASQ-115.0-1 | Transmission Line | 9494 | 801 | 881 | 911 | 1002 | 160 | 175 | 181 | 200
FNSS-LASS-345.0-1 | J05, 7005 | FINNEY SWITCHING STATION | XCEL | LAMAR 345KV SWITCHING STATION | XCEL | 523853 | 599950 | Xcel Owned | FNSS-LASS-345.0-1 | FACILITY |  | 636 | 636 | 1000 | 1000 | 380 | 380 | 598 | 598
FNSS-LASS-345.0-1 | J05, 7005 | FINNEY SWITCHING STATION | XCEL | LAMAR 345KV SWITCHING STATION | XCEL | 523853 | 599950 | Xcel Owned | FNSS-LASS-345.0-1 | Transmission Line | J05, 7005 | 636 | 636 | 1471 | 1471 | 380 | 380 | 879 | 879
FNSS-LASS-345.0-1 | J05, 7005 | FINNEY SWITCHING STATION | XCEL | LAMAR 345KV SWITCHING STATION | XCEL | 523853 | 599950 | Xcel Owned | 7002 246X | CURRENT_TRANSFORMER | LASS | 1000 | 1000 | 1000 | 1000 | 598 | 598 | 598 | 598
FORU-PALM-115.0-1 | 9605 | FOX RUN (TRI-STATE) | FOREIGN | PALMER LAKE SUBSTATION | XCEL | 73414 | 70308 | Jointly Owned | FORU-PALM-115.0-1 | FACILITY |  | 783 | 813 | 813 | 813 | 156 | 162 | 162 | 162
FORU-PALM-115.0-1 | 9605 | FOX RUN (TRI-STATE) | FOREIGN | PALMER LAKE SUBSTATION | XCEL | 73414 | 70308 | Jointly Owned | Hawk | BUSBAR_SECTION | PALM | 783 | 861 | 891 | 980 | 156 | 172 | 178 | 195
FORU-PALM-115.0-1 | 9605 | FOX RUN (TRI-STATE) | FOREIGN | PALMER LAKE SUBSTATION | XCEL | 73414 | 70308 | Jointly Owned | Foreign Ratings | Foreign Ratings | 9605 | 813 | 813 | 813 | 813 | 162 | 162 | 162 | 162
FRGD-PVAL-115.0-1 | 9499 | FAIRGROUNDS SUBSTATION | XCEL | PLATTE VALLEY | XCEL | 70081 | 70307 | Xcel Owned | FRGD-PVAL-115.0-1 | FACILITY |  | 800 | 880 | 910 | 1001 | 159 | 175 | 181 | 199
FRGD-PVAL-115.0-1 | 9499 | FAIRGROUNDS SUBSTATION | XCEL | PLATTE VALLEY | XCEL | 70081 | 70307 | Xcel Owned | FRGD-PVAL-115.0-1 | Transmission Line | 9499 | 800 | 880 | 910 | 1001 | 159 | 175 | 181 | 199
FRGD-THTN-115.0-1 | 9499 | FAIRGROUNDS SUBSTATION | XCEL | THORNTON | XCEL | 70081 | 70099 | Xcel Owned | FRGD-THTN-115.0-1 | FACILITY |  | 800 | 880 | 909 | 1000 | 159 | 175 | 181 | 199
FRGD-THTN-115.0-1 | 9499 | FAIRGROUNDS SUBSTATION | XCEL | THORNTON | XCEL | 70081 | 70099 | Xcel Owned | FRGD-THTN-115.0-1 | Transmission Line | 9499 | 800 | 880 | 909 | 1000 | 159 | 175 | 181 | 199
FSVR-ISAB-230.0-1 | 5307 | FORT SAINT VRAIN SWITCHYARD | XCEL | ISABELLE SUBSTATION | XCEL | 70410 | 70544 | Xcel Owned | FSVR-ISAB-230.0-1 | FACILITY |  | 1274 | 1401 | 1450 | 1595 | 508 | 558 | 578 | 635
FSVR-ISAB-230.0-1 | 5307 | FORT SAINT VRAIN SWITCHYARD | XCEL | ISABELLE SUBSTATION | XCEL | 70410 | 70544 | Xcel Owned | FSVR-ISAB-230.0-1 | Transmission Line | 5307 | 1274 | 1401 | 1450 | 1595 | 508 | 558 | 578 | 635
FSVR-KEEN-230.0-1 | 5327 | FORT SAINT VRAIN SWITCHYARD | XCEL | KEENESBURG SUBSTATION | XCEL | 70410 | 70820 | Xcel Owned | FSVR-KEEN-230.0-1 | FACILITY |  | 1694 | 2074 | 2152 | 2400 | 675 | 826 | 857 | 956
FSVR-KEEN-230.0-1 | 5327 | FORT SAINT VRAIN SWITCHYARD | XCEL | KEENESBURG SUBSTATION | XCEL | 70410 | 70820 | Xcel Owned | 1/4 x 6 | BUSBAR_SECTION | FSVR | 1694 | 2074 | 2152 | 2451 | 675 | 826 | 857 | 977
FSVR-KEEN-230.0-1 | 5327 | FORT SAINT VRAIN SWITCHYARD | XCEL | KEENESBURG SUBSTATION | XCEL | 70410 | 70820 | Xcel Owned | 5960_246X_PK-2 | SECONDARY_CURRENT_LIMITATION | KEEN | 2400 | 2400 | 2400 | 2400 | 956 | 956 | 956 | 956
FSVR-KEEN-230.0-1 | 5327 | FORT SAINT VRAIN SWITCHYARD | XCEL | KEENESBURG SUBSTATION | XCEL | 70410 | 70820 | Xcel Owned | 5960_135X_PK-2 | SECONDARY_CURRENT_LIMITATION | KEEN | 2400 | 2400 | 2400 | 2400 | 956 | 956 | 956 | 956
FSVR-KEEN-230.0-1 | 5327 | FORT SAINT VRAIN SWITCHYARD | XCEL | KEENESBURG SUBSTATION | XCEL | 70410 | 70820 | Xcel Owned | 5327_246Y_PK-2 | SECONDARY_CURRENT_LIMITATION | KEEN | 2400 | 2400 | 2400 | 2400 | 956 | 956 | 956 | 956
FSVR-KEEN-230.0-1 | 5327 | FORT SAINT VRAIN SWITCHYARD | XCEL | KEENESBURG SUBSTATION | XCEL | 70410 | 70820 | Xcel Owned | 5327 PK-2-4 | SECONDARY_CURRENT_LIMITATION | FSVR | 2400 | 2400 | 2400 | 2400 | 956 | 956 | 956 | 956
FSVR-KEEN-230.0-1 | 5327 | FORT SAINT VRAIN SWITCHYARD | XCEL | KEENESBURG SUBSTATION | XCEL | 70410 | 70820 | Xcel Owned | 5322 135Y | CURRENT_TRANSFORMER | FSVR | 2400 | 2400 | 2400 | 2400 | 956 | 956 | 956 | 956
FSVR-KEEN-230.0-1 | 5327 | FORT SAINT VRAIN SWITCHYARD | XCEL | KEENESBURG SUBSTATION | XCEL | 70410 | 70820 | Xcel Owned | 5322 246X | CURRENT_TRANSFORMER | FSVR | 2400 | 2400 | 2400 | 2400 | 956 | 956 | 956 | 956
FSVR-KEEN-230.0-1 | 5327 | FORT SAINT VRAIN SWITCHYARD | XCEL | KEENESBURG SUBSTATION | XCEL | 70410 | 70820 | Xcel Owned | 5322 246Y | CURRENT_TRANSFORMER | FSVR | 2400 | 2400 | 2400 | 2400 | 956 | 956 | 956 | 956
FSVR-KEEN-230.0-1 | 5327 | FORT SAINT VRAIN SWITCHYARD | XCEL | KEENESBURG SUBSTATION | XCEL | 70410 | 70820 | Xcel Owned | 5960 135X | CURRENT_TRANSFORMER | KEEN | 2400 | 2400 | 2400 | 2400 | 956 | 956 | 956 | 956
FSVR-KEEN-230.0-1 | 5327 | FORT SAINT VRAIN SWITCHYARD | XCEL | KEENESBURG SUBSTATION | XCEL | 70410 | 70820 | Xcel Owned | 5322 135X | CURRENT_TRANSFORMER | FSVR | 2400 | 2400 | 2400 | 2400 | 956 | 956 | 956 | 956
FSVR-KEEN-230.0-1 | 5327 | FORT SAINT VRAIN SWITCHYARD | XCEL | KEENESBURG SUBSTATION | XCEL | 70410 | 70820 | Xcel Owned | 5327_246X_PK-2 | SECONDARY_CURRENT_LIMITATION | KEEN | 2400 | 2400 | 2400 | 2400 | 956 | 956 | 956 | 956
FSVR-KEEN-230.0-1 | 5327 | FORT SAINT VRAIN SWITCHYARD | XCEL | KEENESBURG SUBSTATION | XCEL | 70410 | 70820 | Xcel Owned | TL5327 PK-2-2 | SECONDARY_CURRENT_LIMITATION | FSVR | 2400 | 2400 | 2400 | 2400 | 956 | 956 | 956 | 956
FSVR-KEEN-230.0-1 | 5327 | FORT SAINT VRAIN SWITCHYARD | XCEL | KEENESBURG SUBSTATION | XCEL | 70410 | 70820 | Xcel Owned | 5960 246X | CURRENT_TRANSFORMER | KEEN | 2400 | 2400 | 2400 | 2400 | 956 | 956 | 956 | 956
FSVR-KEEN-230.0-1 | 5327 | FORT SAINT VRAIN SWITCHYARD | XCEL | KEENESBURG SUBSTATION | XCEL | 70410 | 70820 | Xcel Owned | 5327 246X | CURRENT_TRANSFORMER | KEEN | 2400 | 2400 | 2400 | 2400 | 956 | 956 | 956 | 956
FSVR-KEEN-230.0-1 | 5327 | FORT SAINT VRAIN SWITCHYARD | XCEL | KEENESBURG SUBSTATION | XCEL | 70410 | 70820 | Xcel Owned | 5327_246Y_PK | SECONDARY_CURRENT_LIMITATION | FSVR | 2400 | 2400 | 2400 | 2400 | 956 | 956 | 956 | 956
FSVR-KEEN-230.0-1 | 5327 | FORT SAINT VRAIN SWITCHYARD | XCEL | KEENESBURG SUBSTATION | XCEL | 70410 | 70820 | Xcel Owned | 5322 PK-2-2 | SECONDARY_CURRENT_LIMITATION | FSVR | 2400 | 2400 | 2400 | 2400 | 956 | 956 | 956 | 956
FSVR-KEEN-230.0-1 | 5327 | FORT SAINT VRAIN SWITCHYARD | XCEL | KEENESBURG SUBSTATION | XCEL | 70410 | 70820 | Xcel Owned | 5322 PK-2-4 | SECONDARY_CURRENT_LIMITATION | FSVR | 2400 | 2400 | 2400 | 2400 | 956 | 956 | 956 | 956
FSVR-KEEN-230.0-1 | 5327 | FORT SAINT VRAIN SWITCHYARD | XCEL | KEENESBURG SUBSTATION | XCEL | 70410 | 70820 | Xcel Owned | 5327 PK-2-1 | SECONDARY_CURRENT_LIMITATION | FSVR | 2400 | 2400 | 2400 | 2400 | 956 | 956 | 956 | 956
FSVR-KEEN-230.0-1 | 5327 | FORT SAINT VRAIN SWITCHYARD | XCEL | KEENESBURG SUBSTATION | XCEL | 70410 | 70820 | Xcel Owned | 5322 PK-2-1 | SECONDARY_CURRENT_LIMITATION | FSVR | 2400 | 2400 | 2400 | 2400 | 956 | 956 | 956 | 956
FSVR-KEEN-230.0-1 | 5327 | FORT SAINT VRAIN SWITCHYARD | XCEL | KEENESBURG SUBSTATION | XCEL | 70410 | 70820 | Xcel Owned | 5960_135Y_PK-2 | SECONDARY_CURRENT_LIMITATION | KEEN | 2400 | 2400 | 2400 | 2400 | 956 | 956 | 956 | 956
FSVR-KEEN-230.0-1 | 5327 | FORT SAINT VRAIN SWITCHYARD | XCEL | KEENESBURG SUBSTATION | XCEL | 70410 | 70820 | Xcel Owned | 5960 135Y | CURRENT_TRANSFORMER | KEEN | 2400 | 2400 | 2400 | 2400 | 956 | 956 | 956 | 956
FSVR-KEEN-230.0-1 | 5327 | FORT SAINT VRAIN SWITCHYARD | XCEL | KEENESBURG SUBSTATION | XCEL | 70410 | 70820 | Xcel Owned | 5327 246Y | CURRENT_TRANSFORMER | KEEN | 2400 | 2400 | 2400 | 2400 | 956 | 956 | 956 | 956
FSVR-KEEN-230.0-1 | 5327 | FORT SAINT VRAIN SWITCHYARD | XCEL | KEENESBURG SUBSTATION | XCEL | 70410 | 70820 | Xcel Owned | 5322 PK-2-3 | SECONDARY_CURRENT_LIMITATION | FSVR | 2400 | 2400 | 2400 | 2400 | 956 | 956 | 956 | 956
FSVR-KEEN-230.0-1 | 5327 | FORT SAINT VRAIN SWITCHYARD | XCEL | KEENESBURG SUBSTATION | XCEL | 70410 | 70820 | Xcel Owned | 5960_246Y_PK-2 | SECONDARY_CURRENT_LIMITATION | KEEN | 2400 | 2400 | 2400 | 2400 | 956 | 956 | 956 | 956
FSVR-KEEN-230.0-1 | 5327 | FORT SAINT VRAIN SWITCHYARD | XCEL | KEENESBURG SUBSTATION | XCEL | 70410 | 70820 | Xcel Owned | 5960 246Y | CURRENT_TRANSFORMER | KEEN | 2400 | 2400 | 2400 | 2400 | 956 | 956 | 956 | 956
FSVR-KEEN-230.0-1 | 5327 | FORT SAINT VRAIN SWITCHYARD | XCEL | KEENESBURG SUBSTATION | XCEL | 70410 | 70820 | Xcel Owned | TL5327 PK-2-1 | SECONDARY_CURRENT_LIMITATION | FSVR | 2400 | 2400 | 2400 | 2400 | 956 | 956 | 956 | 956
FSVR-KEEN-230.0-1 | 5327 | FORT SAINT VRAIN SWITCHYARD | XCEL | KEENESBURG SUBSTATION | XCEL | 70410 | 70820 | Xcel Owned | 5327_135Y_PK-2 | SECONDARY_CURRENT_LIMITATION | FSVR | 2400 | 2400 | 2400 | 2400 | 956 | 956 | 956 | 956
FSVR-KEEN-230.0-1 | 5327 | FORT SAINT VRAIN SWITCHYARD | XCEL | KEENESBURG SUBSTATION | XCEL | 70410 | 70820 | Xcel Owned | 5322_246Y_PK | SECONDARY_CURRENT_LIMITATION | FSVR | 2400 | 2400 | 2400 | 2400 | 956 | 956 | 956 | 956
FSVR-SPIN-230.0-1 | 5953 | FORT SAINT VRAIN SWITCHYARD | XCEL | SPINDLE SUBSTATION | XCEL | 70410 | 70592 | Xcel Owned | FSVR-SPIN-230.0-1 | FACILITY |  | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
FSVR-SPIN-230.0-1 | 5953 | FORT SAINT VRAIN SWITCHYARD | XCEL | SPINDLE SUBSTATION | XCEL | 70410 | 70592 | Xcel Owned | 5953 PKG-BF | SECONDARY_CURRENT_LIMITATION | FSVR | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
FSVR-SPIN-230.0-1 | 5953 | FORT SAINT VRAIN SWITCHYARD | XCEL | SPINDLE SUBSTATION | XCEL | 70410 | 70592 | Xcel Owned | 5310 PK-2-4 | SECONDARY_CURRENT_LIMITATION | FSVR | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
FSVR-WELD-230.0-1 | 5315 | FORT SAINT VRAIN SWITCHYARD | XCEL | WELD SUBSTATION | XCEL | 70410 | 70471 | Xcel Owned | FSVR-WELD-230.0-1 | FACILITY |  | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
FSVR-WELD-230.0-1 | 5315 | FORT SAINT VRAIN SWITCHYARD | XCEL | WELD SUBSTATION | XCEL | 70410 | 70471 | Xcel Owned | 5315_21ZP | SECONDARY_CURRENT_LIMITATION | FSVR | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
FSVR-WIND-230.0-1 | 5313 | FORT SAINT VRAIN SWITCHYARD | XCEL | WINDSOR SUBSTATION | XCEL | 70410 | 70474 | Jointly Owned | FSVR-WIND-230.0-1 | FACILITY |  | 1449 | 1594 | 1600 | 1600 | 577 | 635 | 637 | 637
FSVR-WIND-230.0-1 | 5313 | FORT SAINT VRAIN SWITCHYARD | XCEL | WINDSOR SUBSTATION | XCEL | 70410 | 70474 | Jointly Owned | FSVR-WIND-230.0-1 | Transmission Line | 5313 | 1449 | 1594 | 1653 | 1818 | 577 | 635 | 659 | 724
FSVR-WIND-230.0-1 | 5313 | FORT SAINT VRAIN SWITCHYARD | XCEL | WINDSOR SUBSTATION | XCEL | 70410 | 70474 | Jointly Owned | 5313-2 | CIRCUIT_SWITCHER | WIND | 1600 | 1600 | 1600 | 1600 | 637 | 637 | 637 | 637
FSVR-WIND-230.0-1 | 5313 | FORT SAINT VRAIN SWITCHYARD | XCEL | WINDSOR SUBSTATION | XCEL | 70410 | 70474 | Jointly Owned | 5313-1 | CIRCUIT_SWITCHER | WIND | 1600 | 1600 | 1600 | 1600 | 637 | 637 | 637 | 637
FSVR-WIND-230.0-1 | 5313 | FORT SAINT VRAIN SWITCHYARD | XCEL | WINDSOR SUBSTATION | XCEL | 70410 | 70474 | Jointly Owned | 5674 | BREAKER | WIND | 1600 | 1600 | 1600 | 1600 | 637 | 637 | 637 | 637
FSVR-WIND-230.0-1 | 5313 | FORT SAINT VRAIN SWITCHYARD | XCEL | WINDSOR SUBSTATION | XCEL | 70410 | 70474 | Jointly Owned | 5675 | BREAKER | WIND | 1600 | 1600 | 1600 | 1600 | 637 | 637 | 637 | 637
FULT-PKWY-115.0-1 | 9053 | FULTON SUBSTATION | XCEL | PARKWAY (Tri State) | FOREIGN | 70194 | 70604 | Jointly Owned | FULT-PKWY-115.0-1 | FACILITY |  | 921 | 1072 | 1096 | 1200 | 183 | 213 | 218 | 239
FULT-PKWY-115.0-1 | 9053 | FULTON SUBSTATION | XCEL | PARKWAY (Tri State) | FOREIGN | 70194 | 70604 | Jointly Owned | Arbutus | BUSBAR_SECTION | FULT | 921 | 1072 | 1096 | 1219 | 183 | 213 | 218 | 243
FULT-PKWY-115.0-1 | 9053 | FULTON SUBSTATION | XCEL | PARKWAY (Tri State) | FOREIGN | 70194 | 70604 | Jointly Owned | 9053-11 | CIRCUIT_SWITCHER | FULT | 1200 | 1200 | 1200 | 1200 | 239 | 239 | 239 | 239
FVNG-MIDW-230.0-1 | 5123 | FOUNTAIN VALLEY NUG SWITCHYARD | XCEL | MIDWAY SUBSTATION | XCEL | 70193 | 70286 | Xcel Owned | FVNG-MIDW-230.0-1 | FACILITY |  | 1267 | 1394 | 1443 | 1500 | 505 | 555 | 575 | 598
FVNG-MIDW-230.0-1 | 5123 | FOUNTAIN VALLEY NUG SWITCHYARD | XCEL | MIDWAY SUBSTATION | XCEL | 70193 | 70286 | Xcel Owned | FVNG-MIDW-230.0-1 | Transmission Line | 5123 | 1267 | 1394 | 1443 | 1587 | 505 | 555 | 575 | 632
FVNG-MIDW-230.0-1 | 5123 | FOUNTAIN VALLEY NUG SWITCHYARD | XCEL | MIDWAY SUBSTATION | XCEL | 70193 | 70286 | Xcel Owned | 230 BUSN B | CURRENT_TRANSFORMER | FVNG | 1500 | 1500 | 1500 | 1500 | 598 | 598 | 598 | 598
FVNG-MIDW-230.0-1 | 5123 | FOUNTAIN VALLEY NUG SWITCHYARD | XCEL | MIDWAY SUBSTATION | XCEL | 70193 | 70286 | Xcel Owned | 230 BUSN A | CURRENT_TRANSFORMER | FVNG | 1500 | 1500 | 1500 | 1500 | 598 | 598 | 598 | 598
FVNG-MIDW-230.0-1 | 5123 | FOUNTAIN VALLEY NUG SWITCHYARD | XCEL | MIDWAY SUBSTATION | XCEL | 70193 | 70286 | Xcel Owned | 230 BUSN C | CURRENT_TRANSFORMER | FVNG | 1500 | 1500 | 1500 | 1500 | 598 | 598 | 598 | 598
GEOR-HEND-115.0-1 | 9665 | GEORGETOWN HYDRO SUBSTATION | XCEL | HENDERSON SUBSTATION | XCEL | 70197 | 70218 | Xcel Owned | GEOR-HEND-115.0-1 | FACILITY |  | 748 | 748 | 827 | 827 | 149 | 149 | 165 | 165
GEOR-HEND-115.0-1 | 9665 | GEORGETOWN HYDRO SUBSTATION | XCEL | HENDERSON SUBSTATION | XCEL | 70197 | 70218 | Xcel Owned | GEOR-HEND-115.0-1 | Transmission Line | 9665 | 748 | 748 | 827 | 827 | 149 | 149 | 165 | 165
GILC-GODF-115.0-1 | 9494 | GILCREST SUBSTATION | XCEL | GODFREY SUBSTATION | XCEL | 70198 | 70202 | Xcel Owned | GILC-GODF-115.0-1 | FACILITY |  | 1074 | 1181 | 1200 | 1200 | 214 | 235 | 239 | 239
GILC-GODF-115.0-1 | 9494 | GILCREST SUBSTATION | XCEL | GODFREY SUBSTATION | XCEL | 70198 | 70202 | Xcel Owned | Arbutus | BUSBAR_SECTION | GILC | 1074 | 1181 | 1222 | 1344 | 214 | 235 | 243 | 268
GILC-GODF-115.0-1 | 9494 | GILCREST SUBSTATION | XCEL | GODFREY SUBSTATION | XCEL | 70198 | 70202 | Xcel Owned | 9494-8 | CIRCUIT_SWITCHER | GILC | 1200 | 1200 | 1200 | 1200 | 239 | 239 | 239 | 239
GJCT-HORI-230.0-1 | 5555 | GRAND JUNCTION SUBSTATION (PSCO) | XCEL | HORIZON SUBSTATION | XCEL | 70206 | 70233 | Xcel Owned | GJCT-HORI-230.0-1 | FACILITY |  | 1200 | 1436 | 1468 | 1600 | 478 | 572 | 585 | 637
GJCT-HORI-230.0-1 | 5555 | GRAND JUNCTION SUBSTATION (PSCO) | XCEL | HORIZON SUBSTATION | XCEL | 70206 | 70233 | Xcel Owned | 5570 | SWITCH | HORI | 1200 | 1549 | 1486 | 1780 | 478 | 617 | 592 | 709
GJCT-HORI-230.0-1 | 5555 | GRAND JUNCTION SUBSTATION (PSCO) | XCEL | HORIZON SUBSTATION | XCEL | 70206 | 70233 | Xcel Owned | Narcissus | BUSBAR_SECTION | HORI | 1229 | 1436 | 1468 | 1635 | 489 | 572 | 585 | 651
GJCT-HORI-230.0-1 | 5555 | GRAND JUNCTION SUBSTATION (PSCO) | XCEL | HORIZON SUBSTATION | XCEL | 70206 | 70233 | Xcel Owned | Narcissus | BUSBAR_SECTION | GJCT | 1229 | 1436 | 1468 | 1635 | 489 | 572 | 585 | 651
GJCT-HORI-230.0-1 | 5555 | GRAND JUNCTION SUBSTATION (PSCO) | XCEL | HORIZON SUBSTATION | XCEL | 70206 | 70233 | Xcel Owned | 5555-1 | CIRCUIT_SWITCHER | HORI | 1600 | 1600 | 1600 | 1600 | 637 | 637 | 637 | 637
GLEN-WASH-230.0-1 | 5527 | GLENN SUBSTATION | XCEL | WASHINGTON SUBSTATION | XCEL | 70200 | 70461 | Xcel Owned | GLEN-WASH-230.0-1 | FACILITY |  | 1218 | 1424 | 1454 | 1600 | 485 | 567 | 579 | 637
GLEN-WASH-230.0-1 | 5527 | GLENN SUBSTATION | XCEL | WASHINGTON SUBSTATION | XCEL | 70200 | 70461 | Xcel Owned | Narcissus | BUSBAR_SECTION | GLEN | 1218 | 1424 | 1454 | 1623 | 485 | 567 | 579 | 647
GLEN-WASH-230.0-1 | 5527 | GLENN SUBSTATION | XCEL | WASHINGTON SUBSTATION | XCEL | 70200 | 70461 | Xcel Owned | 5527-4 | CIRCUIT_SWITCHER | WASH | 1600 | 1600 | 1600 | 1600 | 637 | 637 | 637 | 637
GLEN-WASH-230.0-1 | 5527 | GLENN SUBSTATION | XCEL | WASHINGTON SUBSTATION | XCEL | 70200 | 70461 | Xcel Owned | 5527-1 | CIRCUIT_SWITCHER | GLEN | 1600 | 1600 | 1600 | 1600 | 637 | 637 | 637 | 637
GODF-GRLY-115.0-1 | 9118 | GODFREY SUBSTATION | XCEL | GREELEY SUBSTATION | XCEL | 70202 | 70209 | Xcel Owned | GODF-GRLY-115.0-1 | FACILITY |  | 785 | 785 | 898 | 898 | 156 | 156 | 179 | 179
GODF-GRLY-115.0-1 | 9118 | GODFREY SUBSTATION | XCEL | GREELEY SUBSTATION | XCEL | 70202 | 70209 | Xcel Owned | GODF-GRLY-115.0-1 | Transmission Line | 9118 | 785 | 785 | 898 | 898 | 156 | 156 | 179 | 179
GODF-JOHN-115.0-1 | 8365 | GODFREY SUBSTATION | XCEL | JOHNSTOWN SUBSTATION | XCEL | 70202 | 70240 | Xcel Owned | GODF-JOHN-115.0-1 | FACILITY |  | 939 | 1033 | 1068 | 1175 | 187 | 206 | 213 | 234
GODF-JOHN-115.0-1 | 8365 | GODFREY SUBSTATION | XCEL | JOHNSTOWN SUBSTATION | XCEL | 70202 | 70240 | Xcel Owned | Swift | BUSBAR_SECTION | JOHN | 939 | 1033 | 1068 | 1175 | 187 | 206 | 213 | 234
GOOS-MAYV-345.0-1 | 7263 | GOOSE CREEK | XCEL | MAY VALLEY SUBSTATION | XCEL | 70918 | 70919 | Xcel Owned | GOOS-MAYV-345.0-1 | FACILITY |  | 2914 | 3000 | 3000 | 3000 | 1741 | 1793 | 1793 | 1793
GOOS-MAYV-345.0-1 | 7263 | GOOSE CREEK | XCEL | MAY VALLEY SUBSTATION | XCEL | 70918 | 70919 | Xcel Owned | GOOS-MAYV-345.0-1 | Transmission Line | 7263 | 2914 | 3205 | 3322 | 3654 | 1741 | 1915 | 1985 | 2183
GOOS-MAYV-345.0-1 | 7263 | GOOSE CREEK | XCEL | MAY VALLEY SUBSTATION | XCEL | 70918 | 70919 | Xcel Owned | 7252 | BREAKER | GOOS | 3000 | 3000 | 3000 | 3000 | 1793 | 1793 | 1793 | 1793
GOOS-MAYV-345.0-1 | 7263 | GOOSE CREEK | XCEL | MAY VALLEY SUBSTATION | XCEL | 70918 | 70919 | Xcel Owned | 7270 | BREAKER | MAYV | 3000 | 3000 | 3000 | 3000 | 1793 | 1793 | 1793 | 1793
GOOS-MAYV-345.0-1 | 7263 | GOOSE CREEK | XCEL | MAY VALLEY SUBSTATION | XCEL | 70918 | 70919 | Xcel Owned | 7263 | BREAKER | GOOS | 3000 | 3000 | 3000 | 3000 | 1793 | 1793 | 1793 | 1793
GOOS-MAYV-345.0-1 | 7263 | GOOSE CREEK | XCEL | MAY VALLEY SUBSTATION | XCEL | 70918 | 70919 | Xcel Owned | 7263 | BREAKER | MAYV | 3000 | 3000 | 3000 | 3000 | 1793 | 1793 | 1793 | 1793
GOOS-MAYV-345.0-2 | 7277 | GOOSE CREEK | XCEL | MAY VALLEY SUBSTATION | XCEL | 70918 | 70919 | Xcel Owned | GOOS-MAYV-345.0-2 | FACILITY |  | 2914 | 3000 | 3000 | 3000 | 1741 | 1793 | 1793 | 1793
GOOS-MAYV-345.0-2 | 7277 | GOOSE CREEK | XCEL | MAY VALLEY SUBSTATION | XCEL | 70918 | 70919 | Xcel Owned | GOOS-MAYV-345.0-2 | Transmission Line | 7277 | 2914 | 3205 | 3322 | 3654 | 1741 | 1915 | 1985 | 2183
GOOS-MAYV-345.0-2 | 7277 | GOOSE CREEK | XCEL | MAY VALLEY SUBSTATION | XCEL | 70918 | 70919 | Xcel Owned | 7277 | BREAKER | MAYV | 3000 | 3000 | 3000 | 3000 | 1793 | 1793 | 1793 | 1793
GOOS-MAYV-345.0-2 | 7277 | GOOSE CREEK | XCEL | MAY VALLEY SUBSTATION | XCEL | 70918 | 70919 | Xcel Owned | 7254 | BREAKER | GOOS | 3000 | 3000 | 3000 | 3000 | 1793 | 1793 | 1793 | 1793
GOOS-MAYV-345.0-2 | 7277 | GOOSE CREEK | XCEL | MAY VALLEY SUBSTATION | XCEL | 70918 | 70919 | Xcel Owned | 7277 | BREAKER | GOOS | 3000 | 3000 | 3000 | 3000 | 1793 | 1793 | 1793 | 1793
GOOS-MAYV-345.0-2 | 7277 | GOOSE CREEK | XCEL | MAY VALLEY SUBSTATION | XCEL | 70918 | 70919 | Xcel Owned | 7272 | BREAKER | MAYV | 3000 | 3000 | 3000 | 3000 | 1793 | 1793 | 1793 | 1793
GOOS-SHOR-345.0-1 | 7199 | GOOSE CREEK | XCEL | SHORTGRASS | XCEL | 70918 | 70630 | Xcel Owned | GOOS-SHOR-345.0-1 | FACILITY |  | 1200 | 1200 | 1200 | 1200 | 717 | 717 | 717 | 717
GOOS-SHOR-345.0-1 | 7199 | GOOSE CREEK | XCEL | SHORTGRASS | XCEL | 70918 | 70630 | Xcel Owned | 345 7199 C | CURRENT_TRANSFORMER | SHOR | 1200 | 1200 | 1200 | 1200 | 717 | 717 | 717 | 717
GOOS-SHOR-345.0-1 | 7199 | GOOSE CREEK | XCEL | SHORTGRASS | XCEL | 70918 | 70630 | Xcel Owned | 7199_METER | SECONDARY_CURRENT_LIMITATION | SHOR | 1200 | 1200 | 1200 | 1200 | 717 | 717 | 717 | 717
GOOS-SHOR-345.0-1 | 7199 | GOOSE CREEK | XCEL | SHORTGRASS | XCEL | 70918 | 70630 | Xcel Owned | 345 7199 A | CURRENT_TRANSFORMER | SHOR | 1200 | 1200 | 1200 | 1200 | 717 | 717 | 717 | 717
GOOS-SHOR-345.0-1 | 7199 | GOOSE CREEK | XCEL | SHORTGRASS | XCEL | 70918 | 70630 | Xcel Owned | 345 7199 B | CURRENT_TRANSFORMER | SHOR | 1200 | 1200 | 1200 | 1200 | 717 | 717 | 717 | 717
GRAY-LAKE-115.0-1 | 9000 | GRAY STREET SUBSTATION | XCEL | LAKEWOOD SUBSTATION | XCEL | 70208 | 70251 | Xcel Owned | GRAY-LAKE-115.0-1 | FACILITY |  | 557 | 600 | 600 | 600 | 111 | 120 | 120 | 120
GRAY-LAKE-115.0-1 | 9000 | GRAY STREET SUBSTATION | XCEL | LAKEWOOD SUBSTATION | XCEL | 70208 | 70251 | Xcel Owned | 4/0 - 7 | BUSBAR_SECTION | LAKE | 557 | 613 | 640 | 704 | 111 | 122 | 127 | 140
GRAY-LAKE-115.0-1 | 9000 | GRAY STREET SUBSTATION | XCEL | LAKEWOOD SUBSTATION | XCEL | 70208 | 70251 | Xcel Owned | 9000_135Y_METER_AMPSW | SECONDARY_CURRENT_LIMITATION | GRAY | 600 | 600 | 600 | 600 | 120 | 120 | 120 | 120
GRAY-LAKE-115.0-1 | 9000 | GRAY STREET SUBSTATION | XCEL | LAKEWOOD SUBSTATION | XCEL | 70208 | 70251 | Xcel Owned | 9000_246X_67GP | SECONDARY_CURRENT_LIMITATION | GRAY | 600 | 600 | 600 | 600 | 120 | 120 | 120 | 120
GRAY-LAKE-115.0-1 | 9000 | GRAY STREET SUBSTATION | XCEL | LAKEWOOD SUBSTATION | XCEL | 70208 | 70251 | Xcel Owned | 9000_135Y_XDCR_W_VAR | SECONDARY_CURRENT_LIMITATION | GRAY | 600 | 600 | 600 | 600 | 120 | 120 | 120 | 120
GRAY-LAKE-115.0-1 | 9000 | GRAY STREET SUBSTATION | XCEL | LAKEWOOD SUBSTATION | XCEL | 70208 | 70251 | Xcel Owned | 9000_135Y_METER_VAR | SECONDARY_CURRENT_LIMITATION | GRAY | 600 | 600 | 600 | 600 | 120 | 120 | 120 | 120
GRAY-LAKE-115.0-1 | 9000 | GRAY STREET SUBSTATION | XCEL | LAKEWOOD SUBSTATION | XCEL | 70208 | 70251 | Xcel Owned | 9000_135Y_METER_W | SECONDARY_CURRENT_LIMITATION | GRAY | 600 | 600 | 600 | 600 | 120 | 120 | 120 | 120
GRAY-LAKE-115.0-1 | 9000 | GRAY STREET SUBSTATION | XCEL | LAKEWOOD SUBSTATION | XCEL | 70208 | 70251 | Xcel Owned | 9000_246X_21ZP | SECONDARY_CURRENT_LIMITATION | GRAY | 600 | 600 | 600 | 600 | 120 | 120 | 120 | 120
GRAY-LAKE-115.0-1 | 9000 | GRAY STREET SUBSTATION | XCEL | LAKEWOOD SUBSTATION | XCEL | 70208 | 70251 | Xcel Owned | 9000_246Y_67GS | SECONDARY_CURRENT_LIMITATION | GRAY | 600 | 600 | 600 | 600 | 120 | 120 | 120 | 120
GRAY-LAKE-115.0-2 | 9005 | GRAY STREET SUBSTATION | XCEL | LAKEWOOD SUBSTATION | XCEL | 70208 | 70252 | Xcel Owned | GRAY-LAKE-115.0-2 | FACILITY |  | 557 | 600 | 600 | 600 | 111 | 120 | 120 | 120
GRAY-LAKE-115.0-2 | 9005 | GRAY STREET SUBSTATION | XCEL | LAKEWOOD SUBSTATION | XCEL | 70208 | 70252 | Xcel Owned | 4/0 - 7 | BUSBAR_SECTION | LAKE | 557 | 613 | 640 | 704 | 111 | 122 | 127 | 140
GRAY-LAKE-115.0-2 | 9005 | GRAY STREET SUBSTATION | XCEL | LAKEWOOD SUBSTATION | XCEL | 70208 | 70252 | Xcel Owned | 9005_135Y_METER_VAR | SECONDARY_CURRENT_LIMITATION | GRAY | 600 | 600 | 600 | 600 | 120 | 120 | 120 | 120
GRAY-LAKE-115.0-2 | 9005 | GRAY STREET SUBSTATION | XCEL | LAKEWOOD SUBSTATION | XCEL | 70208 | 70252 | Xcel Owned | 9005_135Y_XDCR_W | SECONDARY_CURRENT_LIMITATION | GRAY | 600 | 600 | 600 | 600 | 120 | 120 | 120 | 120
GRAY-LAKE-115.0-2 | 9005 | GRAY STREET SUBSTATION | XCEL | LAKEWOOD SUBSTATION | XCEL | 70208 | 70252 | Xcel Owned | 9005_135X_21ZP | SECONDARY_CURRENT_LIMITATION | GRAY | 600 | 600 | 600 | 600 | 120 | 120 | 120 | 120
GRAY-LAKE-115.0-2 | 9005 | GRAY STREET SUBSTATION | XCEL | LAKEWOOD SUBSTATION | XCEL | 70208 | 70252 | Xcel Owned | 9005_135Y_METER_AMPSW | SECONDARY_CURRENT_LIMITATION | GRAY | 600 | 600 | 600 | 600 | 120 | 120 | 120 | 120
GRAY-LAKE-115.0-2 | 9005 | GRAY STREET SUBSTATION | XCEL | LAKEWOOD SUBSTATION | XCEL | 70208 | 70252 | Xcel Owned | 9005_135X_67GP | SECONDARY_CURRENT_LIMITATION | GRAY | 600 | 600 | 600 | 600 | 120 | 120 | 120 | 120
GRAY-LAKE-115.0-2 | 9005 | GRAY STREET SUBSTATION | XCEL | LAKEWOOD SUBSTATION | XCEL | 70208 | 70252 | Xcel Owned | 9005_135Y_XDCR_VAR | SECONDARY_CURRENT_LIMITATION | GRAY | 600 | 600 | 600 | 600 | 120 | 120 | 120 | 120
GRAY-LAKE-115.0-2 | 9005 | GRAY STREET SUBSTATION | XCEL | LAKEWOOD SUBSTATION | XCEL | 70208 | 70252 | Xcel Owned | 9005_246Y_67GS | SECONDARY_CURRENT_LIMITATION | GRAY | 600 | 600 | 600 | 600 | 120 | 120 | 120 | 120
GRAY-LAKE-115.0-2 | 9005 | GRAY STREET SUBSTATION | XCEL | LAKEWOOD SUBSTATION | XCEL | 70208 | 70252 | Xcel Owned | 9005_135Y_METER_W | SECONDARY_CURRENT_LIMITATION | GRAY | 600 | 600 | 600 | 600 | 120 | 120 | 120 | 120
GRAY-SOUT-115.0-1 | 9332 | GRAY STREET SUBSTATION | XCEL | SOUTH SUBSTATION | XCEL | 70208 | 70402 | Xcel Owned | GRAY-SOUT-115.0-1 | FACILITY |  | 600 | 775 | 743 | 890 | 120 | 154 | 148 | 177
GRAY-SOUT-115.0-1 | 9332 | GRAY STREET SUBSTATION | XCEL | SOUTH SUBSTATION | XCEL | 70208 | 70402 | Xcel Owned | 9332L | SWITCH | GRAY | 600 | 775 | 743 | 890 | 120 | 154 | 148 | 177
GRAY-SOUT-115.0-1 | 9332 | GRAY STREET SUBSTATION | XCEL | SOUTH SUBSTATION | XCEL | 70208 | 70402 | Xcel Owned | 9332M | SWITCH | GRAY | 600 | 775 | 743 | 890 | 120 | 154 | 148 | 177
GRAY-SOUT-115.0-1 | 9332 | GRAY STREET SUBSTATION | XCEL | SOUTH SUBSTATION | XCEL | 70208 | 70402 | Xcel Owned | 9332-2 | SWITCH | SOUT | 600 | 775 | 743 | 890 | 120 | 154 | 148 | 177
GREE-MONA-230.0-1 | 5717 | GREENWOOD SUBSTATION | XCEL | MONACO SUBSTATION | XCEL | 70189 | 70481 | Xcel Owned | GREE-MONA-230.0-1 | FACILITY |  | 1263 | 1389 | 1263 | 1389 | 503 | 553 | 503 | 553
GREE-MONA-230.0-1 | 5717 | GREENWOOD SUBSTATION | XCEL | MONACO SUBSTATION | XCEL | 70189 | 70481 | Xcel Owned | GREE-MONA-230.0-1 | Transmission Line | 5717 | 1263 | 1389 | 1263 | 1389 | 503 | 553 | 503 | 553
GREE-PRAI-230.0-1 | 5707 | GREENWOOD SUBSTATION | XCEL | PRAIRIE SUBSTATION | XCEL | 70189 | 70323 | Xcel Owned | GREE-PRAI-230.0-1 | FACILITY |  | 1436 | 1579 | 1600 | 1600 | 572 | 629 | 637 | 637
GREE-PRAI-230.0-1 | 5707 | GREENWOOD SUBSTATION | XCEL | PRAIRIE SUBSTATION | XCEL | 70189 | 70323 | Xcel Owned | GREE-PRAI-230.0-1 | Transmission Line | 5707 | 1436 | 1579 | 1637 | 1800 | 572 | 629 | 652 | 717
GREE-PRAI-230.0-1 | 5707 | GREENWOOD SUBSTATION | XCEL | PRAIRIE SUBSTATION | XCEL | 70189 | 70323 | Xcel Owned | 5707-2 | CIRCUIT_SWITCHER | PRAI | 1600 | 1600 | 1600 | 1600 | 637 | 637 | 637 | 637
GREE-PRAI-230.0-2 | 5111 | GREENWOOD SUBSTATION | XCEL | PRAIRIE SUBSTATION | XCEL | 70212 | 70331 | Xcel Owned | GREE-PRAI-230.0-2 | FACILITY |  | 1436 | 1579 | 1600 | 1600 | 572 | 629 | 637 | 637
GREE-PRAI-230.0-2 | 5111 | GREENWOOD SUBSTATION | XCEL | PRAIRIE SUBSTATION | XCEL | 70212 | 70331 | Xcel Owned | GREE-PRAI-230.0-2 | Transmission Line | 5111 | 1436 | 1579 | 1637 | 1800 | 572 | 629 | 652 | 717
GREE-PRAI-230.0-2 | 5111 | GREENWOOD SUBSTATION | XCEL | PRAIRIE SUBSTATION | XCEL | 70212 | 70331 | Xcel Owned | 5111-2 | CIRCUIT_SWITCHER | PRAI | 1600 | 1600 | 1600 | 1600 | 637 | 637 | 637 | 637
GRLY-MONF-115.0-1 | 9115 | GREELEY SUBSTATION | XCEL | MONFORT SUBSTATION | XCEL | 70209 | 70290 | Xcel Owned | GRLY-MONF-115.0-1 | FACILITY |  | 1110 | 1200 | 1200 | 1200 | 221 | 239 | 239 | 239
GRLY-MONF-115.0-1 | 9115 | GREELEY SUBSTATION | XCEL | MONFORT SUBSTATION | XCEL | 70209 | 70290 | Xcel Owned | GRLY-MONF-115.0-1 | Transmission Line | 9115 | 1110 | 1221 | 1263 | 1390 | 221 | 243 | 252 | 277
GRLY-MONF-115.0-1 | 9115 | GREELEY SUBSTATION | XCEL | MONFORT SUBSTATION | XCEL | 70209 | 70290 | Xcel Owned | 9115 246Y | CURRENT_TRANSFORMER | MONF | 1200 | 1200 | 1200 | 1200 | 239 | 239 | 239 | 239
GRLY-MONF-115.0-1 | 9115 | GREELEY SUBSTATION | XCEL | MONFORT SUBSTATION | XCEL | 70209 | 70290 | Xcel Owned | 9115 135Y | CURRENT_TRANSFORMER | MONF | 1200 | 1200 | 1200 | 1200 | 239 | 239 | 239 | 239
GRLY-MONF-115.0-1 | 9115 | GREELEY SUBSTATION | XCEL | MONFORT SUBSTATION | XCEL | 70209 | 70290 | Xcel Owned | 9115 135X | CURRENT_TRANSFORMER | MONF | 1200 | 1200 | 1200 | 1200 | 239 | 239 | 239 | 239
GRLY-MONF-115.0-1 | 9115 | GREELEY SUBSTATION | XCEL | MONFORT SUBSTATION | XCEL | 70209 | 70290 | Xcel Owned |  | LINE_TRAP | MONF | 1200 | 1200 | 1267 | 1267 | 239 | 239 | 252 | 252
GRLY-WELD-115.0-1 | 9995 | GREELEY SUBSTATION | XCEL | WELD SUBSTATION | XCEL | 70209 | 70470 | Xcel Owned | GRLY-WELD-115.0-1 | FACILITY |  | 1109 | 1220 | 1262 | 1388 | 221 | 243 | 251 | 276
GRLY-WELD-115.0-1 | 9995 | GREELEY SUBSTATION | XCEL | WELD SUBSTATION | XCEL | 70209 | 70470 | Xcel Owned | GRLY-WELD-115.0-1 | Transmission Line | 9995 | 1109 | 1220 | 1262 | 1388 | 221 | 243 | 251 | 276
GRVL-IMBO-230.0-1 | 5277 | GREEN VALLEY SUBSTATION | XCEL | IMBODEN SUBSTATION | XCEL | 70048 | 70526 | Xcel Owned | GRVL-IMBO-230.0-1 | FACILITY |  | 1423 | 1565 | 1622 | 1784 | 567 | 624 | 646 | 711
GRVL-IMBO-230.0-1 | 5277 | GREEN VALLEY SUBSTATION | XCEL | IMBODEN SUBSTATION | XCEL | 70048 | 70526 | Xcel Owned | Narcissus | BUSBAR_SECTION | IMBO | 1423 | 1565 | 1622 | 1784 | 567 | 624 | 646 | 711
GRVL-KEEN-230.0-1 | 5279 | GREEN VALLEY SUBSTATION | XCEL | KEENESBURG SUBSTATION | XCEL | 70048 | 70820 | Xcel Owned | GRVL-KEEN-230.0-1 | FACILITY |  | 1800 | 1800 | 1800 | 1800 | 717 | 717 | 717 | 717
GRVL-KEEN-230.0-1 | 5279 | GREEN VALLEY SUBSTATION | XCEL | KEENESBURG SUBSTATION | XCEL | 70048 | 70820 | Xcel Owned | TL5279_XDCR_AMP | SECONDARY_CURRENT_LIMITATION | GRVL | 1800 | 1800 | 1800 | 1800 | 717 | 717 | 717 | 717
GRVL-KEEN-230.0-2 | 5961 | GREEN VALLEY SUBSTATION | XCEL | KEENESBURG SUBSTATION | XCEL | 70048 | 70820 | Xcel Owned | GRVL-KEEN-230.0-2 | FACILITY |  | 1800 | 1800 | 1800 | 1800 | 717 | 717 | 717 | 717
GRVL-KEEN-230.0-2 | 5961 | GREEN VALLEY SUBSTATION | XCEL | KEENESBURG SUBSTATION | XCEL | 70048 | 70820 | Xcel Owned | TL5961_XDCR_AMP | SECONDARY_CURRENT_LIMITATION | GRVL | 1800 | 1800 | 1800 | 1800 | 717 | 717 | 717 | 717
GRVL-RMEC-230.0-1 | 5271 | GREEN VALLEY SUBSTATION | XCEL | ROCKY MOUNTAIN ENERGY CENTER | XCEL | 70048 | 70590 | Xcel Owned | GRVL-RMEC-230.0-1 | FACILITY |  | 1800 | 1800 | 1800 | 1800 | 717 | 717 | 717 | 717
GRVL-RMEC-230.0-1 | 5271 | GREEN VALLEY SUBSTATION | XCEL | ROCKY MOUNTAIN ENERGY CENTER | XCEL | 70048 | 70590 | Xcel Owned | TL5271_XDCR_AMP | SECONDARY_CURRENT_LIMITATION | GRVL | 1800 | 1800 | 1800 | 1800 | 717 | 717 | 717 | 717
GRVL-SKYR-230.0-1 | 5275 | GREEN VALLEY SUBSTATION | XCEL | SKY RANCH SUBSTATION | XCEL | 70048 | 70392 | Xcel Owned | GRVL-SKYR-230.0-1 | FACILITY |  | 1215 | 1393 | 1442 | 1587 | 484 | 555 | 574 | 632
GRVL-SKYR-230.0-1 | 5275 | GREEN VALLEY SUBSTATION | XCEL | SKY RANCH SUBSTATION | XCEL | 70048 | 70392 | Xcel Owned | Narcissus | BUSBAR_SECTION | SKYR | 1215 | 1422 | 1452 | 1621 | 484 | 566 | 578 | 646
GRVL-SKYR-230.0-1 | 5275 | GREEN VALLEY SUBSTATION | XCEL | SKY RANCH SUBSTATION | XCEL | 70048 | 70392 | Xcel Owned | GRVL-SKYR-230.0-1 | Transmission Line | 5275 | 1266 | 1393 | 1442 | 1587 | 504 | 555 | 574 | 632
GRVL-SPRU-230.0-1 | 5270 | GREEN VALLEY SUBSTATION | XCEL | SPRUCE SUBSTATION | XCEL | 70048 | 70528 | Xcel Owned | GRVL-SPRU-230.0-1 | FACILITY |  | 1800 | 1800 | 1800 | 1800 | 717 | 717 | 717 | 717
GRVL-SPRU-230.0-1 | 5270 | GREEN VALLEY SUBSTATION | XCEL | SPRUCE SUBSTATION | XCEL | 70048 | 70528 | Xcel Owned | TL5270_XDCR_AMP | SECONDARY_CURRENT_LIMITATION | GRVL | 1800 | 1800 | 1800 | 1800 | 717 | 717 | 717 | 717
GUNB-NIWO-230.0-1 | 5635 | GUNBARREL SUBSTATION | XCEL | NIWOT SUBSTATION | XCEL | 70213 | 70297 | Xcel Owned | GUNB-NIWO-230.0-1 | FACILITY |  | 793 | 872 | 793 | 872 | 316 | 347 | 316 | 347
GUNB-NIWO-230.0-1 | 5635 | GUNBARREL SUBSTATION | XCEL | NIWOT SUBSTATION | XCEL | 70213 | 70297 | Xcel Owned | GUNB-NIWO-230.0-1 | Transmission Line | 5635 | 793 | 872 | 793 | 872 | 316 | 347 | 316 | 347
GUNB-NIWO-230.0-2 | 5639 | GUNBARREL SUBSTATION | XCEL | NIWOT SUBSTATION | XCEL | 70213 | 70297 | Xcel Owned | GUNB-NIWO-230.0-2 | FACILITY |  | 720 | 792 | 720 | 792 | 287 | 316 | 287 | 316
GUNB-NIWO-230.0-2 | 5639 | GUNBARREL SUBSTATION | XCEL | NIWOT SUBSTATION | XCEL | 70213 | 70297 | Xcel Owned | GUNB-NIWO-230.0-2 | Transmission Line | 5639 | 720 | 792 | 720 | 792 | 287 | 316 | 287 | 316
HAGE_TP-MALT-230.0-1 | 5245 | HAGERMAN PASS TAP | XCEL | MALTA SUBSTATION | XCEL | 2053 | 70274 | Xcel Owned | HAGE_TP-MALT-230.0-1 | FACILITY |  | 1037 | 1215 | 1224 | 1347 | 413 | 484 | 488 | 537
HAGE_TP-MALT-230.0-1 | 5245 | HAGERMAN PASS TAP | XCEL | MALTA SUBSTATION | XCEL | 2053 | 70274 | Xcel Owned | Curlew | BUSBAR_SECTION | MALT | 1037 | 1215 | 1244 | 1387 | 413 | 484 | 496 | 553
HAGE_TP-MALT-230.0-1 | 5245 | HAGERMAN PASS TAP | XCEL | MALTA SUBSTATION | XCEL | 2053 | 70274 | Xcel Owned | HAGE_TP-MALT-230.0-1 | Transmission Line | 5245 | 1130 | 1243 | 1224 | 1347 | 450 | 495 | 488 | 537
HARR-LEET-115.0-1 | 9955 | HARRISON SUBSTATION | XCEL | LEETSDALE SUBSTATION | XCEL | 70215 | 70282 | Xcel Owned | HARR-LEET-115.0-1 | FACILITY |  | 708 | 708 | 708 | 708 | 141 | 141 | 141 | 141
HARR-LEET-115.0-1 | 9955 | HARRISON SUBSTATION | XCEL | LEETSDALE SUBSTATION | XCEL | 70215 | 70282 | Xcel Owned | HARR-LEET-115.0-1 | Transmission Line | 9955 | 708 | 708 | 708 | 708 | 141 | 141 | 141 | 141
HAVA-CHAM-115.0-1 | 9543 | HAVANA SUBSTATION | XCEL | CHAMBERS SUBSTATION | XCEL | 70216 | 70538 | Xcel Owned | HAVA-CHAM-115.0-1 | FACILITY |  | 798 | 878 | 908 | 998 | 159 | 175 | 181 | 199
HAVA-CHAM-115.0-1 | 9543 | HAVANA SUBSTATION | XCEL | CHAMBERS SUBSTATION | XCEL | 70216 | 70538 | Xcel Owned | HAVA-CHAM-115.0-1 | Transmission Line | 9543 | 798 | 878 | 908 | 998 | 159 | 175 | 181 | 199
HAVA-CHAM-115.0-2 | 9544 | HAVANA SUBSTATION | XCEL | CHAMBERS SUBSTATION | XCEL | 70217 | 70538 | Xcel Owned | HAVA-CHAM-115.0-2 | FACILITY |  | 798 | 878 | 908 | 998 | 159 | 175 | 181 | 199
HAVA-CHAM-115.0-2 | 9544 | HAVANA SUBSTATION | XCEL | CHAMBERS SUBSTATION | XCEL | 70217 | 70538 | Xcel Owned | HAVA-CHAM-115.0-2 | Transmission Line | 9544 | 798 | 878 | 908 | 998 | 159 | 175 | 181 | 199
HAYD-FOID-230.0-1 | 5815 | HAYDEN (WAPA) | FOREIGN | FOIDEL CREEK SUBSTATION | XCEL | 79039 | 79091 | Xcel Owned | HAYD-FOID-230.0-1 | FACILITY |  | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
HAYD-FOID-230.0-1 | 5815 | HAYDEN (WAPA) | FOREIGN | FOIDEL CREEK SUBSTATION | XCEL | 79039 | 79091 | Xcel Owned | Foreign Ratings | Foreign Ratings | HAYD | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
HEND-PORT-115.0-1 | 8054 | HENDERSON SUBSTATION | XCEL | PORTAL SUBSTATION | XCEL | 70218 | 70328 | Jointly Owned | HEND-PORT-115.0-1 | FACILITY |  | 600 | 762 | 743 | 839 | 120 | 152 | 148 | 167
HEND-PORT-115.0-1 | 8054 | HENDERSON SUBSTATION | XCEL | PORTAL SUBSTATION | XCEL | 70218 | 70328 | Jointly Owned | 8054-2M | SWITCH | PORT | 600 | 775 | 743 | 890 | 120 | 154 | 148 | 177
HEND-PORT-115.0-1 | 8054 | HENDERSON SUBSTATION | XCEL | PORTAL SUBSTATION | XCEL | 70218 | 70328 | Jointly Owned | HEND-PORT-115.0-1 | Transmission Line | 8054 | 762 | 762 | 839 | 839 | 152 | 152 | 167 | 167
HIPO-IMBO-230.0-1 | 5277 | HIGH POINT | XCEL | IMBODEN SUBSTATION | XCEL | 70496 | 70526 | Xcel Owned | HIPO-IMBO-230.0-1 | FACILITY |  | 1423 | 1565 | 1622 | 1784 | 567 | 624 | 646 | 711
HIPO-IMBO-230.0-1 | 5277 | HIGH POINT | XCEL | IMBODEN SUBSTATION | XCEL | 70496 | 70526 | Xcel Owned | Narcissus | BUSBAR_SECTION | IMBO | 1423 | 1565 | 1622 | 1784 | 567 | 624 | 646 | 711
HIPO-SPRU-230.0-1 | 5277 | HIGH POINT | XCEL | SPRUCE SUBSTATION | XCEL | 70496 | 70528 | Xcel Owned | HIPO-SPRU-230.0-1 | FACILITY |  | 1861 | 2047 | 2117 | 2329 | 741 | 815 | 843 | 928
HIPO-SPRU-230.0-1 | 5277 | HIGH POINT | XCEL | SPRUCE SUBSTATION | XCEL | 70496 | 70528 | Xcel Owned | HIPO-SPRU-230.0-1 | Transmission Line | 5277 | 1861 | 2047 | 2117 | 2329 | 741 | 815 | 843 | 928
HMIL-MSST-345.0-1 | 7081 | HARVEST MILE | XCEL | MISSILE SITE | XCEL | 70597 | 70624 | Xcel Owned | HMIL-MSST-345.0-1 | FACILITY |  | 2821 | 2970 | 3136 | 3136 | 1686 | 1775 | 1874 | 1874
HMIL-MSST-345.0-1 | 7081 | HARVEST MILE | XCEL | MISSILE SITE | XCEL | 70597 | 70624 | Xcel Owned | Narcissus | BUSBAR_SECTION | MSST | 2821 | 3103 | 3214 | 3536 | 1686 | 1854 | 1921 | 2113
HMIL-MSST-345.0-1 | 7081 | HARVEST MILE | XCEL | MISSILE SITE | XCEL | 70597 | 70624 | Xcel Owned |  | LINE_TRAP | MSST | 2970 | 2970 | 3136 | 3136 | 1775 | 1775 | 1874 | 1874
HMIL-SMOK-230.0-1 | 5179 | HARVEST MILE | XCEL | SMOKY HILL SUBSTATION | XCEL | 70596 | 70396 | Xcel Owned | HMIL-SMOK-230.0-1 | FACILITY |  | 2400 | 2400 | 2400 | 2400 | 956 | 956 | 956 | 956
HMIL-SMOK-230.0-1 | 5179 | HARVEST MILE | XCEL | SMOKY HILL SUBSTATION | XCEL | 70596 | 70396 | Xcel Owned | 5179 135Y PK-2 | SECONDARY_CURRENT_LIMITATION | SMOK | 2400 | 2400 | 2400 | 2400 | 956 | 956 | 956 | 956
HMIL-SMOK-230.0-1 | 5179 | HARVEST MILE | XCEL | SMOKY HILL SUBSTATION | XCEL | 70596 | 70396 | Xcel Owned | 5166 PK-2-4 | SECONDARY_CURRENT_LIMITATION | SMOK | 2400 | 2400 | 2400 | 2400 | 956 | 956 | 956 | 956
HMIL-SMOK-230.0-1 | 5179 | HARVEST MILE | XCEL | SMOKY HILL SUBSTATION | XCEL | 70596 | 70396 | Xcel Owned | 5166 135Y | CURRENT_TRANSFORMER | SMOK | 2400 | 2400 | 2400 | 2400 | 956 | 956 | 956 | 956
HMIL-SMOK-230.0-1 | 5179 | HARVEST MILE | XCEL | SMOKY HILL SUBSTATION | XCEL | 70596 | 70396 | Xcel Owned | 5179 PK-2-4 | SECONDARY_CURRENT_LIMITATION | SMOK | 2400 | 2400 | 2400 | 2400 | 956 | 956 | 956 | 956
HMIL-SMOK-230.0-1 | 5179 | HARVEST MILE | XCEL | SMOKY HILL SUBSTATION | XCEL | 70596 | 70396 | Xcel Owned | 5166 PK-2-3 | SECONDARY_CURRENT_LIMITATION | SMOK | 2400 | 2400 | 2400 | 2400 | 956 | 956 | 956 | 956
HMIL-SMOK-230.0-1 | 5179 | HARVEST MILE | XCEL | SMOKY HILL SUBSTATION | XCEL | 70596 | 70396 | Xcel Owned | 5166 246Y | CURRENT_TRANSFORMER | SMOK | 2400 | 2400 | 2400 | 2400 | 956 | 956 | 956 | 956
HMIL-SMOK-230.0-1 | 5179 | HARVEST MILE | XCEL | SMOKY HILL SUBSTATION | XCEL | 70596 | 70396 | Xcel Owned | 5166 246Y PK-2 | SECONDARY_CURRENT_LIMITATION | SMOK | 2400 | 2400 | 2400 | 2400 | 956 | 956 | 956 | 956
HMIL-SMOK-230.0-1 | 5179 | HARVEST MILE | XCEL | SMOKY HILL SUBSTATION | XCEL | 70596 | 70396 | Xcel Owned | 5179 135Y | CURRENT_TRANSFORMER | SMOK | 2400 | 2400 | 2400 | 2400 | 956 | 956 | 956 | 956
HMIL-SMOK-230.0-1 | 5179 | HARVEST MILE | XCEL | SMOKY HILL SUBSTATION | XCEL | 70596 | 70396 | Xcel Owned | 5166 246X PK-2 | SECONDARY_CURRENT_LIMITATION | SMOK | 2400 | 2400 | 2400 | 2400 | 956 | 956 | 956 | 956
HMIL-SMOK-345.0-1 | 7081 | HARVEST MILE | XCEL | SMOKY HILL SUBSTATION | XCEL | 70597 | 70599 | Xcel Owned | HMIL-SMOK-345.0-1 | FACILITY |  | 2832 | 2970 | 3136 | 3136 | 1692 | 1775 | 1874 | 1874
HMIL-SMOK-345.0-1 | 7081 | HARVEST MILE | XCEL | SMOKY HILL SUBSTATION | XCEL | 70597 | 70599 | Xcel Owned | Narcissus | BUSBAR_SECTION | SMOK | 2832 | 3115 | 3228 | 3551 | 1692 | 1862 | 1929 | 2122
HMIL-SMOK-345.0-1 | 7081 | HARVEST MILE | XCEL | SMOKY HILL SUBSTATION | XCEL | 70597 | 70599 | Xcel Owned |  | LINE_TRAP | SMOK | 2970 | 2970 | 3136 | 3136 | 1775 | 1775 | 1874 | 1874
HMIL-SMOK-345.0-2 | 7087 | HARVEST MILE | XCEL | SMOKY HILL SUBSTATION | XCEL | 70597 | 70599 | Xcel Owned | HMIL-SMOK-345.0-2 | FACILITY |  | 2820 | 3000 | 3000 | 3000 | 1685 | 1793 | 1793 | 1793
HMIL-SMOK-345.0-2 | 7087 | HARVEST MILE | XCEL | SMOKY HILL SUBSTATION | XCEL | 70597 | 70599 | Xcel Owned | Narcissus | BUSBAR_SECTION | SMOK | 2820 | 3102 | 3214 | 3536 | 1685 | 1854 | 1921 | 2113
HMIL-SMOK-345.0-2 | 7087 | HARVEST MILE | XCEL | SMOKY HILL SUBSTATION | XCEL | 70597 | 70599 | Xcel Owned | 7087 | BREAKER | HMIL | 3000 | 3000 | 3000 | 3000 | 1793 | 1793 | 1793 | 1793
HMIL-SMOK-345.0-2 | 7087 | HARVEST MILE | XCEL | SMOKY HILL SUBSTATION | XCEL | 70597 | 70599 | Xcel Owned | 7151 | BREAKER | HMIL | 3000 | 3000 | 3000 | 3000 | 1793 | 1793 | 1793 | 1793
HMIL-SMOK-345.0-2 | 7087 | HARVEST MILE | XCEL | SMOKY HILL SUBSTATION | XCEL | 70597 | 70599 | Xcel Owned | 7150 | BREAKER | HMIL | 3000 | 3000 | 3000 | 3000 | 1793 | 1793 | 1793 | 1793
HMIL-SMOK-345.0-2 | 7087 | HARVEST MILE | XCEL | SMOKY HILL SUBSTATION | XCEL | 70597 | 70599 | Xcel Owned | 7082 | BREAKER | SMOK | 3000 | 3000 | 3000 | 3000 | 1793 | 1793 | 1793 | 1793
HOGB-LOOK-115.0-1 | 9794 | HOGBACK SUBSTATION | XCEL | LOOKOUT SUBSTATION | XCEL | 70224 | 70265 | Xcel Owned | HOGB-LOOK-115.0-1 | FACILITY |  | 1000 | 1000 | 1000 | 1000 | 199 | 199 | 199 | 199
HOGB-LOOK-115.0-1 | 9794 | HOGBACK SUBSTATION | XCEL | LOOKOUT SUBSTATION | XCEL | 70224 | 70265 | Xcel Owned | 9794_21Z1/2/3-A | SECONDARY_CURRENT_LIMITATION | LOOK | 1000 | 1000 | 1000 | 1000 | 199 | 199 | 199 | 199
HOGB-LOOK-115.0-1 | 9794 | HOGBACK SUBSTATION | XCEL | LOOKOUT SUBSTATION | XCEL | 70224 | 70265 | Xcel Owned | 9794_21Z1/2/3-B | SECONDARY_CURRENT_LIMITATION | LOOK | 1000 | 1000 | 1000 | 1000 | 199 | 199 | 199 | 199
HOGB-LOOK-115.0-1 | 9794 | HOGBACK SUBSTATION | XCEL | LOOKOUT SUBSTATION | XCEL | 70224 | 70265 | Xcel Owned | 9794 135Y | CURRENT_TRANSFORMER | LOOK | 1000 | 1000 | 1000 | 1000 | 199 | 199 | 199 | 199
HOGB-LOOK-115.0-1 | 9794 | HOGBACK SUBSTATION | XCEL | LOOKOUT SUBSTATION | XCEL | 70224 | 70265 | Xcel Owned | 9794 135X | CURRENT_TRANSFORMER | LOOK | 1000 | 1000 | 1000 | 1000 | 199 | 199 | 199 | 199
HOGB-LOOK-115.0-1 | 9794 | HOGBACK SUBSTATION | XCEL | LOOKOUT SUBSTATION | XCEL | 70224 | 70265 | Xcel Owned | 9794_21Z1/2/3-C | SECONDARY_CURRENT_LIMITATION | LOOK | 1000 | 1000 | 1000 | 1000 | 199 | 199 | 199 | 199
HOGB-LOOK-115.0-1 | 9794 | HOGBACK SUBSTATION | XCEL | LOOKOUT SUBSTATION | XCEL | 70224 | 70265 | Xcel Owned | 9794 246X | CURRENT_TRANSFORMER | LOOK | 1000 | 1000 | 1000 | 1000 | 199 | 199 | 199 | 199
HOGB-SODA-115.0-1 | 9794 | HOGBACK SUBSTATION | XCEL | SODA LAKES SUBSTATION | XCEL | 70224 | 70400 | Xcel Owned | HOGB-SODA-115.0-1 | FACILITY |  | 1000 | 1000 | 1000 | 1000 | 199 | 199 | 199 | 199
HOGB-SODA-115.0-1 | 9794 | HOGBACK SUBSTATION | XCEL | SODA LAKES SUBSTATION | XCEL | 70224 | 70400 | Xcel Owned | 9794_246X_21Z1/2/3-C | SECONDARY_CURRENT_LIMITATION | SODA | 1000 | 1000 | 1000 | 1000 | 199 | 199 | 199 | 199
HOGB-SODA-115.0-1 | 9794 | HOGBACK SUBSTATION | XCEL | SODA LAKES SUBSTATION | XCEL | 70224 | 70400 | Xcel Owned | 9794_246X_21Z1/2/3-A | SECONDARY_CURRENT_LIMITATION | SODA | 1000 | 1000 | 1000 | 1000 | 199 | 199 | 199 | 199
HOGB-SODA-115.0-1 | 9794 | HOGBACK SUBSTATION | XCEL | SODA LAKES SUBSTATION | XCEL | 70224 | 70400 | Xcel Owned | 9794_246X_21Z1/2/3-B | SECONDARY_CURRENT_LIMITATION | SODA | 1000 | 1000 | 1000 | 1000 | 199 | 199 | 199 | 199
HOPK_TP-HOPK-115.0-1 | 9256 | HOPKINS TAP | XCEL | HOPKINS SUBSTATION | XCEL | 2203 | 70231 | Xcel Owned | HOPK_TP-HOPK-115.0-1 | FACILITY |  | 435 | 478 | 477 | 525 | 87 | 95 | 95 | 105
HOPK_TP-HOPK-115.0-1 | 9256 | HOPKINS TAP | XCEL | HOPKINS SUBSTATION | XCEL | 2203 | 70231 | Xcel Owned | HOPK_TP-HOPK-115.0-1 | Transmission Line | 9256 | 435 | 478 | 477 | 525 | 87 | 95 | 95 | 105
HOPK-HAGE_TP-230.0-1 | 5245 | HOPKINS SUBSTATION | XCEL | HAGERMAN PASS TAP | XCEL | 70232 | 2053 | Xcel Owned | HOPK-HAGE_TP-230.0-1 | FACILITY |  | 1117 | 1229 | 1225 | 1348 | 445 | 490 | 488 | 537
HOPK-HAGE_TP-230.0-1 | 5245 | HOPKINS SUBSTATION | XCEL | HAGERMAN PASS TAP | XCEL | 70232 | 2053 | Xcel Owned | HOPK-HAGE_TP-230.0-1 | Transmission Line | 5245 | 1117 | 1229 | 1225 | 1348 | 445 | 490 | 488 | 537
HOPK-RIFL-230.0-1 | 5207 | HOPKINS SUBSTATION | XCEL | RIFLE 230KV SUBSTATION (PSCO) | XCEL | 70232 | 70358 | Xcel Owned | HOPK-RIFL-230.0-1 | FACILITY |  | 1085 | 1205 | 1236 | 1359 | 432 | 480 | 492 | 541
HOPK-RIFL-230.0-1 | 5207 | HOPKINS SUBSTATION | XCEL | RIFLE 230KV SUBSTATION (PSCO) | XCEL | 70232 | 70358 | Xcel Owned | Curlew | BUSBAR_SECTION | RIFL | 1085 | 1265 | 1296 | 1441 | 432 | 504 | 516 | 574
HOPK-RIFL-230.0-1 | 5207 | HOPKINS SUBSTATION | XCEL | RIFLE 230KV SUBSTATION (PSCO) | XCEL | 70232 | 70358 | Xcel Owned | HOPK-RIFL-230.0-1 | Transmission Line | 5207 | 1095 | 1205 | 1236 | 1359 | 436 | 480 | 492 | 541
HORI-ADOB-230.0-1 | 5555 | HORIZON SUBSTATION | XCEL | ADOBE SUBSTATION | XCEL | 70233 | 70268 | Xcel Owned | HORI-ADOB-230.0-1 | FACILITY |  | 790 | 790 | 794 | 794 | 315 | 315 | 316 | 316 | Railroad Documentation
HORI-ADOB-230.0-1 | 5555 | HORIZON SUBSTATION | XCEL | ADOBE SUBSTATION | XCEL | 70233 | 70268 | Xcel Owned | HORI-ADOB-230.0-1 | Transmission Line | 5555 | 790 | 790 | 794 | 794 | 315 | 315 | 316 | 316
HOST-MURP-230.0-1 | 5163 | HOMESTEAD SUBSTATION | XCEL | MURPHY CREEK SUBSTATION | XCEL | 70513 | 70551 | Xcel Owned | HOST-MURP-230.0-1 | FACILITY |  | 1840 | 2000 | 2000 | 2000 | 733 | 797 | 797 | 797
HOST-MURP-230.0-1 | 5163 | HOMESTEAD SUBSTATION | XCEL | MURPHY CREEK SUBSTATION | XCEL | 70513 | 70551 | Xcel Owned | HOST-MURP-230.0-1 | Transmission Line | 5163 | 1840 | 2025 | 2088 | 2297 | 733 | 807 | 832 | 915
HOST-MURP-230.0-1 | 5163 | HOMESTEAD SUBSTATION | XCEL | MURPHY CREEK SUBSTATION | XCEL | 70513 | 70551 | Xcel Owned | 5163-3 | CIRCUIT_SWITCHER | HOST | 2000 | 2000 | 2000 | 2000 | 797 | 797 | 797 | 797
HOST-MURP-230.0-1 | 5163 | HOMESTEAD SUBSTATION | XCEL | MURPHY CREEK SUBSTATION | XCEL | 70513 | 70551 | Xcel Owned | 5163-1 | CIRCUIT_SWITCHER | MURP | 2000 | 2000 | 2000 | 2000 | 797 | 797 | 797 | 797
HOST-SULP-230.0-1 | 5163 | HOMESTEAD SUBSTATION | XCEL | SULPHUR SUBSTATION | XCEL | 70513 | 70524 | Xcel Owned | HOST-SULP-230.0-1 | FACILITY |  | 1840 | 2000 | 2000 | 2000 | 733 | 797 | 797 | 797
HOST-SULP-230.0-1 | 5163 | HOMESTEAD SUBSTATION | XCEL | SULPHUR SUBSTATION | XCEL | 70513 | 70524 | Xcel Owned | Grosbeak | BUSBAR_SECTION | SULP | 1840 | 2025 | 2092 | 2301 | 733 | 807 | 833 | 917
HOST-SULP-230.0-1 | 5163 | HOMESTEAD SUBSTATION | XCEL | SULPHUR SUBSTATION | XCEL | 70513 | 70524 | Xcel Owned | 5163-6 | CIRCUIT_SWITCHER | HOST | 2000 | 2000 | 2000 | 2000 | 797 | 797 | 797 | 797
HSKY-WALT-230.0-1 | 55225 | HUSKY SUBSTATION | XCEL | AULT (WAPA) | FOREIGN | 70898 | 73011 | Jointly Owned | HSKY-WALT-230.0-1 | FACILITY |  | 1353 | 1353 | 1353 | 1353 | 539 | 539 | 539 | 539
HSKY-WALT-230.0-1 | 55225 | HUSKY SUBSTATION | XCEL | AULT (WAPA) | FOREIGN | 70898 | 73011 | Jointly Owned | Foreign Ratings | Foreign Ratings | WALT | 1353 | 1353 | 1353 | 1353 | 539 | 539 | 539 | 539
IDAH-LOOK-230.0-1 | 5005 | IDAHO SPRINGS SUBSTATION | XCEL | LOOKOUT SUBSTATION | XCEL | 70237 | 70266 | Xcel Owned | IDAH-LOOK-230.0-1 | FACILITY |  | 1188 | 1188 | 1255 | 1255 | 473 | 473 | 500 | 500
IDAH-LOOK-230.0-1 | 5005 | IDAHO SPRINGS SUBSTATION | XCEL | LOOKOUT SUBSTATION | XCEL | 70237 | 70266 | Xcel Owned |  | LINE_TRAP | LOOK | 1188 | 1188 | 1255 | 1255 | 473 | 473 | 500 | 500
IDAH-LOOK-230.0-1 | 5005 | IDAHO SPRINGS SUBSTATION | XCEL | LOOKOUT SUBSTATION | XCEL | 70237 | 70266 | Xcel Owned | Narcissus | BUSBAR_SECTION | IDAH | 1188 | 1394 | 1422 | 1590 | 473 | 555 | 567 | 633
JEWE-LEET-230.0-1 | 5285 | JEWELL SUBSTATION | XCEL | LEETSDALE SUBSTATION | XCEL | 70239 | 70260 | Xcel Owned | JEWE-LEET-230.0-1 | FACILITY |  | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
JEWE-LEET-230.0-1 | 5285 | JEWELL SUBSTATION | XCEL | LEETSDALE SUBSTATION | XCEL | 70239 | 70260 | Xcel Owned | 5285_50/69 | SECONDARY_CURRENT_LIMITATION | LEET | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
JEWE-LEET-230.0-1 | 5285 | JEWELL SUBSTATION | XCEL | LEETSDALE SUBSTATION | XCEL | 70239 | 70260 | Xcel Owned | 5285_67GP | SECONDARY_CURRENT_LIMITATION | LEET | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
JEWE-LEET-230.0-1 | 5285 | JEWELL SUBSTATION | XCEL | LEETSDALE SUBSTATION | XCEL | 70239 | 70260 | Xcel Owned | 5285_21ZP | SECONDARY_CURRENT_LIMITATION | LEET | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
JEWE-TOLL-230.0-1 | 5285 | JEWELL SUBSTATION | XCEL | TOLLGATE SUBSTATION | XCEL | 70239 | 70491 | Xcel Owned | JEWE-TOLL-230.0-1 | FACILITY |  | 1214 | 1393 | 1443 | 1587 | 484 | 555 | 575 | 632
JEWE-TOLL-230.0-1 | 5285 | JEWELL SUBSTATION | XCEL | TOLLGATE SUBSTATION | XCEL | 70239 | 70491 | Xcel Owned | Narcissus | BUSBAR_SECTION | TOLL | 1214 | 1421 | 1450 | 1619 | 484 | 566 | 578 | 645
JEWE-TOLL-230.0-1 | 5285 | JEWELL SUBSTATION | XCEL | TOLLGATE SUBSTATION | XCEL | 70239 | 70491 | Xcel Owned | JEWE-TOLL-230.0-1 | Transmission Line | 5285 | 1266 | 1393 | 1443 | 1587 | 504 | 555 | 575 | 632
JOHN-WELD-115.0-1 | 8365 | JOHNSTOWN SUBSTATION | XCEL | WELD SUBSTATION | XCEL | 70246 | 70470 | Xcel Owned | JOHN-WELD-115.0-1 | FACILITY |  | 939 | 1033 | 1068 | 1175 | 187 | 206 | 213 | 234
JOHN-WELD-115.0-1 | 8365 | JOHNSTOWN SUBSTATION | XCEL | WELD SUBSTATION | XCEL | 70246 | 70470 | Xcel Owned | Swift | BUSBAR_SECTION | JOHN | 939 | 1033 | 1068 | 1175 | 187 | 206 | 213 | 234
JORD-ORCH-230.0-1 | 5169 | JORDAN ROAD SUBSTATION | XCEL | ORCHARD SUBSTATION | XCEL | 70241 | 70313 | Xcel Owned | JORD-ORCH-230.0-1 | FACILITY |  | 1370 | 1562 | 1600 | 1600 | 546 | 622 | 637 | 637
JORD-ORCH-230.0-1 | 5169 | JORDAN ROAD SUBSTATION | XCEL | ORCHARD SUBSTATION | XCEL | 70241 | 70313 | Xcel Owned | 1/4 x 6 | BUSBAR_SECTION | ORCH | 1370 | 1742 | 1816 | 2100 | 546 | 694 | 724 | 837
JORD-ORCH-230.0-1 | 5169 | JORDAN ROAD SUBSTATION | XCEL | ORCHARD SUBSTATION | XCEL | 70241 | 70313 | Xcel Owned | Narcissus | BUSBAR_SECTION | JORD | 1420 | 1562 | 1618 | 1780 | 566 | 622 | 645 | 709
JORD-ORCH-230.0-1 | 5169 | JORDAN ROAD SUBSTATION | XCEL | ORCHARD SUBSTATION | XCEL | 70241 | 70313 | Xcel Owned | 5169-7S | CIRCUIT_SWITCHER | ORCH | 1600 | 1600 | 1600 | 1600 | 637 | 637 | 637 | 637
LAFA-PKWY-115.0-1 | 9481 | LAFAYETTE SUBSTATION | XCEL | PARKWAY (Tri State) | FOREIGN | 70244 | 70604 | Jointly Owned | LAFA-PKWY-115.0-1 | FACILITY |  | 1200 | 1200 | 1200 | 1200 | 239 | 239 | 239 | 239
LAFA-PKWY-115.0-1 | 9481 | LAFAYETTE SUBSTATION | XCEL | PARKWAY (Tri State) | FOREIGN | 70244 | 70604 | Jointly Owned | 9481-1 | CIRCUIT_SWITCHER | LAFA | 1200 | 1200 | 1200 | 1200 | 239 | 239 | 239 | 239
LAFA-PKWY-115.0-1 | 9481 | LAFAYETTE SUBSTATION | XCEL | PARKWAY (Tri State) | FOREIGN | 70244 | 70604 | Jointly Owned | Foreign Ratings | Foreign Ratings | PKWY | 1200 | 1461 | 1200 | 1461 | 239 | 291 | 239 | 291
LAFA-VALM-115.0-1 | 9481 | LAFAYETTE SUBSTATION | XCEL | VALMONT SWITCHYARD SUBSTATION | XCEL | 70244 | 70444 | Xcel Owned | LAFA-VALM-115.0-1 | FACILITY |  | 799 | 879 | 909 | 999 | 159 | 175 | 181 | 199
LAFA-VALM-115.0-1 | 9481 | LAFAYETTE SUBSTATION | XCEL | VALMONT SWITCHYARD SUBSTATION | XCEL | 70244 | 70444 | Xcel Owned | Grosbeak | BUSBAR_SECTION | LAFA | 799 | 879 | 909 | 999 | 159 | 175 | 181 | 199
LAKE-RIDG-115.0-1 | 9000 | LAKEWOOD SUBSTATION | XCEL | RIDGE SUBSTATION | XCEL | 70251 | 70354 | Xcel Owned | LAKE-RIDG-115.0-1 | FACILITY |  | 557 | 600 | 600 | 600 | 111 | 120 | 120 | 120
LAKE-RIDG-115.0-1 | 9000 | LAKEWOOD SUBSTATION | XCEL | RIDGE SUBSTATION | XCEL | 70251 | 70354 | Xcel Owned | 4/0 - 7 | BUSBAR_SECTION | LAKE | 557 | 613 | 640 | 704 | 111 | 122 | 127 | 140
LAKE-RIDG-115.0-1 | 9000 | LAKEWOOD SUBSTATION | XCEL | RIDGE SUBSTATION | XCEL | 70251 | 70354 | Xcel Owned | 9000_246X_67GP | SECONDARY_CURRENT_LIMITATION | RIDG | 600 | 600 | 600 | 600 | 120 | 120 | 120 | 120
LAKE-RIDG-115.0-1 | 9000 | LAKEWOOD SUBSTATION | XCEL | RIDGE SUBSTATION | XCEL | 70251 | 70354 | Xcel Owned | 9000_135Y_67GS | SECONDARY_CURRENT_LIMITATION | RIDG | 600 | 600 | 600 | 600 | 120 | 120 | 120 | 120
LAKE-RIDG-115.0-1 | 9000 | LAKEWOOD SUBSTATION | XCEL | RIDGE SUBSTATION | XCEL | 70251 | 70354 | Xcel Owned | 9000_246Y_METER_AMPSW | SECONDARY_CURRENT_LIMITATION | RIDG | 600 | 600 | 600 | 600 | 120 | 120 | 120 | 120
LAKE-RIDG-115.0-1 | 9000 | LAKEWOOD SUBSTATION | XCEL | RIDGE SUBSTATION | XCEL | 70251 | 70354 | Xcel Owned | 9000_246X_21ZP | SECONDARY_CURRENT_LIMITATION | RIDG | 600 | 600 | 600 | 600 | 120 | 120 | 120 | 120
LAKE-RIDG-115.0-1 | 9000 | LAKEWOOD SUBSTATION | XCEL | RIDGE SUBSTATION | XCEL | 70251 | 70354 | Xcel Owned | 9000_246X_PKG-BF | SECONDARY_CURRENT_LIMITATION | RIDG | 600 | 600 | 600 | 600 | 120 | 120 | 120 | 120
LAKE-RIDG-115.0-1 | 9000 | LAKEWOOD SUBSTATION | XCEL | RIDGE SUBSTATION | XCEL | 70251 | 70354 | Xcel Owned | 9000_246Y_METER_VAR | SECONDARY_CURRENT_LIMITATION | RIDG | 600 | 600 | 600 | 600 | 120 | 120 | 120 | 120
LAKE-RIDG-115.0-2 | 9005 | LAKEWOOD SUBSTATION | XCEL | RIDGE SUBSTATION | XCEL | 70252 | 70354 | Xcel Owned | LAKE-RIDG-115.0-2 | FACILITY |  | 557 | 600 | 600 | 600 | 111 | 120 | 120 | 120
LAKE-RIDG-115.0-2 | 9005 | LAKEWOOD SUBSTATION | XCEL | RIDGE SUBSTATION | XCEL | 70252 | 70354 | Xcel Owned | 4/0 - 7 | BUSBAR_SECTION | LAKE | 557 | 613 | 640 | 704 | 111 | 122 | 127 | 140
LAKE-RIDG-115.0-2 | 9005 | LAKEWOOD SUBSTATION | XCEL | RIDGE SUBSTATION | XCEL | 70252 | 70354 | Xcel Owned | 9005_246Y_METER_VAR | SECONDARY_CURRENT_LIMITATION | RIDG | 600 | 600 | 600 | 600 | 120 | 120 | 120 | 120
LAKE-RIDG-115.0-2 | 9005 | LAKEWOOD SUBSTATION | XCEL | RIDGE SUBSTATION | XCEL | 70252 | 70354 | Xcel Owned | 9005_135X_67GP | SECONDARY_CURRENT_LIMITATION | RIDG | 600 | 600 | 600 | 600 | 120 | 120 | 120 | 120
LAKE-RIDG-115.0-2 | 9005 | LAKEWOOD SUBSTATION | XCEL | RIDGE SUBSTATION | XCEL | 70252 | 70354 | Xcel Owned | 9005_135X_21ZP | SECONDARY_CURRENT_LIMITATION | RIDG | 600 | 600 | 600 | 600 | 120 | 120 | 120 | 120
LAKE-RIDG-115.0-2 | 9005 | LAKEWOOD SUBSTATION | XCEL | RIDGE SUBSTATION | XCEL | 70252 | 70354 | Xcel Owned | 9005_246Y_METER_AMPSW | SECONDARY_CURRENT_LIMITATION | RIDG | 600 | 600 | 600 | 600 | 120 | 120 | 120 | 120
LASS-LAMA-230.0-1 | 5513 | LAMAR 345KV SWITCHING STATION | XCEL | LAMAR (TRI-STATE) | FOREIGN | 70254 | 70560 | Jointly Owned | LASS-LAMA-230.0-1 | FACILITY |  | 1200 | 1448 | 1200 | 1464 | 478 | 577 | 478 | 583
LASS-LAMA-230.0-1 | 5513 | LAMAR 345KV SWITCHING STATION | XCEL | LAMAR (TRI-STATE) | FOREIGN | 70254 | 70560 | Jointly Owned | Foreign Ratings | Foreign Ratings | LAMA | 1200 | 1463 | 1200 | 1463 | 478 | 583 | 478 | 583
LASS-LAMA-230.0-1 | 5513 | LAMAR 345KV SWITCHING STATION | XCEL | LAMAR (TRI-STATE) | FOREIGN | 70254 | 70560 | Jointly Owned | Narcissus | BUSBAR_SECTION | LASS | 1241 | 1448 | 1481 | 1649 | 494 | 577 | 590 | 657
LEAD_TP1-MALT-115.0-1 | 9254 | LEADVILLE TAP 1 | XCEL | MALTA SUBSTATION | XCEL | 2114 | 70273 | Xcel Owned | LEAD_TP1-MALT-115.0-1 | FACILITY |  | 664 | 730 | 725 | 798 | 132 | 145 | 144 | 159
LEAD_TP1-MALT-115.0-1 | 9254 | LEADVILLE TAP 1 | XCEL | MALTA SUBSTATION | XCEL | 2114 | 70273 | Xcel Owned | LEAD_TP1-MALT-115.0-1 | Transmission Line | 9254 | 664 | 730 | 725 | 798 | 132 | 145 | 144 | 159
LEAD_TP2-LEAD-115.0-2 | 9257 | LEADVILLE TAP 2 | XCEL | LEADVILLE SUBSTATION | XCEL | 2155 | 70258 | Xcel Owned | LEAD_TP2-LEAD-115.0-2 | FACILITY |  | 477 | 554 | 567 | 629 | 95 | 110 | 113 | 125
LEAD_TP2-LEAD-115.0-2 | 9257 | LEADVILLE TAP 2 | XCEL | LEADVILLE SUBSTATION | XCEL | 2155 | 70258 | Xcel Owned | 4/0 - 7 | BUSBAR_SECTION | LEAD | 477 | 554 | 567 | 629 | 95 | 110 | 113 | 125
LEAD_TP2-ROBI-115.0-1 | 9257 | LEADVILLE TAP 2 | XCEL | ROBINSON RACK | XCEL | 2155 | 70364 | Xcel Owned | LEAD_TP2-ROBI-115.0-1 | FACILITY |  | 418 | 460 | 475 | 523 | 83 | 92 | 95 | 104
LEAD_TP2-ROBI-115.0-1 | 9257 | LEADVILLE TAP 2 | XCEL | ROBINSON RACK | XCEL | 2155 | 70364 | Xcel Owned | LEAD_TP2-ROBI-115.0-1 | Transmission Line | 9257 | 418 | 460 | 475 | 523 | 83 | 92 | 95 | 104
LEAD-MALT-115.0-1 | 9257 | LEADVILLE SUBSTATION | XCEL | MALTA SUBSTATION | XCEL | 70258 | 70273 | Xcel Owned | LEAD-MALT-115.0-1 | FACILITY |  | 477 | 554 | 567 | 629 | 95 | 110 | 113 | 125
LEAD-MALT-115.0-1 | 9257 | LEADVILLE SUBSTATION | XCEL | MALTA SUBSTATION | XCEL | 70258 | 70273 | Xcel Owned | 4/0 - 7 | BUSBAR_SECTION | LEAD | 477 | 554 | 567 | 629 | 95 | 110 | 113 | 125
LEET-MONR-230.0-1 | 5283 | LEETSDALE SUBSTATION | XCEL | MONROE SUBSTATION | XCEL | 70260 | 70291 | Xcel Owned | LEET-MONR-230.0-1 | FACILITY |  | 800 | 1000 | 1000 | 1000 | 319 | 398 | 398 | 398
LEET-MONR-230.0-1 | 5283 | LEETSDALE SUBSTATION | XCEL | MONROE SUBSTATION | XCEL | 70260 | 70291 | Xcel Owned | LEET-MONR-230.0-1 | Transmission Line | 5283 | 800 | 1000 | 1000 | 1000 | 319 | 398 | 398 | 398
LEET-SAND-115.0-1 | 9286 | LEETSDALE SUBSTATION | XCEL | SANDOWN SUBSTATION | XCEL | 70259 | 70377 | Xcel Owned | LEET-SAND-115.0-1 | FACILITY |  | 1213 | 1334 | 1213 | 1334 | 242 | 266 | 242 | 266
LEET-SAND-115.0-1 | 9286 | LEETSDALE SUBSTATION | XCEL | SANDOWN SUBSTATION | XCEL | 70259 | 70377 | Xcel Owned | LEET-SAND-115.0-1 | Transmission Line | 9286 | 1213 | 1334 | 1213 | 1334 | 242 | 266 | 242 | 266
LEET-SULL-230.0-1 | 5281 | LEETSDALE SUBSTATION | XCEL | SULLIVAN SUBSTATION | XCEL | 70260 | 70417 | Xcel Owned | LEET-SULL-230.0-1 | FACILITY |  | 1068 | 1068 | 1282 | 1282 | 425 | 425 | 511 | 511
LEET-SULL-230.0-1 | 5281 | LEETSDALE SUBSTATION | XCEL | SULLIVAN SUBSTATION | XCEL | 70260 | 70417 | Xcel Owned | LEET-SULL-230.0-1 | Transmission Line | 5281 | 1068 | 1068 | 1282 | 1282 | 425 | 425 | 511 | 511
LEET-UNIV-115.0-1 | 9338 | LEETSDALE SUBSTATION | XCEL | UNIVERSITY SUBSTATION | XCEL | 70259 | 70441 | Xcel Owned | LEET-UNIV-115.0-1 | FACILITY |  | 957 | 1052 | 1088 | 1197 | 191 | 210 | 217 | 238
LEET-UNIV-115.0-1 | 9338 | LEETSDALE SUBSTATION | XCEL | UNIVERSITY SUBSTATION | XCEL | 70259 | 70441 | Xcel Owned | LEET-UNIV-115.0-1 | Transmission Line | 9338 | 957 | 1052 | 1088 | 1197 | 191 | 210 | 217 | 238
LEGG-NIWO-230.0-1 | 5633 | LEGGETT SUBSTATION | XCEL | NIWOT SUBSTATION | XCEL | 70261 | 70297 | Xcel Owned | LEGG-NIWO-230.0-1 | FACILITY |  | 1188 | 1188 | 1200 | 1200 | 473 | 473 | 478 | 478
LEGG-NIWO-230.0-1 | 5633 | LEGGETT SUBSTATION | XCEL | NIWOT SUBSTATION | XCEL | 70261 | 70297 | Xcel Owned |  | LINE_TRAP | NIWO | 1188 | 1188 | 1255 | 1255 | 473 | 473 | 500 | 500
LEGG-NIWO-230.0-1 | 5633 | LEGGETT SUBSTATION | XCEL | NIWOT SUBSTATION | XCEL | 70261 | 70297 | Xcel Owned | 5633-1 | CIRCUIT_SWITCHER | LEGG | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
LEGG-PLEN-230.0-1 | 5633 | LEGGETT SUBSTATION | XCEL | PLAINS END SWITCHING STATION | XCEL | 70261 | 70570 | Xcel Owned | LEGG-PLEN-230.0-1 | FACILITY |  | 1188 | 1188 | 1200 | 1200 | 473 | 473 | 478 | 478
LEGG-PLEN-230.0-1 | 5633 | LEGGETT SUBSTATION | XCEL | PLAINS END SWITCHING STATION | XCEL | 70261 | 70570 | Xcel Owned |  | LINE_TRAP | PLEN | 1188 | 1188 | 1255 | 1255 | 473 | 473 | 500 | 500
LEGG-PLEN-230.0-1 | 5633 | LEGGETT SUBSTATION | XCEL | PLAINS END SWITCHING STATION | XCEL | 70261 | 70570 | Xcel Owned | 5633-2 | CIRCUIT_SWITCHER | LEGG | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
LITT-WATE-115.0-1 | 9336 | LITTLETON SUBSTATION | XCEL | WATERTON SUBSTATION | XCEL | 70263 | 70463 | Xcel Owned | LITT-WATE-115.0-1 | FACILITY |  | 796 | 875 | 905 | 995 | 159 | 174 | 180 | 198
LITT-WATE-115.0-1 | 9336 | LITTLETON SUBSTATION | XCEL | WATERTON SUBSTATION | XCEL | 70263 | 70463 | Xcel Owned | LITT-WATE-115.0-1 | Transmission Line | 9336 | 796 | 875 | 905 | 995 | 159 | 174 | 180 | 198
LITT-WATE-115.0-1 | 9336 | LITTLETON SUBSTATION | XCEL | WATERTON SUBSTATION | XCEL | 70263 | 70463 | Xcel Owned | Hawk | BUSBAR_SECTION | WATE | 796 | 876 | 905 | 996 | 159 | 174 | 180 | 198
LKGE-TARR-115.0-1 | 8384 | LAKE GEORGE | XCEL | TARRYALL SUBSTATION | XCEL | 70419 | 70426 | Xcel Owned | LKGE-TARR-115.0-1 | FACILITY |  | 1070 | 1177 | 1200 | 1200 | 213 | 235 | 239 | 239
LKGE-TARR-115.0-1 | 8384 | LAKE GEORGE | XCEL | TARRYALL SUBSTATION | XCEL | 70419 | 70426 | Xcel Owned | Drake | BUSBAR_SECTION | LKGE | 1070 | 1177 | 1220 | 1343 | 213 | 235 | 243 | 267
LKGE-TARR-115.0-1 | 8384 | LAKE GEORGE | XCEL | TARRYALL SUBSTATION | XCEL | 70419 | 70426 | Xcel Owned | 8384_135X_PK-2 | SECONDARY_CURRENT_LIMITATION | TARR | 1200 | 1200 | 1200 | 1200 | 239 | 239 | 239 | 239
LKGE-TARR-115.0-1 | 8384 | LAKE GEORGE | XCEL | TARRYALL SUBSTATION | XCEL | 70419 | 70426 | Xcel Owned | 8384 135X | CURRENT_TRANSFORMER | TARR | 1200 | 1200 | 1200 | 1200 | 239 | 239 | 239 | 239
LOOK-PLEN-230.0-1 | 5025 | LOOKOUT SUBSTATION | XCEL | PLAINS END SWITCHING STATION | XCEL | 70266 | 70570 | Xcel Owned | LOOK-PLEN-230.0-1 | FACILITY |  | 1194 | 1194 | 1382 | 1382 | 476 | 476 | 551 | 551
LOOK-PLEN-230.0-1 | 5025 | LOOKOUT SUBSTATION | XCEL | PLAINS END SWITCHING STATION | XCEL | 70266 | 70570 | Xcel Owned | LOOK-PLEN-230.0-1 | Transmission Line | 5025 | 1194 | 1194 | 1382 | 1382 | 476 | 476 | 551 | 551
LOOK-PLEN-230.0-2 | 5027 | LOOKOUT SUBSTATION | XCEL | PLAINS END SWITCHING STATION | XCEL | 70266 | 70570 | Xcel Owned | LOOK-PLEN-230.0-2 | FACILITY |  | 1261 | 1387 | 1429 | 1572 | 502 | 553 | 569 | 626
LOOK-PLEN-230.0-2 | 5027 | LOOKOUT SUBSTATION | XCEL | PLAINS END SWITCHING STATION | XCEL | 70266 | 70570 | Xcel Owned | LOOK-PLEN-230.0-2 | Transmission Line | 5027 | 1261 | 1387 | 1429 | 1572 | 502 | 553 | 569 | 626
LOOK-QUAK_TP-115.0-1 | 9122 | LOOKOUT SUBSTATION | XCEL | QUAKER TAP | XCEL | 70066 | 70342 | Xcel Owned | LOOK-QUAK_TP-115.0-1 | FACILITY |  | 1200 | 1200 | 1200 | 1200 | 239 | 239 | 239 | 239
LOOK-QUAK_TP-115.0-1 | 9122 | LOOKOUT SUBSTATION | XCEL | QUAKER TAP | XCEL | 70066 | 70342 | Xcel Owned | 9122_67GP | SECONDARY_CURRENT_LIMITATION | LOOK | 1200 | 1200 | 1200 | 1200 | 239 | 239 | 239 | 239
LOOK-QUAK_TP-115.0-1 | 9122 | LOOKOUT SUBSTATION | XCEL | QUAKER TAP | XCEL | 70066 | 70342 | Xcel Owned | 9122 135Y | CURRENT_TRANSFORMER | LOOK | 1200 | 1200 | 1200 | 1200 | 239 | 239 | 239 | 239
LOOK-QUAK_TP-115.0-1 | 9122 | LOOKOUT SUBSTATION | XCEL | QUAKER TAP | XCEL | 70066 | 70342 | Xcel Owned | 9122 246X | CURRENT_TRANSFORMER | LOOK | 1200 | 1200 | 1200 | 1200 | 239 | 239 | 239 | 239
LOOK-QUAK_TP-115.0-1 | 9122 | LOOKOUT SUBSTATION | XCEL | QUAKER TAP | XCEL | 70066 | 70342 | Xcel Owned | 9122_21ZP | SECONDARY_CURRENT_LIMITATION | LOOK | 1200 | 1200 | 1200 | 1200 | 239 | 239 | 239 | 239
LOOK-QUAK_TP-115.0-1 | 9122 | LOOKOUT SUBSTATION | XCEL | QUAKER TAP | XCEL | 70066 | 70342 | Xcel Owned | 9122 246Y | CURRENT_TRANSFORMER | LOOK | 1200 | 1200 | 1200 | 1200 | 239 | 239 | 239 | 239
LOOK-QUAK_TP-115.0-1 | 9122 | LOOKOUT SUBSTATION | XCEL | QUAKER TAP | XCEL | 70066 | 70342 | Xcel Owned | 9122 135X | CURRENT_TRANSFORMER | LOOK | 1200 | 1200 | 1200 | 1200 | 239 | 239 | 239 | 239
LOOK-QUAK_TP-115.0-1 | 9122 | LOOKOUT SUBSTATION | XCEL | QUAKER TAP | XCEL | 70066 | 70342 | Xcel Owned | 9122_METER_AMP | SECONDARY_CURRENT_LIMITATION | LOOK | 1200 | 1200 | 1200 | 1200 | 239 | 239 | 239 | 239
LOOK-RIDG-230.0-1 | 5029 | LOOKOUT SUBSTATION | XCEL | RIDGE SUBSTATION | XCEL | 70266 | 70355 | Xcel Owned | LOOK-RIDG-230.0-1 | FACILITY |  | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
LOOK-RIDG-230.0-1 | 5029 | LOOKOUT SUBSTATION | XCEL | RIDGE SUBSTATION | XCEL | 70266 | 70355 | Xcel Owned | 5029 21ZP | SECONDARY_CURRENT_LIMITATION | RIDG | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
LOOK-RIDG-230.0-1 | 5029 | LOOKOUT SUBSTATION | XCEL | RIDGE SUBSTATION | XCEL | 70266 | 70355 | Xcel Owned | L5029 METER AMPSW | SECONDARY_CURRENT_LIMITATION | RIDG | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
LOOK-RIDG-230.0-1 | 5029 | LOOKOUT SUBSTATION | XCEL | RIDGE SUBSTATION | XCEL | 70266 | 70355 | Xcel Owned | 5029_67GS | SECONDARY_CURRENT_LIMITATION | LOOK | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
LOOK-RIDG-230.0-1 | 5029 | LOOKOUT SUBSTATION | XCEL | RIDGE SUBSTATION | XCEL | 70266 | 70355 | Xcel Owned | 5029_21ZP | SECONDARY_CURRENT_LIMITATION | LOOK | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
LOOK-RIDG-230.0-1 | 5029 | LOOKOUT SUBSTATION | XCEL | RIDGE SUBSTATION | XCEL | 70266 | 70355 | Xcel Owned | 5029_67GP | SECONDARY_CURRENT_LIMITATION | LOOK | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
LOOK-RIDG-230.0-1 | 5029 | LOOKOUT SUBSTATION | XCEL | RIDGE SUBSTATION | XCEL | 70266 | 70355 | Xcel Owned | 5029_21Z1/2-A | SECONDARY_CURRENT_LIMITATION | LOOK | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
LOOK-RIDG-230.0-1 | 5029 | LOOKOUT SUBSTATION | XCEL | RIDGE SUBSTATION | XCEL | 70266 | 70355 | Xcel Owned | L5029 METER VAR | SECONDARY_CURRENT_LIMITATION | RIDG | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
LOOK-RIDG-230.0-1 | 5029 | LOOKOUT SUBSTATION | XCEL | RIDGE SUBSTATION | XCEL | 70266 | 70355 | Xcel Owned | 5029 67GS | SECONDARY_CURRENT_LIMITATION | RIDG | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
LOOK-RIDG-230.0-1 | 5029 | LOOKOUT SUBSTATION | XCEL | RIDGE SUBSTATION | XCEL | 70266 | 70355 | Xcel Owned | 5029_21Z1/2-C | SECONDARY_CURRENT_LIMITATION | LOOK | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
LOOK-RIDG-230.0-1 | 5029 | LOOKOUT SUBSTATION | XCEL | RIDGE SUBSTATION | XCEL | 70266 | 70355 | Xcel Owned | 5029_21Z1/2-B | SECONDARY_CURRENT_LIMITATION | LOOK | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
LOOK-RIDG-230.0-1 | 5029 | LOOKOUT SUBSTATION | XCEL | RIDGE SUBSTATION | XCEL | 70266 | 70355 | Xcel Owned | 5029 67GP | SECONDARY_CURRENT_LIMITATION | RIDG | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
LOOK-RIDG-230.0-1 | 5029 | LOOKOUT SUBSTATION | XCEL | RIDGE SUBSTATION | XCEL | 70266 | 70355 | Xcel Owned | 5029W | SWITCH | RIDG | 1200 | 1549 | 1486 | 1780 | 478 | 617 | 592 | 709
LOOK-RIDG-230.0-1 | 5029 | LOOKOUT SUBSTATION | XCEL | RIDGE SUBSTATION | XCEL | 70266 | 70355 | Xcel Owned | 5029E | SWITCH | RIDG | 1200 | 1549 | 1486 | 1780 | 478 | 617 | 592 | 709
LOOK-RIDG-230.0-1 | 5029 | LOOKOUT SUBSTATION | XCEL | RIDGE SUBSTATION | XCEL | 70266 | 70355 | Xcel Owned | 5062W | SWITCH | RIDG | 1200 | 1549 | 1486 | 1780 | 478 | 617 | 592 | 709
LOOK-RIDG-230.0-1 | 5029 | LOOKOUT SUBSTATION | XCEL | RIDGE SUBSTATION | XCEL | 70266 | 70355 | Xcel Owned | 5026S | SWITCH | LOOK | 1200 | 1549 | 1486 | 1780 | 478 | 617 | 592 | 709
LOOK-RIDG-230.0-1 | 5029 | LOOKOUT SUBSTATION | XCEL | RIDGE SUBSTATION | XCEL | 70266 | 70355 | Xcel Owned | 5029N | SWITCH | LOOK | 1200 | 1549 | 1486 | 1780 | 478 | 617 | 592 | 709
LOOK-RIDG-230.0-1 | 5029 | LOOKOUT SUBSTATION | XCEL | RIDGE SUBSTATION | XCEL | 70266 | 70355 | Xcel Owned | 5066W | SWITCH | RIDG | 1200 | 1549 | 1486 | 1780 | 478 | 617 | 592 | 709
LOOK-RIDG-230.0-1 | 5029 | LOOKOUT SUBSTATION | XCEL | RIDGE SUBSTATION | XCEL | 70266 | 70355 | Xcel Owned | 5066E | SWITCH | RIDG | 1200 | 1549 | 1486 | 1780 | 478 | 617 | 592 | 709
LOOK-RIDG-230.0-1 | 5029 | LOOKOUT SUBSTATION | XCEL | RIDGE SUBSTATION | XCEL | 70266 | 70355 | Xcel Owned | 5026N | SWITCH | LOOK | 1200 | 1549 | 1486 | 1780 | 478 | 617 | 592 | 709
LOOK-RIDG-230.0-1 | 5029 | LOOKOUT SUBSTATION | XCEL | RIDGE SUBSTATION | XCEL | 70266 | 70355 | Xcel Owned | 5029S | SWITCH | LOOK | 1200 | 1549 | 1486 | 1780 | 478 | 617 | 592 | 709
LOOK-WEST-230.0-1 | 5629 | LOOKOUT SUBSTATION | XCEL | WEST SUBSTATION | XCEL | 70266 | 70480 | Xcel Owned | LOOK-WEST-230.0-1 | FACILITY |  | 1016 | 1207 | 1227 | 1247 | 405 | 481 | 489 | 497
LOOK-WEST-230.0-1 | 5629 | LOOKOUT SUBSTATION | XCEL | WEST SUBSTATION | XCEL | 70266 | 70480 | Xcel Owned | Narcissus | BUSBAR_SECTION | WEST | 1016 | 1207 | 1227 | 1382 | 405 | 481 | 489 | 550
LOOK-WEST-230.0-1 | 5629 | LOOKOUT SUBSTATION | XCEL | WEST SUBSTATION | XCEL | 70266 | 70480 | Xcel Owned | LOOK-WEST-230.0-1 | Transmission Line | 5629 | 1247 | 1247 | 1247 | 1247 | 497 | 497 | 497 | 497
LOUI-VALM-115.0-1 | 9052 | LOUISVILLE SUBSTATION | XCEL | VALMONT SWITCHYARD SUBSTATION | XCEL | 70269 | 70444 | Xcel Owned | LOUI-VALM-115.0-1 | FACILITY |  | 961 | 1057 | 1106 | 1200 | 191 | 211 | 220 | 239
LOUI-VALM-115.0-1 | 9052 | LOUISVILLE SUBSTATION | XCEL | VALMONT SWITCHYARD SUBSTATION | XCEL | 70269 | 70444 | Xcel Owned | 500 - 37 | BUSBAR_SECTION | VALM | 961 | 1057 | 1106 | 1217 | 191 | 211 | 220 | 242
LOUI-VALM-115.0-1 | 9052 | LOUISVILLE SUBSTATION | XCEL | VALMONT SWITCHYARD SUBSTATION | XCEL | 70269 | 70444 | Xcel Owned | 9052 246X | CURRENT_TRANSFORMER | VALM | 1200 | 1200 | 1200 | 1200 | 239 | 239 | 239 | 239
LOUI-VALM-115.0-1 | 9052 | LOUISVILLE SUBSTATION | XCEL | VALMONT SWITCHYARD SUBSTATION | XCEL | 70269 | 70444 | Xcel Owned | 9052 135X | CURRENT_TRANSFORMER | VALM | 1200 | 1200 | 1200 | 1200 | 239 | 239 | 239 | 239
LOUI-VALM-115.0-1 | 9052 | LOUISVILLE SUBSTATION | XCEL | VALMONT SWITCHYARD SUBSTATION | XCEL | 70269 | 70444 | Xcel Owned | 9052 135Y | CURRENT_TRANSFORMER | VALM | 1200 | 1200 | 1200 | 1200 | 239 | 239 | 239 | 239
LOUI-VALM-115.0-1 | 9052 | LOUISVILLE SUBSTATION | XCEL | VALMONT SWITCHYARD SUBSTATION | XCEL | 70269 | 70444 | Xcel Owned | 9052 DFR | SECONDARY_CURRENT_LIMITATION | VALM | 1200 | 1200 | 1200 | 1200 | 239 | 239 | 239 | 239
LOUI-VALM-115.0-1 | 9052 | LOUISVILLE SUBSTATION | XCEL | VALMONT SWITCHYARD SUBSTATION | XCEL | 70269 | 70444 | Xcel Owned | 9052-1 | CIRCUIT_SWITCHER | LOUI | 1200 | 1200 | 1200 | 1200 | 239 | 239 | 239 | 239
LOUI-VALM-115.0-1 | 9052 | LOUISVILLE SUBSTATION | XCEL | VALMONT SWITCHYARD SUBSTATION | XCEL | 70269 | 70444 | Xcel Owned | 9052 246Y | CURRENT_TRANSFORMER | VALM | 1200 | 1200 | 1200 | 1200 | 239 | 239 | 239 | 239
LPNO_TP-ROSE-115.0-1 | 8265 | LEPRINO TAP | XCEL | ROSEDALE SUBSTATION | XCEL | 70805 | 70368 | Xcel Owned | LPNO_TP-ROSE-115.0-1 | FACILITY |  | 601 | 601 | 928 | 928 | 120 | 120 | 185 | 185
LPNO_TP-ROSE-115.0-1 | 8265 | LEPRINO TAP | XCEL | ROSEDALE SUBSTATION | XCEL | 70805 | 70368 | Xcel Owned | LPNO_TP-ROSE-115.0-1 | Transmission Line | 8265 | 601 | 601 | 928 | 928 | 120 | 120 | 185 | 185
LYDS_TP-PLNV_TP-115.0-1 | 9584 | LEYDEN SITE | XCEL | PLAINVIEW TAP | XCEL | 70262 | 70300 | Xcel Owned | LYDS_TP-PLNV_TP-115.0-1 | FACILITY |  | 793 | 873 | 900 | 990 | 158 | 174 | 179 | 197
LYDS_TP-PLNV_TP-115.0-1 | 9584 | LEYDEN SITE | XCEL | PLAINVIEW TAP | XCEL | 70262 | 70300 | Xcel Owned | LYDS_TP-PLNV_TP-115.0-1 | Transmission Line | 9584 | 793 | 873 | 900 | 990 | 158 | 174 | 179 | 197
LYDS_TP-RIDG-115.0-1 | 9584 | LEYDEN SITE | XCEL | RIDGE SUBSTATION | XCEL | 70262 | 70354 | Xcel Owned | LYDS_TP-RIDG-115.0-1 | FACILITY |  | 1264 | 1390 | 1440 | 1584 | 252 | 277 | 287 | 316
LYDS_TP-RIDG-115.0-1 | 9584 | LEYDEN SITE | XCEL | RIDGE SUBSTATION | XCEL | 70262 | 70354 | Xcel Owned | LYDS_TP-RIDG-115.0-1 | Transmission Line | 9584 | 1264 | 1390 | 1440 | 1584 | 252 | 277 | 287 | 316
MALT-BASA-230.0-1 | 5149 | MALTA SUBSTATION | XCEL | BASALT SUBSTATION | XCEL | 70274 | 79004 | Xcel Owned | MALT-BASA-230.0-1 | FACILITY |  | 900 | 900 | 900 | 900 | 359 | 359 | 359 | 359
MALT-BASA-230.0-1 | 5149 | MALTA SUBSTATION | XCEL | BASALT SUBSTATION | XCEL | 70274 | 79004 | Xcel Owned | 230 5149 C | CURRENT_TRANSFORMER | BASA | 900 | 900 | 900 | 900 | 359 | 359 | 359 | 359
MALT-BASA-230.0-1 | 5149 | MALTA SUBSTATION | XCEL | BASALT SUBSTATION | XCEL | 70274 | 79004 | Xcel Owned | 230 5149 A | CURRENT_TRANSFORMER | BASA | 900 | 900 | 900 | 900 | 359 | 359 | 359 | 359
MALT-BASA-230.0-1 | 5149 | MALTA SUBSTATION | XCEL | BASALT SUBSTATION | XCEL | 70274 | 79004 | Xcel Owned | 230 5149 B | CURRENT_TRANSFORMER | BASA | 900 | 900 | 900 | 900 | 359 | 359 | 359 | 359
MALT-HARS-230.0-1 | 5145 | MALTA SUBSTATION | XCEL | HARTSEL (CORE) | XCEL | 70274 | 70927 | Xcel Owned | MALT-HARS-230.0-1 | FACILITY |  | 1037 | 1188 | 1244 | 1255 | 413 | 473 | 496 | 500
MALT-HARS-230.0-1 | 5145 | MALTA SUBSTATION | XCEL | HARTSEL (CORE) | XCEL | 70274 | 70927 | Xcel Owned | Curlew | BUSBAR_SECTION | MALT | 1037 | 1215 | 1244 | 1387 | 413 | 484 | 496 | 553
MALT-HARS-230.0-1 | 5145 | MALTA SUBSTATION | XCEL | HARTSEL (CORE) | XCEL | 70274 | 70927 | Xcel Owned |  | LINE_TRAP | MALT | 1188 | 1188 | 1255 | 1255 | 473 | 473 | 500 | 500
MALT-TWLA_TP-115.0-1 | 9255 | MALTA SUBSTATION | XCEL | TWIN LAKES TAP | XCEL | 70273 | 70435 | Xcel Owned | MALT-TWLA_TP-115.0-1 | FACILITY | [9 empty] | See Ambient Adjusted Ratings Section
MAPL-CALI_TP-115.0-1 | 9547 | MAPLETON SUBSTATION | XCEL | CALIFORNIA TAP | XCEL | 70276 | 2050 | Xcel Owned | MAPL-CALI_TP-115.0-1 | FACILITY |  | 914 | 1005 | 914 | 1005 | 182 | 200 | 182 | 200
MAPL-CALI_TP-115.0-1 | 9547 | MAPLETON SUBSTATION | XCEL | CALIFORNIA TAP | XCEL | 70276 | 2050 | Xcel Owned | MAPL-CALI_TP-115.0-1 | Transmission Line | 9547 | 914 | 1005 | 914 | 1005 | 182 | 200 | 182 | 200
MAPL-SAND-115.0-1 | 9546 | MAPLETON SUBSTATION | XCEL | SANDOWN SUBSTATION | XCEL | 70277 | 70377 | Xcel Owned | MAPL-SAND-115.0-1 | FACILITY |  | 799 | 879 | 909 | 999 | 159 | 175 | 181 | 199
MAPL-SAND-115.0-1 | 9546 | MAPLETON SUBSTATION | XCEL | SANDOWN SUBSTATION | XCEL | 70277 | 70377 | Xcel Owned | MAPL-SAND-115.0-1 | Transmission Line | 9546 | 799 | 879 | 909 | 999 | 159 | 175 | 181 | 199
MARC-WATE-230.0-1 | 5085 | MARCY SUBSTATION | XCEL | WATERTON SUBSTATION | XCEL | 70278 | 70959 | Xcel Owned | MARC-WATE-230.0-1 | FACILITY |  | 1261 | 1387 | 1437 | 1580 | 502 | 553 | 572 | 629
MARC-WATE-230.0-1 | 5085 | MARCY SUBSTATION | XCEL | WATERTON SUBSTATION | XCEL | 70278 | 70959 | Xcel Owned | MARC-WATE-230.0-1 | Transmission Line | 5085 | 1261 | 1387 | 1437 | 1580 | 502 | 553 | 572 | 629
MAYF-SUMM-115.0-1 | 8189 | MAYFLOWER SUBSTATION | XCEL | SUMMIT SUBSTATION | XCEL | 70281 | 70421 | Xcel Owned | MAYF-SUMM-115.0-1 | FACILITY |  | 413 | 413 | 453 | 453 | 82 | 82 | 90 | 90
MAYF-SUMM-115.0-1 | 8189 | MAYFLOWER SUBSTATION | XCEL | SUMMIT SUBSTATION | XCEL | 70281 | 70421 | Xcel Owned | MAYF-SUMM-115.0-1 | Transmission Line | 8189 | 413 | 413 | 453 | 453 | 82 | 82 | 90 | 90
MEAD-ORCH-230.0-1 | 5169 | MEADOW HILLS SUBSTATION | XCEL | ORCHARD SUBSTATION | XCEL | 70283 | 70313 | Xcel Owned | MEAD-ORCH-230.0-1 | FACILITY |  | 1370 | 1559 | 1600 | 1600 | 546 | 621 | 637 | 637
MEAD-ORCH-230.0-1 | 5169 | MEADOW HILLS SUBSTATION | XCEL | ORCHARD SUBSTATION | XCEL | 70283 | 70313 | Xcel Owned | 1/4 x 6 | BUSBAR_SECTION | ORCH | 1370 | 1742 | 1816 | 2100 | 546 | 694 | 724 | 837
MEAD-ORCH-230.0-1 | 5169 | MEADOW HILLS SUBSTATION | XCEL | ORCHARD SUBSTATION | XCEL | 70283 | 70313 | Xcel Owned | Narcissus | BUSBAR_SECTION | MEAD | 1417 | 1559 | 1616 | 1777 | 565 | 621 | 644 | 708
MEAD-ORCH-230.0-1 | 5169 | MEADOW HILLS SUBSTATION | XCEL | ORCHARD SUBSTATION | XCEL | 70283 | 70313 | Xcel Owned | 5169-5N | CIRCUIT_SWITCHER | ORCH | 1600 | 1600 | 1600 | 1600 | 637 | 637 | 637 | 637
MEAD-ORCH-230.0-1 | 5169 | MEADOW HILLS SUBSTATION | XCEL | ORCHARD SUBSTATION | XCEL | 70283 | 70313 | Xcel Owned | 5169-2 | CIRCUIT_SWITCHER | MEAD | 1600 | 1600 | 1600 | 1600 | 637 | 637 | 637 | 637
MEAD-SMOK-230.0-1 | 5169 | MEADOW HILLS SUBSTATION | XCEL | SMOKY HILL SUBSTATION | XCEL | 70283 | 70396 | Xcel Owned | MEAD-SMOK-230.0-1 | FACILITY |  | 1417 | 1558 | 1615 | 1673 | 564 | 621 | 643 | 666
MEAD-SMOK-230.0-1 | 5169 | MEADOW HILLS SUBSTATION | XCEL | SMOKY HILL SUBSTATION | XCEL | 70283 | 70396 | Xcel Owned | Narcissus | BUSBAR_SECTION | SMOK | 1417 | 1558 | 1615 | 1776 | 564 | 621 | 643 | 708
MEAD-SMOK-230.0-1 | 5169 | MEADOW HILLS SUBSTATION | XCEL | SMOKY HILL SUBSTATION | XCEL | 70283 | 70396 | Xcel Owned | Narcissus | BUSBAR_SECTION | MEAD | 1417 | 1559 | 1616 | 1777 | 565 | 621 | 644 | 708
MEAD-SMOK-230.0-1 | 5169 | MEADOW HILLS SUBSTATION | XCEL | SMOKY HILL SUBSTATION | XCEL | 70283 | 70396 | Xcel Owned |  | LINE_TRAP | SMOK | 1584 | 1584 | 1673 | 1673 | 631 | 631 | 666 | 666
METO-THTN-115.0-1 | 9737 | METRO | XCEL | THORNTON | XCEL | 70494 | 70099 | Xcel Owned | METO-THTN-115.0-1 | FACILITY |  | 800 | 880 | 910 | 1001 | 159 | 175 | 181 | 199
METO-THTN-115.0-1 | 9737 | METRO | XCEL | THORNTON | XCEL | 70494 | 70099 | Xcel Owned | METO-THTN-115.0-1 | Transmission Line | 9737 | 800 | 880 | 910 | 1001 | 159 | 175 | 181 | 199
MIDW-JFUL-230.0-1 | 5129 | MIDWAY SUBSTATION | XCEL | JACKSON FULLER SUBSTATION | XCEL | 70286 | 73477 | Xcel Owned | MIDW-JFUL-230.0-1 | FACILITY |  | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
MIDW-JFUL-230.0-1 | 5129 | MIDWAY SUBSTATION | XCEL | JACKSON FULLER SUBSTATION | XCEL | 70286 | 73477 | Xcel Owned | 5129_W_VAR_XDCR_230KV | SECONDARY_CURRENT_LIMITATION | MIDW | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
MIDW-JFUL-230.0-1 | 5129 | MIDWAY SUBSTATION | XCEL | JACKSON FULLER SUBSTATION | XCEL | 70286 | 73477 | Xcel Owned | 5129_AM_230KV | SECONDARY_CURRENT_LIMITATION | MIDW | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
MIDW-JFUL-230.0-1 | 5129 | MIDWAY SUBSTATION | XCEL | JACKSON FULLER SUBSTATION | XCEL | 70286 | 73477 | Xcel Owned | 5129_A_XDCR_230KV | SECONDARY_CURRENT_LIMITATION | MIDW | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
MIDW-MDWW-230.0-1 | BUS | MIDWAY SUBSTATION | XCEL | MIDWAY (WAPA) SUBSTATION | FOREIGN | 70286 | 73413 | Jointly Owned | MIDW-MDWW-230.0-1 | FACILITY |  | 1600 | 1600 | 1600 | 1600 | 637 | 637 | 637 | 637
MIDW-MDWW-230.0-1 | BUS | MIDWAY SUBSTATION | XCEL | MIDWAY (WAPA) SUBSTATION | FOREIGN | 70286 | 73413 | Jointly Owned | 5120 | BREAKER | MIDW | 1600 | 1600 | 1600 | 1600 | 637 | 637 | 637 | 637
MIDW-MSOL-230.0-1 | 55255 | MIDWAY SUBSTATION | XCEL | MIRASOL SUBSTATION | XCEL | 70286 | 70652 | Xcel Owned | MIDW-MSOL-230.0-1 | FACILITY |  | 1267 | 1393 | 1443 | 1587 | 505 | 555 | 575 | 632
MIDW-MSOL-230.0-1 | 55255 | MIDWAY SUBSTATION | XCEL | MIRASOL SUBSTATION | XCEL | 70286 | 70652 | Xcel Owned | MIDW-MSOL-230.0-1 | Transmission Line | 55255 | 1267 | 1393 | 1443 | 1587 | 505 | 555 | 575 | 632
MIDW-WATE-345.0-1 | 7051 | MIDWAY SUBSTATION | XCEL | WATERTON SUBSTATION | XCEL | 70465 | 70466 | Xcel Owned | MIDW-WATE-345.0-1 | FACILITY |  | 1980 | 1980 | 2091 | 2091 | 1183 | 1183 | 1249 | 1249
MIDW-WATE-345.0-1 | 7051 | MIDWAY SUBSTATION | XCEL | WATERTON SUBSTATION | XCEL | 70465 | 70466 | Xcel Owned |  | LINE_TRAP | WATE | 1980 | 1980 | 2091 | 2091 | 1183 | 1183 | 1249 | 1249
MIDW-WATE-345.0-1 | 7051 | MIDWAY SUBSTATION | XCEL | WATERTON SUBSTATION | XCEL | 70465 | 70466 | Xcel Owned |  | LINE_TRAP | MIDW | 1980 | 1980 | 2091 | 2091 | 1183 | 1183 | 1249 | 1249
MILL-PORT-115.0-1 | 8054 | MILL SUBSTATION | XCEL | PORTAL SUBSTATION | XCEL | 70287 | 70328 | Jointly Owned | MILL-PORT-115.0-1 | FACILITY |  | 600 | 775 | 743 | 890 | 120 | 154 | 148 | 177
MILL-PORT-115.0-1 | 8054 | MILL SUBSTATION | XCEL | PORTAL SUBSTATION | XCEL | 70287 | 70328 | Jointly Owned | 8054-1M | SWITCH | PORT | 600 | 775 | 743 | 890 | 120 | 154 | 148 | 177
MNGL-PLEN-230.0-1 | 5389 | MOON GULCH SUBSTATION | XCEL | PLAINS END SWITCHING STATION | XCEL | 70574 | 70570 | Xcel Owned | MNGL-PLEN-230.0-1 | FACILITY |  | 1271 | 1398 | 1435 | 1579 | 506 | 557 | 572 | 629
MNGL-PLEN-230.0-1 | 5389 | MOON GULCH SUBSTATION | XCEL | PLAINS END SWITCHING STATION | XCEL | 70574 | 70570 | Xcel Owned | MNGL-PLEN-230.0-1 | Transmission Line | 5389 | 1271 | 1398 | 1435 | 1579 | 506 | 557 | 572 | 629
MNGL-SIMM-230.0-1 | 5389 | MOON GULCH SUBSTATION | XCEL | SIMMS SUBSTATION | XCEL | 70574 | 70543 | Xcel Owned | MNGL-SIMM-230.0-1 | FACILITY |  | 1214 | 1387 | 1435 | 1579 | 483 | 553 | 572 | 629
MNGL-SIMM-230.0-1 | 5389 | MOON GULCH SUBSTATION | XCEL | SIMMS SUBSTATION | XCEL | 70574 | 70543 | Xcel Owned | Narcissus | BUSBAR_SECTION | SIMM | 1214 | 1420 | 1450 | 1619 | 483 | 566 | 578 | 645
MNGL-SIMM-230.0-1 | 5389 | MOON GULCH SUBSTATION | XCEL | SIMMS SUBSTATION | XCEL | 70574 | 70543 | Xcel Owned | MNGL-SIMM-230.0-1 | Transmission Line | 5389 | 1261 | 1387 | 1435 | 1579 | 502 | 553 | 572 | 629
MONA-GREE-230.0-2 | 5705 | MONACO SUBSTATION | XCEL | GREENWOOD SUBSTATION | XCEL | 70481 | 70212 | Xcel Owned | MONA-GREE-230.0-2 | FACILITY |  | 1017 | 1180 | 1180 | 1180 | 405 | 470 | 470 | 470
MONA-GREE-230.0-2 | 5705 | MONACO SUBSTATION | XCEL | GREENWOOD SUBSTATION | XCEL | 70481 | 70212 | Xcel Owned | Narcissus | BUSBAR_SECTION | MONA | 1017 | 1208 | 1228 | 1383 | 405 | 481 | 489 | 551
MONA-GREE-230.0-2 | 5705 | MONACO SUBSTATION | XCEL | GREENWOOD SUBSTATION | XCEL | 70481 | 70212 | Xcel Owned | MONA-GREE-230.0-2 | Transmission Line | 5705 | 1180 | 1180 | 1180 | 1180 | 470 | 470 | 470 | 470
MONA-SULL-230.0-1 | 5717 | MONACO SUBSTATION | XCEL | SULLIVAN SUBSTATION | XCEL | 70481 | 70417 | Xcel Owned | MONA-SULL-230.0-1 | FACILITY |  | 1117 | 1117 | 1316 | 1316 | 445 | 445 | 524 | 524
MONA-SULL-230.0-1 | 5717 | MONACO SUBSTATION | XCEL | SULLIVAN SUBSTATION | XCEL | 70481 | 70417 | Xcel Owned | MONA-SULL-230.0-1 | Transmission Line | 5717 | 1117 | 1117 | 1316 | 1316 | 445 | 445 | 524 | 524
MONA-TECH-230.0-1 | 5705 | MONACO SUBSTATION | XCEL | TECH CENTER SUBSTATION | XCEL | 70481 | 70428 | Xcel Owned | MONA-TECH-230.0-1 | FACILITY |  | 1017 | 1208 | 1180 | 1298 | 405 | 481 | 470 | 517
MONA-TECH-230.0-1 | 5705 | MONACO SUBSTATION | XCEL | TECH CENTER SUBSTATION | XCEL | 70481 | 70428 | Xcel Owned | Narcissus | BUSBAR_SECTION | MONA | 1017 | 1208 | 1228 | 1383 | 405 | 481 | 489 | 551
MONA-TECH-230.0-1 | 5705 | MONACO SUBSTATION | XCEL | TECH CENTER SUBSTATION | XCEL | 70481 | 70428 | Xcel Owned | MONA-TECH-230.0-1 | Transmission Line | 5705 | 1180 | 1298 | 1180 | 1298 | 470 | 517 | 470 | 517
MONF-DCPL_TP-115.0-1 | 8266 | MONFORT SUBSTATION | XCEL | DCP LUCERNE | FOREIGN | 70290 | 2133 | Xcel Owned | MONF-DCPL_TP-115.0-1 | FACILITY |  | 1110 | 1221 | 1264 | 1390 | 221 | 243 | 252 | 277
MONF-DCPL_TP-115.0-1 | 8266 | MONFORT SUBSTATION | XCEL | DCP LUCERNE | FOREIGN | 70290 | 2133 | Xcel Owned | MONF-DCPL_TP-115.0-1 | Transmission Line | 8266 | 1110 | 1221 | 1264 | 1390 | 221 | 243 | 252 | 277
MONF-DCPL_TP-115.0-1 | 8266 | MONFORT SUBSTATION | XCEL | DCP LUCERNE | FOREIGN | 70290 | 2133 | Xcel Owned | Drake | BUSBAR_SECTION | MONF | 1111 | 1222 | 1264 | 1391 | 221 | 243 | 252 | 277
MONF-LPNO_TP-115.0-1 | 8265 | MONFORT SUBSTATION | XCEL | LEPRINO TAP | XCEL | 70290 | 70805 | Xcel Owned | MONF-LPNO_TP-115.0-1 | FACILITY |  | 924 | 1075 | 1099 | 1200 | 184 | 214 | 219 | 239
MONF-LPNO_TP-115.0-1 | 8265 | MONFORT SUBSTATION | XCEL | LEPRINO TAP | XCEL | 70290 | 70805 | Xcel Owned | Arbutus | BUSBAR_SECTION | MONF | 924 | 1075 | 1099 | 1223 | 184 | 214 | 219 | 244
MONF-LPNO_TP-115.0-1 | 8265 | MONFORT SUBSTATION | XCEL | LEPRINO TAP | XCEL | 70290 | 70805 | Xcel Owned | 8265 135Y | CURRENT_TRANSFORMER | MONF | 1200 | 1200 | 1200 | 1200 | 239 | 239 | 239 | 239
MONF-LPNO_TP-115.0-1 | 8265 | MONFORT SUBSTATION | XCEL | LEPRINO TAP | XCEL | 70290 | 70805 | Xcel Owned | 8265 135X | CURRENT_TRANSFORMER | MONF | 1200 | 1200 | 1200 | 1200 | 239 | 239 | 239 | 239
MONF-LPNO_TP-115.0-1 | 8265 | MONFORT SUBSTATION | XCEL | LEPRINO TAP | XCEL | 70290 | 70805 | Xcel Owned | 8265 246Y | CURRENT_TRANSFORMER | MONF | 1200 | 1200 | 1200 | 1200 | 239 | 239 | 239 | 239
MSST-PRHN-345.0-1 | 7107 | MISSILE SITE | XCEL | PRONGHORN | XCEL | 70624 | 70628 | Xcel Owned | MSST-PRHN-345.0-1 | FACILITY |  | 2425 | 2740 | 2740 | 2740 | 1449 | 1637 | 1637 | 1637
MSST-PRHN-345.0-1 | 7107 | MISSILE SITE | XCEL | PRONGHORN | XCEL | 70624 | 70628 | Xcel Owned | Narcissus | BUSBAR_SECTION | MSST | 2425 | 2838 | 2897 | 3233 | 1449 | 1696 | 1731 | 1932
MSST-PRHN-345.0-1 | 7107 | MISSILE SITE | XCEL | PRONGHORN | XCEL | 70624 | 70628 | Xcel Owned | MSST-PRHN-345.0-1 | Transmission Line | 7107 | 2740 | 2740 | 2740 | 2740 | 1637 | 1637 | 1637 | 1637
MTHR-HAYD-138.0-1 | 3003 | MT. HARRIS SUBSTATION | XCEL | HAYDEN (WAPA) | FOREIGN | 70525 | 79038 | Xcel Owned | MTHR-HAYD-138.0-1 | FACILITY |  | 301 | 301 | 301 | 301 | 72 | 72 | 72 | 72
MTHR-HAYD-138.0-1 | 3003 | MT. HARRIS SUBSTATION | XCEL | HAYDEN (WAPA) | FOREIGN | 70525 | 79038 | Xcel Owned | Foreign Ratings | Foreign Ratings | HAYD | 301 | 301 | 301 | 301 | 72 | 72 | 72 | 72
NIWO-ISAB-230.0-1 | 5637 | NIWOT SUBSTATION | XCEL | ISABELLE SUBSTATION | XCEL | 70297 | 70544 | Xcel Owned | NIWO-ISAB-230.0-1 | FACILITY |  | 1219 | 1426 | 1456 | 1625 | 486 | 568 | 580 | 647
NIWO-ISAB-230.0-1 | 5637 | NIWOT SUBSTATION | XCEL | ISABELLE SUBSTATION | XCEL | 70297 | 70544 | Xcel Owned | Narcissus | BUSBAR_SECTION | NIWO | 1219 | 1426 | 1456 | 1625 | 486 | 568 | 580 | 647
NORT-CHER-115.0-1 | 9541 | NORTH SUBSTATION | XCEL | CHEROKEE SWITCHYARD SUBSTATION | XCEL | 70298 | 70108 | Xcel Owned | NORT-CHER-115.0-1 | FACILITY |  | 1001 | 1101 | 1139 | 1200 | 199 | 219 | 227 | 239
NORT-CHER-115.0-1 | 9541 | NORTH SUBSTATION | XCEL | CHEROKEE SWITCHYARD SUBSTATION | XCEL | 70298 | 70108 | Xcel Owned | NORT-CHER-115.0-1 | Transmission Line | 9541 | 1001 | 1101 | 1139 | 1253 | 199 | 219 | 227 | 250
NORT-CHER-115.0-1 | 9541 | NORTH SUBSTATION | XCEL | CHEROKEE SWITCHYARD SUBSTATION | XCEL | 70298 | 70108 | Xcel Owned | Violet | BUSBAR_SECTION | NORT | 1001 | 1101 | 1139 | 1253 | 199 | 219 | 227 | 250
NORT-CHER-115.0-1 | 9541 | NORTH SUBSTATION | XCEL | CHEROKEE SWITCHYARD SUBSTATION | XCEL | 70298 | 70108 | Xcel Owned | 9304 135X | CURRENT_TRANSFORMER | NORT | 1200 | 1200 | 1200 | 1200 | 239 | 239 | 239 | 239
NORT-CHER-115.0-1 | 9541 | NORTH SUBSTATION | XCEL | CHEROKEE SWITCHYARD SUBSTATION | XCEL | 70298 | 70108 | Xcel Owned | 9309 135X | CURRENT_TRANSFORMER | NORT | 1200 | 1200 | 1200 | 1200 | 239 | 239 | 239 | 239
NORT-CHER-115.0-1 | 9541 | NORTH SUBSTATION | XCEL | CHEROKEE SWITCHYARD SUBSTATION | XCEL | 70298 | 70108 | Xcel Owned | 9309 246X | CURRENT_TRANSFORMER | NORT | 1200 | 1200 | 1200 | 1200 | 239 | 239 | 239 | 239
NORT-CHER-115.0-1 | 9541 | NORTH SUBSTATION | XCEL | CHEROKEE SWITCHYARD SUBSTATION | XCEL | 70298 | 70108 | Xcel Owned | 9304 246X | CURRENT_TRANSFORMER | NORT | 1200 | 1200 | 1200 | 1200 | 239 | 239 | 239 | 239
NORT-CHER-115.0-1 | 9541 | NORTH SUBSTATION | XCEL | CHEROKEE SWITCHYARD SUBSTATION | XCEL | 70298 | 70108 | Xcel Owned | 9300_135X_XDCR_AMP | SECONDARY_CURRENT_LIMITATION | NORT | 1200 | 1200 | 1200 | 1200 | 239 | 239 | 239 | 239
NORT-CHER-115.0-1 | 9541 | NORTH SUBSTATION | XCEL | CHEROKEE SWITCHYARD SUBSTATION | XCEL | 70298 | 70108 | Xcel Owned | 9309 246Y | CURRENT_TRANSFORMER | NORT | 1200 | 1200 | 1200 | 1200 | 239 | 239 | 239 | 239
NORT-CHER-115.0-1 | 9541 | NORTH SUBSTATION | XCEL | CHEROKEE SWITCHYARD SUBSTATION | XCEL | 70298 | 70108 | Xcel Owned | 9304 135Y | CURRENT_TRANSFORMER | NORT | 1200 | 1200 | 1200 | 1200 | 239 | 239 | 239 | 239
NORT-CHER-115.0-1 | 9541 | NORTH SUBSTATION | XCEL | CHEROKEE SWITCHYARD SUBSTATION | XCEL | 70298 | 70108 | Xcel Owned | 9304 246Y | CURRENT_TRANSFORMER | NORT | 1200 | 1200 | 1200 | 1200 | 239 | 239 | 239 | 239
NORT-CHER-115.0-1 | 9541 | NORTH SUBSTATION | XCEL | CHEROKEE SWITCHYARD SUBSTATION | XCEL | 70298 | 70108 | Xcel Owned | 9300_135X_XDCR_WVAR | SECONDARY_CURRENT_LIMITATION | NORT | 1200 | 1200 | 1200 | 1200 | 239 | 239 | 239 | 239
NORT-CHER-115.0-1 | 9541 | NORTH SUBSTATION | XCEL | CHEROKEE SWITCHYARD SUBSTATION | XCEL | 70298 | 70108 | Xcel Owned | 9309 135Y | CURRENT_TRANSFORMER | NORT | 1200 | 1200 | 1200 | 1200 | 239 | 239 | 239 | 239
NORT-SAND-115.0-1 | 9311 | NORTH SUBSTATION | XCEL | SANDOWN SUBSTATION | XCEL | 70298 | 70377 | Xcel Owned | NORT-SAND-115.0-1 | FACILITY |  | 958 | 1054 | 1090 | 1199 | 191 | 210 | 217 | 239
NORT-SAND-115.0-1 | 9311 | NORTH SUBSTATION | XCEL | SANDOWN SUBSTATION | XCEL | 70298 | 70377 | Xcel Owned | NORT-SAND-115.0-1 | Transmission Line | 9311 | 958 | 1054 | 1090 | 1199 | 191 | 210 | 217 | 239
NREL-PLNV_TP-115.0-1 | 9584 | NREL | XCEL | PLAINVIEW TAP | XCEL | 70170 | 70300 | Xcel Owned | NREL-PLNV_TP-115.0-1 | FACILITY |  | 798 | 878 | 900 | 990 | 159 | 175 | 179 | 197
NREL-PLNV_TP-115.0-1 | 9584 | NREL | XCEL | PLAINVIEW TAP | XCEL | 70170 | 70300 | Xcel Owned | NREL-PLNV_TP-115.0-1 | Transmission Line | 9584 | 798 | 878 | 900 | 990 | 159 | 175 | 179 | 197
OTER_TP-BUVI_TP-115.0-1 | 9255 | OTERO PUMPING STATION | XCEL | BUENA VISTA TAP | XCEL | 70304 | 70056 | Xcel Owned | OTER_TP-BUVI_TP-115.0-1 | FACILITY | [9 empty] | See Ambient Adjusted Ratings Section
PARA_TP-PARA-230.0-1 | 5503 | PARACHUTE TAP | XCEL | PARACHUTE SUBSTATION | XCEL | 2143 | 70309 | Xcel Owned | PARA_TP-PARA-230.0-1 | FACILITY |  | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
PARA_TP-PARA-230.0-1 | 5503 | PARACHUTE TAP | XCEL | PARACHUTE SUBSTATION | XCEL | 2143 | 70309 | Xcel Owned | 5501_135X_PK | SECONDARY_CURRENT_LIMITATION | PARA | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
PARA_TP-PARA-230.0-1 | 5503 | PARACHUTE TAP | XCEL | PARACHUTE SUBSTATION | XCEL | 2143 | 70309 | Xcel Owned | 55160_246X_PK | SECONDARY_CURRENT_LIMITATION | PARA | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
PARA_TP-UTER-230.0-1 | 5503 | PARACHUTE TAP | XCEL | RIFLE UTE 230/345KV SUBSTATION | XCEL | 2143 | 79057 | Xcel Owned | PARA_TP-UTER-230.0-1 | FACILITY |  | 1423 | 1565 | 1611 | 1772 | 567 | 623 | 642 | 706
PARA_TP-UTER-230.0-1 | 5503 | PARACHUTE TAP | XCEL | RIFLE UTE 230/345KV SUBSTATION | XCEL | 2143 | 79057 | Xcel Owned | Narcissus | BUSBAR_SECTION | UTER | 1423 | 1565 | 1621 | 1783 | 567 | 623 | 646 | 710
PARA_TP-UTER-230.0-1 | 5503 | PARACHUTE TAP | XCEL | RIFLE UTE 230/345KV SUBSTATION | XCEL | 2143 | 79057 | Xcel Owned | PARA_TP-UTER-230.0-1 | Transmission Line | 5503 | 1434 | 1578 | 1611 | 1772 | 571 | 629 | 642 | 706
PARA-RIFL-230.0-1 | 5205 | PARACHUTE SUBSTATION | XCEL | RIFLE 230KV SUBSTATION (PSCO) | XCEL | 70309 | 70358 | Xcel Owned | PARA-RIFL-230.0-1 | FACILITY |  | 1085 | 1188 | 1200 | 1200 | 432 | 473 | 478 | 478
PARA-RIFL-230.0-1 | 5205 | PARACHUTE SUBSTATION | XCEL | RIFLE 230KV SUBSTATION (PSCO) | XCEL | 70309 | 70358 | Xcel Owned | Curlew | BUSBAR_SECTION | RIFL | 1085 | 1265 | 1296 | 1441 | 432 | 504 | 516 | 574
PARA-RIFL-230.0-1 | 5205 | PARACHUTE SUBSTATION | XCEL | RIFLE 230KV SUBSTATION (PSCO) | XCEL | 70309 | 70358 | Xcel Owned |  | LINE_TRAP | PARA | 1188 | 1188 | 1255 | 1255 | 473 | 473 | 500 | 500
PARA-RIFL-230.0-1 | 5205 | PARACHUTE SUBSTATION | XCEL | RIFLE 230KV SUBSTATION (PSCO) | XCEL | 70309 | 70358 | Xcel Owned |  | LINE_TRAP | RIFL | 1188 | 1188 | 1255 | 1255 | 473 | 473 | 500 | 500
PARA-RIFL-230.0-1 | 5205 | PARACHUTE SUBSTATION | XCEL | RIFLE 230KV SUBSTATION (PSCO) | XCEL | 70309 | 70358 | Xcel Owned | 5205 246Y | CURRENT_TRANSFORMER | RIFL | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
PARA-RIFL-230.0-1 | 5205 | PARACHUTE SUBSTATION | XCEL | RIFLE 230KV SUBSTATION (PSCO) | XCEL | 70309 | 70358 | Xcel Owned | 5205 135X | CURRENT_TRANSFORMER | RIFL | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
PARA-RIFL-230.0-1 | 5205 | PARACHUTE SUBSTATION | XCEL | RIFLE 230KV SUBSTATION (PSCO) | XCEL | 70309 | 70358 | Xcel Owned | 5205 246X | CURRENT_TRANSFORMER | RIFL | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
PARA-RIFL-230.0-1 | 5205 | PARACHUTE SUBSTATION | XCEL | RIFLE 230KV SUBSTATION (PSCO) | XCEL | 70309 | 70358 | Xcel Owned | 5205 135Y | CURRENT_TRANSFORMER | RIFL | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
PAWN-BRIC-230.0-1 | 5467 | PAWNEE 345KV | XCEL | BRICK CENTER | XCEL | 70311 | 70545 | Xcel Owned | PAWN-BRIC-230.0-1 | FACILITY |  | 1813 | 1813 | 1920 | 1920 | 722 | 722 | 765 | 765
PAWN-BRIC-230.0-1 | 5467 | PAWNEE 345KV | XCEL | BRICK CENTER | XCEL | 70311 | 70545 | Xcel Owned | PAWN-BRIC-230.0-1 | Transmission Line | 5467 | 1813 | 1813 | 2094 | 2094 | 722 | 722 | 834 | 834
PAWN-BRIC-230.0-1 | 5467 | PAWNEE 345KV | XCEL | BRICK CENTER | XCEL | 70311 | 70545 | Xcel Owned | 5467_246X_PKG-BF | SECONDARY_CURRENT_LIMITATION | PAWN | 1920 | 1920 | 1920 | 1920 | 765 | 765 | 765 | 765
PAWN-BRIC-230.0-1 | 5467 | PAWNEE 345KV | XCEL | BRICK CENTER | XCEL | 70311 | 70545 | Xcel Owned | TL5467_50/69S | SECONDARY_CURRENT_LIMITATION | PAWN | 1920 | 1920 | 1920 | 1920 | 765 | 765 | 765 | 765
PAWN-MANC-230.0-1 | 5461 | PAWNEE 345KV | XCEL | MANCHIEF | XCEL | 70311 | 2021 | Xcel Owned | PAWN-MANC-230.0-1 | FACILITY |  | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
PAWN-MANC-230.0-1 | 5461 | PAWNEE 345KV | XCEL | MANCHIEF | XCEL | 70311 | 2021 | Xcel Owned | 5461 PRI B | CURRENT_TRANSFORMER | MANC | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
PAWN-MANC-230.0-1 | 5461 | PAWNEE 345KV | XCEL | MANCHIEF | XCEL | 70311 | 2021 | Xcel Owned | L5461 W/VAR XDCR | SECONDARY_CURRENT_LIMITATION | MANC | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
PAWN-MANC-230.0-1 | 5461 | PAWNEE 345KV | XCEL | MANCHIEF | XCEL | 70311 | 2021 | Xcel Owned | L5461 PK-2 | SECONDARY_CURRENT_LIMITATION | MANC | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
PAWN-MANC-230.0-1 | 5461 | PAWNEE 345KV | XCEL | MANCHIEF | XCEL | 70311 | 2021 | Xcel Owned | 5461 PRI A | CURRENT_TRANSFORMER | MANC | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
PAWN-MANC-230.0-1 | 5461 | PAWNEE 345KV | XCEL | MANCHIEF | XCEL | 70311 | 2021 | Xcel Owned | 5461 PRI C | CURRENT_TRANSFORMER | MANC | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
PAWN-MSST-230.0-1 | 5457 | PAWNEE 345KV | XCEL | MISSILE SITE | XCEL | 70311 | 70623 | Xcel Owned | PAWN-MSST-230.0-1 | FACILITY |  | 1916 | 1980 | 2000 | 2000 | 763 | 789 | 797 | 797
PAWN-MSST-230.0-1 | 5457 | PAWNEE 345KV | XCEL | MISSILE SITE | XCEL | 70311 | 70623 | Xcel Owned | PAWN-MSST-230.0-1 | Transmission Line | 5457 | 1916 | 2108 | 2180 | 2398 | 763 | 840 | 868 | 955
PAWN-MSST-230.0-1 | 5457 | PAWNEE 345KV | XCEL | MISSILE SITE | XCEL | 70311 | 70623 | Xcel Owned |  | LINE_TRAP | MSST | 1980 | 1980 | 2091 | 2091 | 789 | 789 | 833 | 833
PAWN-MSST-230.0-1 | 5457 | PAWNEE 345KV | XCEL | MISSILE SITE | XCEL | 70311 | 70623 | Xcel Owned | 5457 246X | CURRENT_TRANSFORMER | PAWN | 2000 | 2000 | 2000 | 2000 | 797 | 797 | 797 | 797
PAWN-MSST-230.0-1 | 5457 | PAWNEE 345KV | XCEL | MISSILE SITE | XCEL | 70311 | 70623 | Xcel Owned | 5457 | BREAKER | PAWN | 2000 | 2000 | 2000 | 2000 | 797 | 797 | 797 | 797
PAWN-STOR-230.0-1 | 5455 | PAWNEE 345KV | XCEL | STORY SUBSTATION | XCEL | 70311 | 73192 | Xcel Owned | PAWN-STOR-230.0-1 | FACILITY |  | 1459 | 1478 | 1549 | 1627 | 581 | 589 | 617 | 648
PAWN-STOR-230.0-1 | 5455 | PAWNEE 345KV | XCEL | STORY SUBSTATION | XCEL | 70311 | 73192 | Xcel Owned | PAWN-STOR-230.0-1 | Transmission Line | 5455 | 1459 | 1478 | 1664 | 1812 | 581 | 589 | 663 | 722
PAWN-STOR-230.0-1 | 5455 | PAWNEE 345KV | XCEL | STORY SUBSTATION | XCEL | 70311 | 73192 | Xcel Owned | Foreign Ratings | Foreign Ratings | STOR | 1549 | 1627 | 1549 | 1627 | 617 | 648 | 617 | 648
PLEN-PCOG-230.0-1 | 5267 | PLAINS END SWITCHING STATION | XCEL | PLAINS END (COGENTRIX NUG) | FOREIGN | 70570 | 2099 | Xcel Owned | PLEN-PCOG-230.0-1 | FACILITY |  | 400 | 400 | 400 | 400 | 159 | 159 | 159 | 159
PLEN-PCOG-230.0-1 | 5267 | PLAINS END SWITCHING STATION | XCEL | PLAINS END (COGENTRIX NUG) | FOREIGN | 70570 | 2099 | Xcel Owned | Foreign Ratings | Foreign Ratings | PCOG | 400 | 400 | 400 | 400 | 159 | 159 | 159 | 159
PLEN-PENG-230.0-1 | 5261 | PLAINS END SWITCHING STATION | XCEL | PLAINS END NUG (PG&E) | XCEL | 70570 | 2100 | Xcel Owned | PLEN-PENG-230.0-1 | FACILITY |  | 800 | 800 | 800 | 800 | 319 | 319 | 319 | 319
PLEN-PENG-230.0-1 | 5261 | PLAINS END SWITCHING STATION | XCEL | PLAINS END NUG (PG&E) | XCEL | 70570 | 2100 | Xcel Owned | 5261 METER, JEM 10 | SECONDARY_CURRENT_LIMITATION | PENG | 800 | 800 | 800 | 800 | 319 | 319 | 319 | 319
PLEN-PENG-230.0-1 | 5261 | PLAINS END SWITCHING STATION | XCEL | PLAINS END NUG (PG&E) | XCEL | 70570 | 2100 | Xcel Owned | 230 BUS MU B | CURRENT_TRANSFORMER | PENG | 800 | 800 | 800 | 800 | 319 | 319 | 319 | 319
PLEN-PENG-230.0-1 | 5261 | PLAINS END SWITCHING STATION | XCEL | PLAINS END NUG (PG&E) | XCEL | 70570 | 2100 | Xcel Owned | 230 BUS MU C | CURRENT_TRANSFORMER | PENG | 800 | 800 | 800 | 800 | 319 | 319 | 319 | 319
PLEN-PENG-230.0-1 | 5261 | PLAINS END SWITCHING STATION | XCEL | PLAINS END NUG (PG&E) | XCEL | 70570 | 2100 | Xcel Owned | 230 BUS MU A | CURRENT_TRANSFORMER | PENG | 800 | 800 | 800 | 800 | 319 | 319 | 319 | 319
PLEN-PENG-230.0-1 | 5261 | PLAINS END SWITCHING STATION | XCEL | PLAINS END NUG (PG&E) | XCEL | 70570 | 2100 | Xcel Owned | 5261 PK2 | SECONDARY_CURRENT_LIMITATION | PENG | 800 | 800 | 800 | 800 | 319 | 319 | 319 | 319
PONC-PNCW-230.0-1 | 5747 | PONCHA JUNCTION SUBSTATION | XCEL | PONCHA (WAPA) | FOREIGN | 70393 | 79054 | Xcel Owned | PONC-PNCW-230.0-1 | FACILITY |  | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
PONC-PNCW-230.0-1 | 5747 | PONCHA JUNCTION SUBSTATION | XCEL | PONCHA (WAPA) | FOREIGN | 70393 | 79054 | Xcel Owned | Foreign Ratings | Foreign Ratings | PNCW | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
PONC-SARG-115.0-1 | 9811 | PONCHA JUNCTION SUBSTATION | XCEL | SARGENT SUBSTATION | XCEL | 70327 | 70379 | Xcel Owned | PONC-SARG-115.0-1 | FACILITY |  | 600 | 600 | 600 | 600 | 120 | 120 | 120 | 120
PONC-SARG-115.0-1 | 9811 | PONCHA JUNCTION SUBSTATION | XCEL | SARGENT SUBSTATION | XCEL | 70327 | 70379 | Xcel Owned | 9811_67GB | SECONDARY_CURRENT_LIMITATION | PONC | 600 | 600 | 600 | 600 | 120 | 120 | 120 | 120
PONC-SARG-115.0-1 | 9811 | PONCHA JUNCTION SUBSTATION | XCEL | SARGENT SUBSTATION | XCEL | 70327 | 70379 | Xcel Owned | 9811_67GP | SECONDARY_CURRENT_LIMITATION | PONC | 600 | 600 | 600 | 600 | 120 | 120 | 120 | 120
PONC-SARG-115.0-1 | 9811 | PONCHA JUNCTION SUBSTATION | XCEL | SARGENT SUBSTATION | XCEL | 70327 | 70379 | Xcel Owned | 9811_21Z2-5 | SECONDARY_CURRENT_LIMITATION | PONC | 600 | 600 | 600 | 600 | 120 | 120 | 120 | 120
PONC-SARG-115.0-1 | 9811 | PONCHA JUNCTION SUBSTATION | XCEL | SARGENT SUBSTATION | XCEL | 70327 | 70379 | Xcel Owned | 9811 135X | CURRENT_TRANSFORMER | PONC | 600 | 600 | 600 | 600 | 120 | 120 | 120 | 120
PONC-SARG-115.0-1 | 9811 | PONCHA JUNCTION SUBSTATION | XCEL | SARGENT SUBSTATION | XCEL | 70327 | 70379 | Xcel Owned | 9811_A_XDCR_115KV | SECONDARY_CURRENT_LIMITATION | PONC | 600 | 600 | 600 | 600 | 120 | 120 | 120 | 120
PONC-SARG-115.0-1 | 9811 | PONCHA JUNCTION SUBSTATION | XCEL | SARGENT SUBSTATION | XCEL | 70327 | 70379 | Xcel Owned | 9811_W_XDCR_115KV | SECONDARY_CURRENT_LIMITATION | PONC | 600 | 600 | 600 | 600 | 120 | 120 | 120 | 120
PONC-SARG-115.0-1 | 9811 | PONCHA JUNCTION SUBSTATION | XCEL | SARGENT SUBSTATION | XCEL | 70327 | 70379 | Xcel Owned | 9811 246Y | CURRENT_TRANSFORMER | PONC | 600 | 600 | 600 | 600 | 120 | 120 | 120 | 120
PONC-SARG-115.0-1 | 9811 | PONCHA JUNCTION SUBSTATION | XCEL | SARGENT SUBSTATION | XCEL | 70327 | 70379 | Xcel Owned | 9811_21Z3 | SECONDARY_CURRENT_LIMITATION | PONC | 600 | 600 | 600 | 600 | 120 | 120 | 120 | 120
PONC-SARG-115.0-1 | 9811 | PONCHA JUNCTION SUBSTATION | XCEL | SARGENT SUBSTATION | XCEL | 70327 | 70379 | Xcel Owned | 9811 246X | CURRENT_TRANSFORMER | PONC | 600 | 600 | 600 | 600 | 120 | 120 | 120 | 120
PONC-SARG-115.0-1 | 9811 | PONCHA JUNCTION SUBSTATION | XCEL | SARGENT SUBSTATION | XCEL | 70327 | 70379 | Xcel Owned | 9811_21Z2 | SECONDARY_CURRENT_LIMITATION | PONC | 600 | 600 | 600 | 600 | 120 | 120 | 120 | 120
PONC-SARG-115.0-1 | 9811 | PONCHA JUNCTION SUBSTATION | XCEL | SARGENT SUBSTATION | XCEL | 70327 | 70379 | Xcel Owned | 9811_VAR_XDCR_115KV | SECONDARY_CURRENT_LIMITATION | PONC | 600 | 600 | 600 | 600 | 120 | 120 | 120 | 120
PONC-SARG-115.0-1 | 9811 | PONCHA JUNCTION SUBSTATION | XCEL | SARGENT SUBSTATION | XCEL | 70327 | 70379 | Xcel Owned | 9811L C | SWITCH | PONC | 600 | 775 | 743 | 890 | 120 | 154 | 148 | 177
PONC-SARG-115.0-1 | 9811 | PONCHA JUNCTION SUBSTATION | XCEL | SARGENT SUBSTATION | XCEL | 70327 | 70379 | Xcel Owned | 9811L A | SWITCH | PONC | 600 | 775 | 743 | 890 | 120 | 154 | 148 | 177
PONC-SARG-115.0-1 | 9811 | PONCHA JUNCTION SUBSTATION | XCEL | SARGENT SUBSTATION | XCEL | 70327 | 70379 | Xcel Owned | 9811L B | SWITCH | PONC | 600 | 775 | 743 | 890 | 120 | 154 | 148 | 177
PRHN-RUCC-345.0-1 | 7131 | PRONGHORN | XCEL | RUSH CREEK 1 (ES) | FOREIGN | 70628 | 70764 | Jointly Owned | PRHN-RUCC-345.0-1 | FACILITY |  | 1200 | 1200 | 1200 | 1200 | 717 | 717 | 717 | 717
PRHN-RUCC-345.0-1 | 7131 | PRONGHORN | XCEL | RUSH CREEK 1 (ES) | FOREIGN | 70628 | 70764 | Jointly Owned | 345 7131A | CURRENT_TRANSFORMER | PRHN | 1200 | 1200 | 1200 | 1200 | 717 | 717 | 717 | 717
PRHN-RUCC-345.0-1 | 7131 | PRONGHORN | XCEL | RUSH CREEK 1 (ES) | FOREIGN | 70628 | 70764 | Jointly Owned | 345 7131B | CURRENT_TRANSFORMER | PRHN | 1200 | 1200 | 1200 | 1200 | 717 | 717 | 717 | 717
PRHN-RUCC-345.0-1 | 7131 | PRONGHORN | XCEL | RUSH CREEK 1 (ES) | FOREIGN | 70628 | 70764 | Jointly Owned | 345 7131C | CURRENT_TRANSFORMER | PRHN | 1200 | 1200 | 1200 | 1200 | 717 | 717 | 717 | 717
PRHN-SHOR-345.0-1 | 7132 | PRONGHORN | XCEL | SHORTGRASS | XCEL | 70628 | 70630 | Xcel Owned | PRHN-SHOR-345.0-1 | FACILITY |  | 2740 | 2740 | 2740 | 2740 | 1637 | 1637 | 1637 | 1637
PRHN-SHOR-345.0-1 | 7132 | PRONGHORN | XCEL | SHORTGRASS | XCEL | 70628 | 70630 | Xcel Owned | PRHN-SHOR-345.0-1 | Transmission Line | 7132 | 2740 | 2740 | 2740 | 2740 | 1637 | 1637 | 1637 | 1637
PTAR-BLUE-230.0-1 | 5367 | PTARMIGAN | XCEL | BLUE RIVER SUBSTATION | XCEL | 70057 | 70053 | Jointly Owned | PTAR-BLUE-230.0-1 | FACILITY |  | 1174 | 1379 | 1407 | 1563 | 468 | 549 | 561 | 623
PTAR-BLUE-230.0-1 | 5367 | PTARMIGAN | XCEL | BLUE RIVER SUBSTATION | XCEL | 70057 | 70053 | Jointly Owned | Narcissus | BUSBAR_SECTION | BLUE | 1174 | 1379 | 1407 | 1574 | 468 | 549 | 561 | 627
PTAR-BLUE-230.0-1 | 5367 | PTARMIGAN | XCEL | BLUE RIVER SUBSTATION | XCEL | 70057 | 70053 | Jointly Owned | PTAR-BLUE-230.0-1 | Transmission Line | 5367 | 1295 | 1424 | 1421 | 1563 | 516 | 567 | 566 | 623
QUIN-BRIC-230.0-1 | 5165 | QUINCY SUBSTATION | XCEL | BRICK CENTER | XCEL | 70343 | 70545 | Xcel Owned | QUIN-BRIC-230.0-1 | FACILITY |  | 1980 | 1980 | 2000 | 2000 | 789 | 789 | 797 | 797
QUIN-BRIC-230.0-1 | 5165 | QUINCY SUBSTATION | XCEL | BRICK CENTER | XCEL | 70343 | 70545 | Xcel Owned |  | LINE_TRAP | BRIC | 1980 | 1980 | 2091 | 2091 | 789 | 789 | 833 | 833
QUIN-BRIC-230.0-1 | 5165 | QUINCY SUBSTATION | XCEL | BRICK CENTER | XCEL | 70343 | 70545 | Xcel Owned | 5165-1 | CIRCUIT_SWITCHER | QUIN | 2000 | 2000 | 2000 | 2000 | 797 | 797 | 797 | 797
QUIN-BRIC-230.0-1 | 5165 | QUINCY SUBSTATION | XCEL | BRICK CENTER | XCEL | 70343 | 70545 | Xcel Owned | 5165-2 | CIRCUIT_SWITCHER | QUIN | 2000 | 2000 | 2000 | 2000 | 797 | 797 | 797 | 797
QUIN-BRIC-230.0-1 | 5165 | QUINCY SUBSTATION | XCEL | BRICK CENTER | XCEL | 70343 | 70545 | Xcel Owned | 5165-2S | CIRCUIT_SWITCHER | QUIN | 2000 | 2000 | 2000 | 2000 | 797 | 797 | 797 | 797
QUIN-SMOK-230.0-1 | 5165 | QUINCY SUBSTATION | XCEL | SMOKY HILL SUBSTATION | XCEL | 70343 | 70396 | Xcel Owned | QUIN-SMOK-230.0-1 | FACILITY |  | 1904 | 1980 | 2000 | 2000 | 758 | 789 | 797 | 797
QUIN-SMOK-230.0-1 | 5165 | QUINCY SUBSTATION | XCEL | SMOKY HILL SUBSTATION | XCEL | 70343 | 70396 | Xcel Owned | QUIN-SMOK-230.0-1 | Transmission Line | 5165 | 1904 | 2094 | 2167 | 2384 | 758 | 834 | 863 | 950
QUIN-SMOK-230.0-1 | 5165 | QUINCY SUBSTATION | XCEL | SMOKY HILL SUBSTATION | XCEL | 70343 | 70396 | Xcel Owned | Grosbeak | BUSBAR_SECTION | SMOK | 1904 | 2094 | 2167 | 2384 | 758 | 834 | 863 | 950
QUIN-SMOK-230.0-1 | 5165 | QUINCY SUBSTATION | XCEL | SMOKY HILL SUBSTATION | XCEL | 70343 | 70396 | Xcel Owned |  | LINE_TRAP | SMOK | 1980 | 1980 | 2091 | 2091 | 789 | 789 | 833 | 833
QUIN-SMOK-230.0-1 | 5165 | QUINCY SUBSTATION | XCEL | SMOKY HILL SUBSTATION | XCEL | 70343 | 70396 | Xcel Owned | 5165-2 | CIRCUIT_SWITCHER | QUIN | 2000 | 2000 | 2000 | 2000 | 797 | 797 | 797 | 797
QUIN-SMOK-230.0-1 | 5165 | QUINCY SUBSTATION | XCEL | SMOKY HILL SUBSTATION | XCEL | 70343 | 70396 | Xcel Owned | 5165-1 | CIRCUIT_SWITCHER | QUIN | 2000 | 2000 | 2000 | 2000 | 797 | 797 | 797 | 797
QUIN-SMOK-230.0-1 | 5165 | QUINCY SUBSTATION | XCEL | SMOKY HILL SUBSTATION | XCEL | 70343 | 70396 | Xcel Owned | 5165-2S | CIRCUIT_SWITCHER | QUIN | 2000 | 2000 | 2000 | 2000 | 797 | 797 | 797 | 797
RALS-RIDG-115.0-1 | 9054 | RALSTON SUBSTATION | XCEL | RIDGE SUBSTATION | XCEL | 70345 | 70354 | Xcel Owned | RALS-RIDG-115.0-1 | FACILITY |  | 600 | 600 | 600 | 600 | 120 | 120 | 120 | 120
RALS-RIDG-115.0-1 | 9054 | RALSTON SUBSTATION | XCEL | RIDGE SUBSTATION | XCEL | 70345 | 70354 | Xcel Owned | 9054_135Y_METER_VAR | SECONDARY_CURRENT_LIMITATION | RIDG | 600 | 600 | 600 | 600 | 120 | 120 | 120 | 120
RALS-RIDG-115.0-1 | 9054 | RALSTON SUBSTATION | XCEL | RIDGE SUBSTATION | XCEL | 70345 | 70354 | Xcel Owned | 9054_135Y_METER_AMPSW | SECONDARY_CURRENT_LIMITATION | RIDG | 600 | 600 | 600 | 600 | 120 | 120 | 120 | 120
RALS-RIDG-115.0-2 | 9688 | RALSTON SUBSTATION | XCEL | RIDGE SUBSTATION | XCEL | 70346 | 70354 | Xcel Owned | RALS-RIDG-115.0-2 | FACILITY |  | 600 | 600 | 600 | 600 | 120 | 120 | 120 | 120
RALS-RIDG-115.0-2 | 9688 | RALSTON SUBSTATION | XCEL | RIDGE SUBSTATION | XCEL | 70346 | 70354 | Xcel Owned | 9688_135Y_METER_VAR | SECONDARY_CURRENT_LIMITATION | RIDG | 600 | 600 | 600 | 600 | 120 | 120 | 120 | 120
RALS-VALM-115.0-1 | 9054 | RALSTON SUBSTATION | XCEL | VALMONT SWITCHYARD SUBSTATION | XCEL | 70345 | 70440 | Xcel Owned | RALS-VALM-115.0-1 | FACILITY |  | 600 | 702 | 725 | 797 | 120 | 140 | 144 | 159
RALS-VALM-115.0-1 | 9054 | RALSTON SUBSTATION | XCEL | VALMONT SWITCHYARD SUBSTATION | XCEL | 70345 | 70440 | Xcel Owned | 9054L A | SWITCH | VALM | 600 | 775 | 743 | 890 | 120 | 154 | 148 | 177
RALS-VALM-115.0-1 | 9054 | RALSTON SUBSTATION | XCEL | VALMONT SWITCHYARD SUBSTATION | XCEL | 70345 | 70440 | Xcel Owned | 9054M A | SWITCH | VALM | 600 | 775 | 743 | 890 | 120 | 154 | 148 | 177
RALS-VALM-115.0-1 | 9054 | RALSTON SUBSTATION | XCEL | VALMONT SWITCHYARD SUBSTATION | XCEL | 70345 | 70440 | Xcel Owned | 9054L C | SWITCH | VALM | 600 | 775 | 743 | 890 | 120 | 154 | 148 | 177
RALS-VALM-115.0-1 | 9054 | RALSTON SUBSTATION | XCEL | VALMONT SWITCHYARD SUBSTATION | XCEL | 70345 | 70440 | Xcel Owned | 9054M B | SWITCH | VALM | 600 | 775 | 743 | 890 | 120 | 154 | 148 | 177
RALS-VALM-115.0-1 | 9054 | RALSTON SUBSTATION | XCEL | VALMONT SWITCHYARD SUBSTATION | XCEL | 70345 | 70440 | Xcel Owned | 9054L B | SWITCH | VALM | 600 | 775 | 743 | 890 | 120 | 154 | 148 | 177
RALS-VALM-115.0-1 | 9054 | RALSTON SUBSTATION | XCEL | VALMONT SWITCHYARD SUBSTATION | XCEL | 70345 | 70440 | Xcel Owned | 9054M C | SWITCH | VALM | 600 | 775 | 743 | 890 | 120 | 154 | 148 | 177
RALS-VALM-115.0-1 | 9054 | RALSTON SUBSTATION | XCEL | VALMONT SWITCHYARD SUBSTATION | XCEL | 70345 | 70440 | Xcel Owned | RALS-VALM-115.0-1 | Transmission Line | 9054 | 638 | 702 | 725 | 797 | 127 | 140 | 144 | 159
RAYL-PONC-115.0-1 | 9255 | RAY LEWIS | XCEL | PONCHA JUNCTION SUBSTATION | XCEL | 70312 | 70327 | Xcel Owned | RAYL-PONC-115.0-1 | FACILITY | [9 empty] | See Ambient Adjusted Ratings Section
RCII-SHOR-345.0-1 | 7192 | RUSH CREEK II (ES) | FOREIGN | SHORTGRASS | XCEL | 70773 | 70630 | Jointly Owned | RCII-SHOR-345.0-1 | FACILITY |  | 1200 | 1200 | 1200 | 1200 | 717 | 717 | 717 | 717
RCII-SHOR-345.0-1 | 7192 | RUSH CREEK II (ES) | FOREIGN | SHORTGRASS | XCEL | 70773 | 70630 | Jointly Owned | 7192_RM | SECONDARY_CURRENT_LIMITATION | SHOR | 1200 | 1200 | 1200 | 1200 | 717 | 717 | 717 | 717
RCII-SHOR-345.0-1 | 7192 | RUSH CREEK II (ES) | FOREIGN | SHORTGRASS | XCEL | 70773 | 70630 | Jointly Owned | 345 7192 C | CURRENT_TRANSFORMER | SHOR | 1200 | 1200 | 1200 | 1200 | 717 | 717 | 717 | 717
RCII-SHOR-345.0-1 | 7192 | RUSH CREEK II (ES) | FOREIGN | SHORTGRASS | XCEL | 70773 | 70630 | Jointly Owned | 345 7192 B | CURRENT_TRANSFORMER | SHOR | 1200 | 1200 | 1200 | 1200 | 717 | 717 | 717 | 717
RCII-SHOR-345.0-1 | 7192 | RUSH CREEK II (ES) | FOREIGN | SHORTGRASS | XCEL | 70773 | 70630 | Jointly Owned | 345 7192 A | CURRENT_TRANSFORMER | SHOR | 1200 | 1200 | 1200 | 1200 | 717 | 717 | 717 | 717
RCII-SHOR-345.0-1 | 7192 | RUSH CREEK II (ES) | FOREIGN | SHORTGRASS | XCEL | 70773 | 70630 | Jointly Owned | 7192_METER | SECONDARY_CURRENT_LIMITATION | SHOR | 1200 | 1200 | 1200 | 1200 | 717 | 717 | 717 | 717
RECY-FLUP-115.0-1 | 9053 | RECYCLING - COORS | XCEL | FORT LUPTON SUBSTATION | XCEL | 70127 | 70191 | Xcel Owned | RECY-FLUP-115.0-1 | FACILITY |  | 1200 | 1520 | 1483 | 1657 | 239 | 303 | 295 | 330
RECY-FLUP-115.0-1 | 9053 | RECYCLING - COORS | XCEL | FORT LUPTON SUBSTATION | XCEL | 70127 | 70191 | Xcel Owned | 9053-7 | SWITCH | RECY | 1200 | 1549 | 1486 | 1780 | 239 | 309 | 296 | 355
RECY-FLUP-115.0-1 | 9053 | RECYCLING - COORS | XCEL | FORT LUPTON SUBSTATION | XCEL | 70127 | 70191 | Xcel Owned | 9053M | SWITCH | FLUP | 1200 | 1549 | 1486 | 1780 | 239 | 309 | 296 | 355
RECY-FLUP-115.0-1 | 9053 | RECYCLING - COORS | XCEL | FORT LUPTON SUBSTATION | XCEL | 70127 | 70191 | Xcel Owned | 9053L | SWITCH | FLUP | 1294 | 1520 | 1483 | 1657 | 258 | 303 | 295 | 330
RECY-FULT-115.0-1 | 9053 | RECYCLING - COORS | XCEL | FULTON SUBSTATION | XCEL | 70127 | 70194 | Xcel Owned | RECY-FULT-115.0-1 | FACILITY |  | 1072 | 1179 | 1219 | 1341 | 213 | 235 | 243 | 267
RECY-FULT-115.0-1 | 9053 | RECYCLING - COORS | XCEL | FULTON SUBSTATION | XCEL | 70127 | 70194 | Xcel Owned | Arbutus | BUSBAR_SECTION | FULT | 1072 | 1179 | 1219 | 1341 | 213 | 235 | 243 | 267
RIDG-RIDG_TP-230.0-1 | 5067 | RIDGE SUBSTATION | XCEL | RIDGE TAP | XCEL | 70355 | 2210 | Xcel Owned | RIDG-RIDG_TP-230.0-1 | FACILITY |  | 1200 | 1394 | 1444 | 1588 | 478 | 555 | 575 | 633
RIDG-RIDG_TP-230.0-1 | 5067 | RIDGE SUBSTATION | XCEL | RIDGE TAP | XCEL | 70355 | 2210 | Xcel Owned | 5021E | SWITCH | RIDG | 1200 | 1549 | 1486 | 1780 | 478 | 617 | 592 | 709
RIDG-RIDG_TP-230.0-1 | 5067 | RIDGE SUBSTATION | XCEL | RIDGE TAP | XCEL | 70355 | 2210 | Xcel Owned | 5021W | SWITCH | RIDG | 1200 | 1549 | 1486 | 1780 | 478 | 617 | 592 | 709
RIDG-RIDG_TP-230.0-1 | 5067 | RIDGE SUBSTATION | XCEL | RIDGE TAP | XCEL | 70355 | 2210 | Xcel Owned | 5064W | SWITCH | RIDG | 1200 | 1549 | 1486 | 1780 | 478 | 617 | 592 | 709
RIDG-RIDG_TP-230.0-1 | 5067 | RIDGE SUBSTATION | XCEL | RIDGE TAP | XCEL | 70355 | 2210 | Xcel Owned | 5064E | SWITCH | RIDG | 1200 | 1549 | 1486 | 1780 | 478 | 617 | 592 | 709
RIDG-RIDG_TP-230.0-1 | 5067 | RIDGE SUBSTATION | XCEL | RIDGE TAP | XCEL | 70355 | 2210 | Xcel Owned | RIDG-RIDG_TP-230.0-1 | Transmission Line | 5067 | 1268 | 1394 | 1444 | 1588 | 505 | 555 | 575 | 633
RIVE-HNLK-230.0-1 | 5309 | RIVERDALE SUBSTATION | XCEL | HENRY LAKE (Tri State) | FOREIGN | 70362 | 70605 | Xcel Owned | RIVE-HNLK-230.0-1 | FACILITY |  | 1270 | 1397 | 1447 | 1591 | 506 | 557 | 576 | 634
RIVE-HNLK-230.0-1 | 5309 | RIVERDALE SUBSTATION | XCEL | HENRY LAKE (Tri State) | FOREIGN | 70362 | 70605 | Xcel Owned | RIVE-HNLK-230.0-1 | Transmission Line | 5309 | 1270 | 1397 | 1447 | 1591 | 506 | 557 | 576 | 634
RMEC-KEEN-230.0-1 | 5565 | ROCKY MOUNTAIN ENERGY CENTER | XCEL | KEENESBURG SUBSTATION | XCEL | 70590 | 70820 | Xcel Owned | RMEC-KEEN-230.0-1 | FACILITY |  | 2000 | 2000 | 2000 | 2000 | 797 | 797 | 797 | 797
RMEC-KEEN-230.0-1 | 5565 | ROCKY MOUNTAIN ENERGY CENTER | XCEL | KEENESBURG SUBSTATION | XCEL | 70590 | 70820 | Xcel Owned | 230 5565 MU B | CURRENT_TRANSFORMER | RMEC | 2000 | 2000 | 2000 | 2000 | 797 | 797 | 797 | 797
RMEC-KEEN-230.0-1 | 5565 | ROCKY MOUNTAIN ENERGY CENTER | XCEL | KEENESBURG SUBSTATION | XCEL | 70590 | 70820 | Xcel Owned | 5565 | BREAKER | RMEC | 2000 | 2000 | 2000 | 2000 | 797 | 797 | 797 | 797
RMEC-KEEN-230.0-1 | 5565 | ROCKY MOUNTAIN ENERGY CENTER | XCEL | KEENESBURG SUBSTATION | XCEL | 70590 | 70820 | Xcel Owned | 230 5565 MU C | CURRENT_TRANSFORMER | RMEC | 2000 | 2000 | 2000 | 2000 | 797 | 797 | 797 | 797
RMEC-KEEN-230.0-1 | 5565 | ROCKY MOUNTAIN ENERGY CENTER | XCEL | KEENESBURG SUBSTATION | XCEL | 70590 | 70820 | Xcel Owned | 230 5565 MU A | CURRENT_TRANSFORMER | RMEC | 2000 | 2000 | 2000 | 2000 | 797 | 797 | 797 | 797
RMEC-KEEN-230.0-1 | 5565 | ROCKY MOUNTAIN ENERGY CENTER | XCEL | KEENESBURG SUBSTATION | XCEL | 70590 | 70820 | Xcel Owned | 5565_MU_PK-2_230KV | SECONDARY_CURRENT_LIMITATION | RMEC | 2000 | 2000 | 2000 | 2000 | 797 | 797 | 797 | 797
RMEC-KEEN-230.0-1 | 5565 | ROCKY MOUNTAIN ENERGY CENTER | XCEL | KEENESBURG SUBSTATION | XCEL | 70590 | 70820 | Xcel Owned | 5564 | BREAKER | RMEC | 2000 | 2000 | 2000 | 2000 | 797 | 797 | 797 | 797
ROSE-ARRL-115.0-1 | 9996 | ROSEDALE SUBSTATION | XCEL | ARROWHEAD SUBSTATION | XCEL | 70368 | 70475 | Xcel Owned | ROSE-ARRL-115.0-1 | FACILITY |  | 803 | 883 | 913 | 1004 | 160 | 176 | 182 | 200
ROSE-ARRL-115.0-1 | 9996 | ROSEDALE SUBSTATION | XCEL | ARROWHEAD SUBSTATION | XCEL | 70368 | 70475 | Xcel Owned | ROSE-ARRL-115.0-1 | Transmission Line | 9996 | 803 | 883 | 913 | 1004 | 160 | 176 | 182 | 200
RUSS-CHER-230.0-1 | 5021 | RUSSELL SUBSTATION | XCEL | CHEROKEE SWITCHYARD SUBSTATION | XCEL | 70369 | 70107 | Xcel Owned | RUSS-CHER-230.0-1 | FACILITY |  | 1091 | 1271 | 1303 | 1448 | 435 | 506 | 519 | 577
RUSS-CHER-230.0-1 | 5021 | RUSSELL SUBSTATION | XCEL | CHEROKEE SWITCHYARD SUBSTATION | XCEL | 70369 | 70107 | Xcel Owned | Curlew | BUSBAR_SECTION | CHER | 1091 | 1271 | 1303 | 1448 | 435 | 506 | 519 | 577
RUSS-RIDG-230.0-1 | 5021 | RUSSELL SUBSTATION | XCEL | RIDGE SUBSTATION | XCEL | 70369 | 70355 | Xcel Owned | RUSS-RIDG-230.0-1 | FACILITY |  | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
RUSS-RIDG-230.0-1 | 5021 | RUSSELL SUBSTATION | XCEL | RIDGE SUBSTATION | XCEL | 70369 | 70355 | Xcel Owned | L5021 METER VAR | SECONDARY_CURRENT_LIMITATION | RIDG | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
RUSS-RIDG-230.0-1 | 5021 | RUSSELL SUBSTATION | XCEL | RIDGE SUBSTATION | XCEL | 70369 | 70355 | Xcel Owned | L5021 METER AMPSW | SECONDARY_CURRENT_LIMITATION | RIDG | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
RUSS-RIDG-230.0-1 | 5021 | RUSSELL SUBSTATION | XCEL | RIDGE SUBSTATION | XCEL | 70369 | 70355 | Xcel Owned | 5066E | SWITCH | RIDG | 1200 | 1549 | 1486 | 1780 | 478 | 617 | 592 | 709
RUSS-RIDG-230.0-1 | 5021 | RUSSELL SUBSTATION | XCEL | RIDGE SUBSTATION | XCEL | 70369 | 70355 | Xcel Owned | 5021W | SWITCH | RIDG | 1200 | 1549 | 1486 | 1780 | 478 | 617 | 592 | 709
RUSS-RIDG-230.0-1 | 5021 | RUSSELL SUBSTATION | XCEL | RIDGE SUBSTATION | XCEL | 70369 | 70355 | Xcel Owned | 5066W | SWITCH | RIDG | 1200 | 1549 | 1486 | 1780 | 478 | 617 | 592 | 709
RUSS-RIDG-230.0-1 | 5021 | RUSSELL SUBSTATION | XCEL | RIDGE SUBSTATION | XCEL | 70369 | 70355 | Xcel Owned | 5021E | SWITCH | RIDG | 1200 | 1549 | 1486 | 1780 | 478 | 617 | 592 | 709
SHOR-BRPL-345.0-1 | 7191 | SHORTGRASS | XCEL | BRONCO PLAINS (NEXTERA) | FOREIGN | 70630 | 70750 | Jointly Owned | SHOR-BRPL-345.0-1 | FACILITY |  | 1200 | 1200 | 1200 | 1200 | 717 | 717 | 717 | 717
SHOR-BRPL-345.0-1 | 7191 | SHORTGRASS | XCEL | BRONCO PLAINS (NEXTERA) | FOREIGN | 70630 | 70750 | Jointly Owned | 345 7191 C | CURRENT_TRANSFORMER | SHOR | 1200 | 1200 | 1200 | 1200 | 717 | 717 | 717 | 717
SHOR-BRPL-345.0-1 | 7191 | SHORTGRASS | XCEL | BRONCO PLAINS (NEXTERA) | FOREIGN | 70630 | 70750 | Jointly Owned | 7191_RM | SECONDARY_CURRENT_LIMITATION | SHOR | 1200 | 1200 | 1200 | 1200 | 717 | 717 | 717 | 717
SHOR-BRPL-345.0-1 | 7191 | SHORTGRASS | XCEL | BRONCO PLAINS (NEXTERA) | FOREIGN | 70630 | 70750 | Jointly Owned | 345 7191 B | CURRENT_TRANSFORMER | SHOR | 1200 | 1200 | 1200 | 1200 | 717 | 717 | 717 | 717
SHOR-BRPL-345.0-1 | 7191 | SHORTGRASS | XCEL | BRONCO PLAINS (NEXTERA) | FOREIGN | 70630 | 70750 | Jointly Owned | 345 7191 A | CURRENT_TRANSFORMER | SHOR | 1200 | 1200 | 1200 | 1200 | 717 | 717 | 717 | 717
SHOR-BRPL-345.0-1 | 7191 | SHORTGRASS | XCEL | BRONCO PLAINS (NEXTERA) | FOREIGN | 70630 | 70750 | Jointly Owned | 7191_METER | SECONDARY_CURRENT_LIMITATION | SHOR | 1200 | 1200 | 1200 | 1200 | 717 | 717 | 717 | 717
SISA-REUN-230.0-1 | 5877 | SILVER SADDLE SUBSTATION | XCEL | REUNION (TSGT) | FOREIGN | 70609 | 72026 | Jointly Owned | SISA-REUN-230.0-1 | FACILITY |  | 1627 | 1627 | 1627 | 1627 | 648 | 648 | 648 | 648
SISA-REUN-230.0-1 | 5877 | SILVER SADDLE SUBSTATION | XCEL | REUNION (TSGT) | FOREIGN | 70609 | 72026 | Jointly Owned | Foreign Ratings | Foreign Ratings | REUN | 1627 | 1627 | 1627 | 1627 | 648 | 648 | 648 | 648
SKYR-SPRU-230.0-1 | 5735 | SKY RANCH SUBSTATION | XCEL | SPRUCE SUBSTATION | XCEL | 70392 | 70528 | Xcel Owned | SKYR-SPRU-230.0-1 | FACILITY |  | 1215 | 1393 | 1443 | 1587 | 484 | 555 | 575 | 632
SKYR-SPRU-230.0-1 | 5735 | SKY RANCH SUBSTATION | XCEL | SPRUCE SUBSTATION | XCEL | 70392 | 70528 | Xcel Owned | Narcissus | BUSBAR_SECTION | SKYR | 1215 | 1422 | 1452 | 1621 | 484 | 566 | 578 | 646
SKYR-SPRU-230.0-1 | 5735 | SKY RANCH SUBSTATION | XCEL | SPRUCE SUBSTATION | XCEL | 70392 | 70528 | Xcel Owned | SKYR-SPRU-230.0-1 | Transmission Line | 5735 | 1266 | 1393 | 1443 | 1587 | 504 | 555 | 575 | 632
SLVA-BLPK-115.0-1 | 9431 | SAN LUIS VALLEY SUBSTATION | XCEL | BLANCA PEAK SUBSTATION | XCEL | 70374 | 70937 | Xcel Owned | SLVA-BLPK-115.0-1 | FACILITY |  | 450 | 450 | 450 | 450 | 90 | 90 | 90 | 90
SLVA-BLPK-115.0-1 | 9431 | SAN LUIS VALLEY SUBSTATION | XCEL | BLANCA PEAK SUBSTATION | XCEL | 70374 | 70937 | Xcel Owned | 9431_XD_A_115KV | SECONDARY_CURRENT_LIMITATION | SLVA | 450 | 450 | 450 | 450 | 90 | 90 | 90 | 90
SLVA-BLPK-115.0-1 | 9431 | SAN LUIS VALLEY SUBSTATION | XCEL | BLANCA PEAK SUBSTATION | XCEL | 70374 | 70937 | Xcel Owned | 9431_XD_C_115KV | SECONDARY_CURRENT_LIMITATION | SLVA | 450 | 450 | 450 | 450 | 90 | 90 | 90 | 90
SLVA-BLPK-115.0-1 | 9431 | SAN LUIS VALLEY SUBSTATION | XCEL | BLANCA PEAK SUBSTATION | XCEL | 70374 | 70937 | Xcel Owned | 9431_XD_B_115KV | SECONDARY_CURRENT_LIMITATION | SLVA | 450 | 450 | 450 | 450 | 90 | 90 | 90 | 90
SLVA-SARG-115.0-1 | 9827 | SAN LUIS VALLEY SUBSTATION | XCEL | SARGENT SUBSTATION | XCEL | 70374 | 70379 | Xcel Owned | SLVA-SARG-115.0-1 | FACILITY |  | 814 | 843 | 843 | 843 | 162 | 168 | 168 | 168
SLVA-SARG-115.0-1 | 9827 | SAN LUIS VALLEY SUBSTATION | XCEL | SARGENT SUBSTATION | XCEL | 70374 | 70379 | Xcel Owned | SLVA-SARG-115.0-1 | Transmission Line | 9827 | 814 | 895 | 893 | 982 | 162 | 178 | 178 | 196
SLVA-SARG-115.0-1 | 9827 | SAN LUIS VALLEY SUBSTATION | XCEL | SARGENT SUBSTATION | XCEL | 70374 | 70379 | Xcel Owned | Foreign Ratings | Foreign Ratings | SLVA | 843 | 843 | 843 | 843 | 168 | 168 | 168 | 168 | Transfer bus ratings from Tri-State
SMOK-MURP-230.0-1 | 5163 | SMOKY HILL SUBSTATION | XCEL | MURPHY CREEK SUBSTATION | XCEL | 70396 | 70551 | Xcel Owned | SMOK-MURP-230.0-1 | FACILITY |  | 1841 | 2000 | 2000 | 2000 | 733 | 797 | 797 | 797
SMOK-MURP-230.0-1 | 5163 | SMOKY HILL SUBSTATION | XCEL | MURPHY CREEK SUBSTATION | XCEL | 70396 | 70551 | Xcel Owned | SMOK-MURP-230.0-1 | Transmission Line | 5163 | 1841 | 2025 | 2095 | 2304 | 733 | 807 | 835 | 918
SMOK-MURP-230.0-1 | 5163 | SMOKY HILL SUBSTATION | XCEL | MURPHY CREEK SUBSTATION | XCEL | 70396 | 70551 | Xcel Owned | 5163-2 | CIRCUIT_SWITCHER | MURP | 2000 | 2000 | 2000 | 2000 | 797 | 797 | 797 | 797
SMOK-POWH-230.0-1 | 5171 | SMOKY HILL SUBSTATION | XCEL | POWHATON SUBSTATION | XCEL | 70396 | 70532 | Xcel Owned | SMOK-POWH-230.0-1 | FACILITY |  | 1857 | 2000 | 2000 | 2000 | 740 | 797 | 797 | 797
SMOK-POWH-230.0-1 | 5171 | SMOKY HILL SUBSTATION | XCEL | POWHATON SUBSTATION | XCEL | 70396 | 70532 | Xcel Owned | SMOK-POWH-230.0-1 | Transmission Line | 5171 | 1857 | 2042 | 2112 | 2324 | 740 | 813 | 841 | 926
SMOK-POWH-230.0-1 | 5171 | SMOKY HILL SUBSTATION | XCEL | POWHATON SUBSTATION | XCEL | 70396 | 70532 | Xcel Owned | Swift | BUSBAR_SECTION | SMOK | 1857 | 2042 | 2112 | 2324 | 740 | 813 | 841 | 926
SMOK-POWH-230.0-1 | 5171 | SMOKY HILL SUBSTATION | XCEL | POWHATON SUBSTATION | XCEL | 70396 | 70532 | Xcel Owned | 5171-1 | CIRCUIT_SWITCHER | POWH | 2000 | 2000 | 2000 | 2000 | 797 | 797 | 797 | 797
SMOK-SPRU-230.0-1 | 5177 | SMOKY HILL SUBSTATION | XCEL | SPRUCE SUBSTATION | XCEL | 70396 | 70528 | Xcel Owned | SMOK-SPRU-230.0-1 | FACILITY |  | 1857 | 2042 | 2112 | 2324 | 740 | 813 | 841 | 926
SMOK-SPRU-230.0-1 | 5177 | SMOKY HILL SUBSTATION | XCEL | SPRUCE SUBSTATION | XCEL | 70396 | 70528 | Xcel Owned | Swift | BUSBAR_SECTION | SMOK | 1857 | 2042 | 2112 | 2324 | 740 | 813 | 841 | 926
SMOK-SPRU-230.0-1 | 5177 | SMOKY HILL SUBSTATION | XCEL | SPRUCE SUBSTATION | XCEL | 70396 | 70528 | Xcel Owned | SMOK-SPRU-230.0-1 | Transmission Line | 5177 | 1857 | 2042 | 2112 | 2324 | 740 | 813 | 841 | 926
SODA-CHAT-230.0-1 | 5023 | SODA LAKES SUBSTATION | XCEL | CHATFIELD SUBSTATION | XCEL | 70018 | 70100 | Xcel Owned | SODA-CHAT-230.0-1 | FACILITY |  | 1214 | 1388 | 1434 | 1577 | 483 | 553 | 571 | 628
SODA-CHAT-230.0-1 | 5023 | SODA LAKES SUBSTATION | XCEL | CHATFIELD SUBSTATION | XCEL | 70018 | 70100 | Xcel Owned | Narcissus | BUSBAR_SECTION | CHAT | 1214 | 1420 | 1450 | 1619 | 483 | 566 | 578 | 645
SODA-CHAT-230.0-1 | 5023 | SODA LAKES SUBSTATION | XCEL | CHATFIELD SUBSTATION | XCEL | 70018 | 70100 | Xcel Owned | SODA-CHAT-230.0-1 | Transmission Line | 5023 | 1260 | 1388 | 1434 | 1577 | 502 | 553 | 571 | 628
SODA-LOOK-230.0-1 | 5851 | SODA LAKES SUBSTATION | XCEL | LOOKOUT SUBSTATION | XCEL | 70018 | 70266 | Xcel Owned | SODA-LOOK-230.0-1 | FACILITY |  | 1200 | 1259 | 1425 | 1425 | 478 | 502 | 568 | 568
SODA-LOOK-230.0-1 | 5851 | SODA LAKES SUBSTATION | XCEL | LOOKOUT SUBSTATION | XCEL | 70018 | 70266 | Xcel Owned | 5851N | SWITCH | LOOK | 1200 | 1549 | 1486 | 1780 | 478 | 617 | 592 | 709
SODA-LOOK-230.0-1 | 5851 | SODA LAKES SUBSTATION | XCEL | LOOKOUT SUBSTATION | XCEL | 70018 | 70266 | Xcel Owned | 5024N | SWITCH | LOOK | 1200 | 1549 | 1486 | 1780 | 478 | 617 | 592 | 709
SODA-LOOK-230.0-1 | 5851 | SODA LAKES SUBSTATION | XCEL | LOOKOUT SUBSTATION | XCEL | 70018 | 70266 | Xcel Owned | 5024S | SWITCH | LOOK | 1200 | 1549 | 1486 | 1780 | 478 | 617 | 592 | 709
SODA-LOOK-230.0-1 | 5851 | SODA LAKES SUBSTATION | XCEL | LOOKOUT SUBSTATION | XCEL | 70018 | 70266 | Xcel Owned | 5851S | SWITCH | LOOK | 1200 | 1549 | 1486 | 1780 | 478 | 617 | 592 | 709
SODA-LOOK-230.0-1 | 5851 | SODA LAKES SUBSTATION | XCEL | LOOKOUT SUBSTATION | XCEL | 70018 | 70266 | Xcel Owned | SODA-LOOK-230.0-1 | Transmission Line | 5851 | 1259 | 1259 | 1425 | 1425 | 502 | 502 | 568 | 568
SODA-LOOK-230.0-1 | 5851 | SODA LAKES SUBSTATION | XCEL | LOOKOUT SUBSTATION | XCEL | 70018 | 70266 | Xcel Owned | Narcissus | BUSBAR_SECTION | SODA | 1259 | 1259 | 1425 | 1425 | 502 | 502 | 568 | 568
SOUT-ARLQ_TP-115.0-1 | 9332 | SOUTH SUBSTATION | XCEL | AIR LIQUIDE TAP | XCEL | 70402 | 70531 | Xcel Owned | SOUT-ARLQ_TP-115.0-1 | FACILITY |  | 600 | 775 | 743 | 890 | 120 | 154 | 148 | 177
SOUT-ARLQ_TP-115.0-1 | 9332 | SOUTH SUBSTATION | XCEL | AIR LIQUIDE TAP | XCEL | 70402 | 70531 | Xcel Owned | 9332-1 | SWITCH | SOUT | 600 | 775 | 743 | 890 | 120 | 154 | 148 | 177
SPRU-CHAM-230.0-1 | 5185 | SPRUCE SUBSTATION | XCEL | CHAMBERS SUBSTATION | XCEL | 70528 | 70539 | Xcel Owned | SPRU-CHAM-230.0-1 | FACILITY |  | 1800 | 1800 | 1800 | 1800 | 717 | 717 | 717 | 717
SPRU-CHAM-230.0-1 | 5185 | SPRUCE SUBSTATION | XCEL | CHAMBERS SUBSTATION | XCEL | 70528 | 70539 | Xcel Owned | 5185 AMP XDCR | SECONDARY_CURRENT_LIMITATION | SPRU | 1800 | 1800 | 1800 | 1800 | 717 | 717 | 717 | 717
SPRU-PICA-230.0-1 | 5187 | SPRUCE SUBSTATION | XCEL | PICADILLY | XCEL | 70528 | 70530 | Xcel Owned | SPRU-PICA-230.0-1 | FACILITY |  | 1894 | 2101 | 2173 | 2390 | 755 | 837 | 866 | 952
SPRU-PICA-230.0-1 | 5187 | SPRUCE SUBSTATION | XCEL | PICADILLY | XCEL | 70528 | 70530 | Xcel Owned | 2½" (AL 40) | BUSBAR_SECTION | SPRU | 1894 | 2252 | 2290 | 2581 | 755 | 897 | 912 | 1028
SPRU-PICA-230.0-1 | 5187 | SPRUCE SUBSTATION | XCEL | PICADILLY | XCEL | 70528 | 70530 | Xcel Owned | SPRU-PICA-230.0-1 | Transmission Line | 5187 | 1910 | 2101 | 2173 | 2390 | 761 | 837 | 866 | 952
SPRU-POWH-230.0-1 | 5171 | SPRUCE SUBSTATION | XCEL | POWHATON SUBSTATION | XCEL | 70528 | 70532 | Xcel Owned | SPRU-POWH-230.0-1 | FACILITY |  | 1860 | 2000 | 2000 | 2000 | 741 | 797 | 797 | 797
SPRU-POWH-230.0-1 | 5171 | SPRUCE SUBSTATION | XCEL | POWHATON SUBSTATION | XCEL | 70528 | 70532 | Xcel Owned | SPRU-POWH-230.0-1 | Transmission Line | 5171 | 1860 | 2046 | 2116 | 2328 | 741 | 815 | 843 | 927
SPRU-POWH-230.0-1 | 5171 | SPRUCE SUBSTATION | XCEL | POWHATON SUBSTATION | XCEL | 70528 | 70532 | Xcel Owned | 5171-2 | CIRCUIT_SWITCHER | POWH | 2000 | 2000 | 2000 | 2000 | 797 | 797 | 797 | 797
SRDG-LEMO-230.0-1 | 5115 | SURREY RIDGE | XCEL | LEMON GULCH | XCEL | 70284 | 70533 | Xcel Owned | SRDG-LEMO-230.0-1 | FACILITY |  | 1840 | 2000 | 2000 | 2000 | 733 | 797 | 797 | 797
SRDG-LEMO-230.0-1 | 5115 | SURREY RIDGE | XCEL | LEMON GULCH | XCEL | 70284 | 70533 | Xcel Owned | Swift | BUSBAR_SECTION | LEMO | 1840 | 2025 | 2088 | 2297 | 733 | 807 | 832 | 915
SRDG-LEMO-230.0-1 | 5115 | SURREY RIDGE | XCEL | LEMON GULCH | XCEL | 70284 | 70533 | Xcel Owned | 5115-1 | CIRCUIT_SWITCHER | LEMO | 2000 | 2000 | 2000 | 2000 | 797 | 797 | 797 | 797
SRDG-LEMO-230.0-1 | 5115 | SURREY RIDGE | XCEL | LEMON GULCH | XCEL | 70284 | 70533 | Xcel Owned | 5115-5 | CIRCUIT_SWITCHER | SRDG | 2000 | 2000 | 2000 | 2000 | 797 | 797 | 797 | 797
STEA-FOID-230.0-1 | 5817 | STEAMBOAT SUBSTATION | XCEL | FOIDEL CREEK SUBSTATION | XCEL | 79065 | 79091 | Xcel Owned | STEA-FOID-230.0-1 | FACILITY |  | 1000 | 1000 | 1000 | 1000 | 398 | 398 | 398 | 398
STEA-FOID-230.0-1 | 5817 | STEAMBOAT SUBSTATION | XCEL | FOIDEL CREEK SUBSTATION | XCEL | 79065 | 79091 | Xcel Owned | 5817_135Y_87T2S | SECONDARY_CURRENT_LIMITATION | STEA | 1000 | 1000 | 1000 | 1000 | 398 | 398 | 398 | 398
STEA-FOID-230.0-1 | 5817 | STEAMBOAT SUBSTATION | XCEL | FOIDEL CREEK SUBSTATION | XCEL | 79065 | 79091 | Xcel Owned | 5817 135X | CURRENT_TRANSFORMER | STEA | 1000 | 1000 | 1000 | 1000 | 398 | 398 | 398 | 398
STEA-FOID-230.0-1 | 5817 | STEAMBOAT SUBSTATION | XCEL | FOIDEL CREEK SUBSTATION | XCEL | 79065 | 79091 | Xcel Owned | 5881 246Y | CURRENT_TRANSFORMER | STEA | 1000 | 1000 | 1000 | 1000 | 398 | 398 | 398 | 398
STEA-FOID-230.0-1 | 5817 | STEAMBOAT SUBSTATION | XCEL | FOIDEL CREEK SUBSTATION | XCEL | 79065 | 79091 | Xcel Owned | 5817 135Y | CURRENT_TRANSFORMER | STEA | 1000 | 1000 | 1000 | 1000 | 398 | 398 | 398 | 398
STEA-FOID-230.0-1 | 5817 | STEAMBOAT SUBSTATION | XCEL | FOIDEL CREEK SUBSTATION | XCEL | 79065 | 79091 | Xcel Owned | 5881 246X | CURRENT_TRANSFORMER | STEA | 1000 | 1000 | 1000 | 1000 | 398 | 398 | 398 | 398
STEA-FOID-230.0-1 | 5817 | STEAMBOAT SUBSTATION | XCEL | FOIDEL CREEK SUBSTATION | XCEL | 79065 | 79091 | Xcel Owned | 5817_135X_PK | SECONDARY_CURRENT_LIMITATION | STEA | 1000 | 1000 | 1000 | 1000 | 398 | 398 | 398 | 398
STEA-FOID-230.0-1 | 5817 | STEAMBOAT SUBSTATION | XCEL | FOIDEL CREEK SUBSTATION | XCEL | 79065 | 79091 | Xcel Owned | 5817_135X_87T2P | SECONDARY_CURRENT_LIMITATION | STEA | 1000 | 1000 | 1000 | 1000 | 398 | 398 | 398 | 398
STEA-FOID-230.0-1 | 5817 | STEAMBOAT SUBSTATION | XCEL | FOIDEL CREEK SUBSTATION | XCEL | 79065 | 79091 | Xcel Owned | 5817_135Y_PK | SECONDARY_CURRENT_LIMITATION | STEA | 1000 | 1000 | 1000 | 1000 | 398 | 398 | 398 | 398
STEA-FOID-230.0-2 | 5811 | STEAMBOAT SUBSTATION | XCEL | FOIDEL CREEK SUBSTATION | XCEL | 79065 | 79091 | Xcel Owned | STEA-FOID-230.0-2 | FACILITY |  | 1000 | 1000 | 1000 | 1000 | 398 | 398 | 398 | 398
STEA-FOID-230.0-2 | 5811 | STEAMBOAT SUBSTATION | XCEL | FOIDEL CREEK SUBSTATION | XCEL | 79065 | 79091 | Xcel Owned | 5882_135Y_87T2S | SECONDARY_CURRENT_LIMITATION | STEA | 1000 | 1000 | 1000 | 1000 | 398 | 398 | 398 | 398
STEA-FOID-230.0-2 | 5811 | STEAMBOAT SUBSTATION | XCEL | FOIDEL CREEK SUBSTATION | XCEL | 79065 | 79091 | Xcel Owned | 5882 135X | CURRENT_TRANSFORMER | STEA | 1000 | 1000 | 1000 | 1000 | 398 | 398 | 398 | 398
STEA-FOID-230.0-2 | 5811 | STEAMBOAT SUBSTATION | XCEL | FOIDEL CREEK SUBSTATION | XCEL | 79065 | 79091 | Xcel Owned | 5811 246X | CURRENT_TRANSFORMER | STEA | 1000 | 1000 | 1000 | 1000 | 398 | 398 | 398 | 398
STEA-FOID-230.0-2 | 5811 | STEAMBOAT SUBSTATION | XCEL | FOIDEL CREEK SUBSTATION | XCEL | 79065 | 79091 | Xcel Owned | 5811 246Y | CURRENT_TRANSFORMER | STEA | 1000 | 1000 | 1000 | 1000 | 398 | 398 | 398 | 398
STEA-FOID-230.0-2 | 5811 | STEAMBOAT SUBSTATION | XCEL | FOIDEL CREEK SUBSTATION | XCEL | 79065 | 79091 | Xcel Owned | 5882 135Y | CURRENT_TRANSFORMER | STEA | 1000 | 1000 | 1000 | 1000 | 398 | 398 | 398 | 398
STEA-FOID-230.0-2 | 5811 | STEAMBOAT SUBSTATION | XCEL | FOIDEL CREEK SUBSTATION | XCEL | 79065 | 79091 | Xcel Owned | 5882_135Y_PK | SECONDARY_CURRENT_LIMITATION | STEA | 1000 | 1000 | 1000 | 1000 | 398 | 398 | 398 | 398
STEA-FOID-230.0-2 | 5811 | STEAMBOAT SUBSTATION | XCEL | FOIDEL CREEK SUBSTATION | XCEL | 79065 | 79091 | Xcel Owned | 5882_135X_PK | SECONDARY_CURRENT_LIMITATION | STEA | 1000 | 1000 | 1000 | 1000 | 398 | 398 | 398 | 398
STEA-FOID-230.0-2 | 5811 | STEAMBOAT SUBSTATION | XCEL | FOIDEL CREEK SUBSTATION | XCEL | 79065 | 79091 | Xcel Owned | 5882_135X_87T2P | SECONDARY_CURRENT_LIMITATION | STEA | 1000 | 1000 | 1000 | 1000 | 398 | 398 | 398 | 398
SULL-JEWE-230.0-1 | 5167 | SULLIVAN SUBSTATION | XCEL | JEWELL SUBSTATION | XCEL | 70417 | 70512 | Xcel Owned | SULL-JEWE-230.0-1 | FACILITY |  | 1266 | 1393 | 1443 | 1587 | 504 | 555 | 575 | 632
SULL-JEWE-230.0-1 | 5167 | SULLIVAN SUBSTATION | XCEL | JEWELL SUBSTATION | XCEL | 70417 | 70512 | Xcel Owned | SULL-JEWE-230.0-1 | Transmission Line | 5167 | 1266 | 1393 | 1443 | 1587 | 504 | 555 | 575 | 632
SULL-TECH-230.0-1 | 5705 | SULLIVAN SUBSTATION | XCEL | TECH CENTER SUBSTATION | XCEL | 70417 | 70428 | Xcel Owned | SULL-TECH-230.0-1 | FACILITY |  | 1134 | 1134 | 1334 | 1334 | 452 | 452 | 531 | 531
SULL-TECH-230.0-1 | 5705 | SULLIVAN SUBSTATION | XCEL | TECH CENTER SUBSTATION | XCEL | 70417 | 70428 | Xcel Owned | SULL-TECH-230.0-1 | Transmission Line | 5705 | 1134 | 1134 | 1334 | 1334 | 452 | 452 | 531 | 531
SULP-LEMO-230.0-1 | 5115 | SULPHUR SUBSTATION | XCEL | LEMON GULCH | XCEL | 70524 | 70533 | Xcel Owned | SULP-LEMO-230.0-1 | FACILITY |  | 1841 | 2000 | 2000 | 2000 | 733 | 797 | 797 | 797
SULP-LEMO-230.0-1 | 5115 | SULPHUR SUBSTATION | XCEL | LEMON GULCH | XCEL | 70524 | 70533 | Xcel Owned | Grosbeak | BUSBAR_SECTION | SULP | 1841 | 2025 | 2094 | 2303 | 733 | 807 | 834 | 917
SULP-LEMO-230.0-1 | 5115 | SULPHUR SUBSTATION | XCEL | LEMON GULCH | XCEL | 70524 | 70533 | Xcel Owned | Swift | BUSBAR_SECTION | LEMO | 1841 | 2025 | 2094 | 2303 | 733 | 807 | 834 | 917
SULP-LEMO-230.0-1 | 5115 | SULPHUR SUBSTATION | XCEL | LEMON GULCH | XCEL | 70524 | 70533 | Xcel Owned | 5115-3 | CIRCUIT_SWITCHER | LEMO | 2000 | 2000 | 2000 | 2000 | 797 | 797 | 797 | 797
TARR-HARS-230.0-1 | 5995 | TARRYALL SUBSTATION | XCEL | HARTSEL (CORE) | XCEL | 70427 | 70927 | Xcel Owned | TARR-HARS-230.0-1 | FACILITY |  | 1175 | 1188 | 1255 | 1255 | 468 | 473 | 500 | 500
TARR-HARS-230.0-1 | 5995 | TARRYALL SUBSTATION | XCEL | HARTSEL (CORE) | XCEL | 70427 | 70927 | Xcel Owned | Narcissus | BUSBAR_SECTION | TARR | 1175 | 1380 | 1408 | 1575 | 468 | 550 | 561 | 628
TARR-HARS-230.0-1 | 5995 | TARRYALL SUBSTATION | XCEL | HARTSEL (CORE) | XCEL | 70427 | 70927 | Xcel Owned |  | LINE_TRAP | TARR | 1188 | 1188 | 1255 | 1255 | 473 | 473 | 500 | 500
TARR-WATE-230.0-1 | 5803 | TARRYALL SUBSTATION | XCEL | WATERTON SUBSTATION | XCEL | 70427 | 70464 | Xcel Owned | TARR-WATE-230.0-1 | FACILITY |  | 1175 | 1188 | 1255 | 1255 | 468 | 473 | 500 | 500
TARR-WATE-230.0-1 | 5803 | TARRYALL SUBSTATION | XCEL | WATERTON SUBSTATION | XCEL | 70427 | 70464 | Xcel Owned | Narcissus | BUSBAR_SECTION | TARR | 1175 | 1380 | 1408 | 1575 | 468 | 550 | 561 | 628
TARR-WATE-230.0-1 | 5803 | TARRYALL SUBSTATION | XCEL | WATERTON SUBSTATION | XCEL | 70427 | 70464 | Xcel Owned |  | LINE_TRAP | TARR | 1188 | 1188 | 1255 | 1255 | 473 | 473 | 500 | 500
TOWE-CHAM-230.0-1 | 5907 | TOWER SUBSTATION | XCEL | CHAMBERS SUBSTATION | XCEL | 70432 | 70539 | Xcel Owned | TOWE-CHAM-230.0-1 | FACILITY |  | 1423 | 1566 | 1600 | 1600 | 567 | 624 | 637 | 637
TOWE-CHAM-230.0-1 | 5907 | TOWER SUBSTATION | XCEL | CHAMBERS SUBSTATION | XCEL | 70432 | 70539 | Xcel Owned | Narcissus | BUSBAR_SECTION | TOWE | 1423 | 1566 | 1622 | 1784 | 567 | 624 | 646 | 711
TOWE-CHAM-230.0-1 | 5907 | TOWER SUBSTATION | XCEL | CHAMBERS SUBSTATION | XCEL | 70432 | 70539 | Xcel Owned | 5907-1 | CIRCUIT_SWITCHER | TOWE | 1600 | 1600 | 1600 | 1600 | 637 | 637 | 637 | 637
TOWE-PICA-230.0-1 | 5907 | TOWER SUBSTATION | XCEL | PICADILLY | XCEL | 70432 | 70530 | Xcel Owned | TOWE-PICA-230.0-1 | FACILITY |  | 1423 | 1566 | 1600 | 1600 | 567 | 624 | 637 | 637
TOWE-PICA-230.0-1 | 5907 | TOWER SUBSTATION | XCEL | PICADILLY | XCEL | 70432 | 70530 | Xcel Owned | Narcissus | BUSBAR_SECTION | TOWE | 1423 | 1566 | 1622 | 1784 | 567 | 624 | 646 | 711
TOWE-PICA-230.0-1 | 5907 | TOWER SUBSTATION | XCEL | PICADILLY | XCEL | 70432 | 70530 | Xcel Owned | 5907-2 | CIRCUIT_SWITCHER | TOWE | 1600 | 1600 | 1600 | 1600 | 637 | 637 | 637 | 637
TWLA_TP-OTER_TP-115.0-1 | 9255 | TWIN LAKES TAP | XCEL | OTERO PUMPING STATION | XCEL | 70435 | 70304 | Xcel Owned | TWLA_TP-OTER_TP-115.0-1 | FACILITY |  | 1241 | 1383 | 1281 | 1415 | 247 | 275 | 255 | 282
TWLA_TP-OTER_TP-115.0-1 | 9255 | TWIN LAKES TAP | XCEL | OTERO PUMPING STATION | XCEL | 70435 | 70304 | Xcel Owned | TWLA_TP-OTER_TP-115.0-1 | Transmission Line | 9255 | 1241 | 1383 | 1281 | 1415 | 247 | 275 | 255 | 282
UTEG-COLL-138.0-1 | 3015 | UTE GRAND JUNCTION SUBSTATION | XCEL | COLLBRAN SUBSTATION | XCEL | 79035 | 79047 | Xcel Owned | UTEG-COLL-138.0-1 | FACILITY |  | 579 | 579 | 600 | 600 | 138 | 138 | 143 | 143
UTEG-COLL-138.0-1 | 3015 | UTE GRAND JUNCTION SUBSTATION | XCEL | COLLBRAN SUBSTATION | XCEL | 79035 | 79047 | Xcel Owned | UTEG-COLL-138.0-1 | Transmission Line | 3015 | 579 | 579 | 717 | 717 | 138 | 138 | 171 | 171
UTEG-COLL-138.0-1 | 3015 | UTE GRAND JUNCTION SUBSTATION | XCEL | COLLBRAN SUBSTATION | XCEL | 79035 | 79047 | Xcel Owned | C841 246X | CURRENT_TRANSFORMER | COLL | 600 | 600 | 600 | 600 | 143 | 143 | 143 | 143
UTEG-UTER-345.0-1 | 7302 | UTE GRAND JUNCTION SUBSTATION | XCEL | RIFLE UTE 230/345KV SUBSTATION | XCEL | 79036 | 79058 | Xcel Owned | UTEG-UTER-345.0-1 | FACILITY |  | 1200 | 1200 | 1200 | 1200 | 717 | 717 | 717 | 717
UTEG-UTER-345.0-1 | 7302 | UTE GRAND JUNCTION SUBSTATION | XCEL | RIFLE UTE 230/345KV SUBSTATION | XCEL | 79036 | 79058 | Xcel Owned | G331K V A | CURRENT_TRANSFORMER | UTEG | 1200 | 1200 | 1200 | 1200 | 717 | 717 | 717 | 717
UTEG-UTER-345.0-1 | 7302 | UTE GRAND JUNCTION SUBSTATION | XCEL | RIFLE UTE 230/345KV SUBSTATION | XCEL | 79036 | 79058 | Xcel Owned | G331K W C | CURRENT_TRANSFORMER | UTEG | 1200 | 1200 | 1200 | 1200 | 717 | 717 | 717 | 717
UTEG-UTER-345.0-1 | 7302 | UTE GRAND JUNCTION SUBSTATION | XCEL | RIFLE UTE 230/345KV SUBSTATION | XCEL | 79036 | 79058 | Xcel Owned | G331K W A | CURRENT_TRANSFORMER | UTEG | 1200 | 1200 | 1200 | 1200 | 717 | 717 | 717 | 717
UTEG-UTER-345.0-1 | 7302 | UTE GRAND JUNCTION SUBSTATION | XCEL | RIFLE UTE 230/345KV SUBSTATION | XCEL | 79036 | 79058 | Xcel Owned | G331K V C | CURRENT_TRANSFORMER | UTEG | 1200 | 1200 | 1200 | 1200 | 717 | 717 | 717 | 717
UTEG-UTER-345.0-1 | 7302 | UTE GRAND JUNCTION SUBSTATION | XCEL | RIFLE UTE 230/345KV SUBSTATION | XCEL | 79036 | 79058 | Xcel Owned | G331K W B | CURRENT_TRANSFORMER | UTEG | 1200 | 1200 | 1200 | 1200 | 717 | 717 | 717 | 717
UTEG-UTER-345.0-1 | 7302 | UTE GRAND JUNCTION SUBSTATION | XCEL | RIFLE UTE 230/345KV SUBSTATION | XCEL | 79036 | 79058 | Xcel Owned | G331K V B | CURRENT_TRANSFORMER | UTEG | 1200 | 1200 | 1200 | 1200 | 717 | 717 | 717 | 717
UTER-MEEK-345.0-1 | 7300 | RIFLE UTE 230/345KV SUBSTATION | XCEL | MEEKER (TRI STATE) | FOREIGN | 79058 | 79266 | Jointly Owned | UTER-MEEK-345.0-1 | FACILITY |  | 1584 | 1584 | 1600 | 1673 | 947 | 947 | 956 | 1000
UTER-MEEK-345.0-1 | 7300 | RIFLE UTE 230/345KV SUBSTATION | XCEL | MEEKER (TRI STATE) | FOREIGN | 79058 | 79266 | Jointly Owned |  | LINE_TRAP | UTER | 1584 | 1584 | 1673 | 1673 | 947 | 947 | 1000 | 1000
UTER-MEEK-345.0-1 | 7300 | RIFLE UTE 230/345KV SUBSTATION | XCEL | MEEKER (TRI STATE) | FOREIGN | 79058 | 79266 | Jointly Owned | Foreign Ratings | Foreign Ratings | MEEK | 1600 | 2063 | 1600 | 2063 | 956 | 1233 | 956 | 1233
UTER-RIFL-230.0-1 | 3007 | RIFLE UTE 230/345KV SUBSTATION | XCEL | RIFLE (WAPA) | FOREIGN | 79057 | 79059 | Jointly Owned | UTER-RIFL-230.0-1 | FACILITY |  | 1200 | 1318 | 1318 | 1318 | 478 | 525 | 525 | 525
UTER-RIFL-230.0-1 | 3007 | RIFLE UTE 230/345KV SUBSTATION | XCEL | RIFLE (WAPA) | FOREIGN | 79057 | 79059 | Jointly Owned | 55134W | SWITCH | UTER | 1200 | 1549 | 1486 | 1780 | 478 | 617 | 592 | 709
UTER-RIFL-230.0-1 | 3007 | RIFLE UTE 230/345KV SUBSTATION | XCEL | RIFLE (WAPA) | FOREIGN | 79057 | 79059 | Jointly Owned | 55134E | SWITCH | UTER | 1200 | 1549 | 1486 | 1780 | 478 | 617 | 592 | 709
UTER-RIFL-230.0-1 | 3007 | RIFLE UTE 230/345KV SUBSTATION | XCEL | RIFLE (WAPA) | FOREIGN | 79057 | 79059 | Jointly Owned | Foreign Ratings | Foreign Ratings | RIFL | 1318 | 1318 | 1318 | 1318 | 525 | 525 | 525 | 525
VAIL-AVON-115.0-1 | 8425 | VAIL SUBSTATION | XCEL | AVON SUBSTATION | XCEL | 79066 | 79092 | Jointly Owned | VAIL-AVON-115.0-1 | FACILITY |  | 600 | 775 | 743 | 800 | 120 | 154 | 148 | 159
VAIL-AVON-115.0-1 | 8425 | VAIL SUBSTATION | XCEL | AVON SUBSTATION | XCEL | 79066 | 79092 | Jointly Owned | 552 | SWITCH | AVON | 600 | 775 | 743 | 890 | 120 | 154 | 148 | 177
VAIL-AVON-115.0-1 | 8425 | VAIL SUBSTATION | XCEL | AVON SUBSTATION | XCEL | 79066 | 79092 | Jointly Owned | 514 | SWITCH | AVON | 600 | 775 | 743 | 890 | 120 | 154 | 148 | 177
VAIL-AVON-115.0-1 | 8425 | VAIL SUBSTATION | XCEL | AVON SUBSTATION | XCEL | 79066 | 79092 | Jointly Owned | 512 | SWITCH | AVON | 600 | 775 | 743 | 890 | 120 | 154 | 148 | 177
VAIL-AVON-115.0-1 | 8425 | VAIL SUBSTATION | XCEL | AVON SUBSTATION | XCEL | 79066 | 79092 | Jointly Owned | 564 | SWITCH | AVON | 600 | 775 | 743 | 890 | 120 | 154 | 148 | 177
VAIL-AVON-115.0-1 | 8425 | VAIL SUBSTATION | XCEL | AVON SUBSTATION | XCEL | 79066 | 79092 | Jointly Owned | 532 | SWITCH | AVON | 600 | 775 | 743 | 890 | 120 | 154 | 148 | 177
VAIL-AVON-115.0-1 | 8425 | VAIL SUBSTATION | XCEL | AVON SUBSTATION | XCEL | 79066 | 79092 | Jointly Owned | 554 | SWITCH | AVON | 600 | 775 | 743 | 890 | 120 | 154 | 148 | 177
VAIL-AVON-115.0-1 | 8425 | VAIL SUBSTATION | XCEL | AVON SUBSTATION | XCEL | 79066 | 79092 | Jointly Owned | 534 | SWITCH | AVON | 600 | 775 | 743 | 890 | 120 | 154 | 148 | 177
VAIL-AVON-115.0-1 | 8425 | VAIL SUBSTATION | XCEL | AVON SUBSTATION | XCEL | 79066 | 79092 | Jointly Owned | 511_246X_PK2 | SECONDARY_CURRENT_LIMITATION | AVON | 800 | 800 | 800 | 800 | 159 | 159 | 159 | 159
VAIL-AVON-115.0-1 | 8425 | VAIL SUBSTATION | XCEL | AVON SUBSTATION | XCEL | 79066 | 79092 | Jointly Owned | 551 246Y | CURRENT_TRANSFORMER | AVON | 800 | 800 | 800 | 800 | 159 | 159 | 159 | 159
VAIL-AVON-115.0-1 | 8425 | VAIL SUBSTATION | XCEL | AVON SUBSTATION | XCEL | 79066 | 79092 | Jointly Owned | 511_246Y_PK2 | SECONDARY_CURRENT_LIMITATION | AVON | 800 | 800 | 800 | 800 | 159 | 159 | 159 | 159
VAIL-AVON-115.0-1 | 8425 | VAIL SUBSTATION | XCEL | AVON SUBSTATION | XCEL | 79066 | 79092 | Jointly Owned | 551_246Y_PK2 | SECONDARY_CURRENT_LIMITATION | AVON | 800 | 800 | 800 | 800 | 159 | 159 | 159 | 159
VAIL-AVON-115.0-1 | 8425 | VAIL SUBSTATION | XCEL | AVON SUBSTATION | XCEL | 79066 | 79092 | Jointly Owned | 551 246X | CURRENT_TRANSFORMER | AVON | 800 | 800 | 800 | 800 | 159 | 159 | 159 | 159
VAIL-AVON-115.0-1 | 8425 | VAIL SUBSTATION | XCEL | AVON SUBSTATION | XCEL | 79066 | 79092 | Jointly Owned | 551_246X_PK2 | SECONDARY_CURRENT_LIMITATION | AVON | 800 | 800 | 800 | 800 | 159 | 159 | 159 | 159
VAIL-AVON-115.0-1 | 8425 | VAIL SUBSTATION | XCEL | AVON SUBSTATION | XCEL | 79066 | 79092 | Jointly Owned | 511 246X | CURRENT_TRANSFORMER | AVON | 800 | 800 | 800 | 800 | 159 | 159 | 159 | 159
VAIL-AVON-115.0-1 | 8425 | VAIL SUBSTATION | XCEL | AVON SUBSTATION | XCEL | 79066 | 79092 | Jointly Owned | 511 246Y | CURRENT_TRANSFORMER | AVON | 800 | 800 | 800 | 800 | 159 | 159 | 159 | 159
VAIL-WOLC-115.0-1 | 8416 | VAIL SUBSTATION | XCEL | WOLCOTT (HCEA) | FOREIGN | 79066 | 79068 | Jointly Owned | VAIL-WOLC-115.0-1 | FACILITY |  | 881 | 900 | 900 | 900 | 175 | 179 | 179 | 179
VAIL-WOLC-115.0-1 | 8416 | VAIL SUBSTATION | XCEL | WOLCOTT (HCEA) | FOREIGN | 79066 | 79068 | Jointly Owned | Arbutus | BUSBAR_SECTION | VAIL | 881 | 1030 | 1053 | 1174 | 175 | 205 | 210 | 234
VAIL-WOLC-115.0-1 | 8416 | VAIL SUBSTATION | XCEL | WOLCOTT (HCEA) | FOREIGN | 79066 | 79068 | Jointly Owned | 8430_246Y_PK2 | SECONDARY_CURRENT_LIMITATION | VAIL | 900 | 900 | 900 | 900 | 179 | 179 | 179 | 179
VALM-SIMM-230.0-1 | 5389 | VALMONT SWITCHYARD SUBSTATION | XCEL | SIMMS SUBSTATION | XCEL | 70447 | 70543 | Xcel Owned | VALM-SIMM-230.0-1 | FACILITY |  | 1199 | 1199 | 1200 | 1200 | 478 | 478 | 478 | 478
VALM-SIMM-230.0-1 | 5389 | VALMONT SWITCHYARD SUBSTATION | XCEL | SIMMS SUBSTATION | XCEL | 70447 | 70543 | Xcel Owned | VALM-SIMM-230.0-1 | Transmission Line | 5389 | 1199 | 1199 | 1386 | 1386 | 478 | 478 | 552 | 552
VALM-SIMM-230.0-1 | 5389 | VALMONT SWITCHYARD SUBSTATION | XCEL | SIMMS SUBSTATION | XCEL | 70447 | 70543 | Xcel Owned | 5382_246Y_PKG-BF | SECONDARY_CURRENT_LIMITATION | VALM | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
VALM-SIMM-230.0-1 | 5389 | VALMONT SWITCHYARD SUBSTATION | XCEL | SIMMS SUBSTATION | XCEL | 70447 | 70543 | Xcel Owned | 5389_135Y_PKG-BF | SECONDARY_CURRENT_LIMITATION | VALM | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
VALM-SPIN-230.0-1 | 5385 | VALMONT SWITCHYARD SUBSTATION | XCEL | SPINDLE SUBSTATION | XCEL | 70447 | 70592 | Xcel Owned | VALM-SPIN-230.0-1 | FACILITY |  | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
VALM-SPIN-230.0-1 | 5385 | VALMONT SWITCHYARD SUBSTATION | XCEL | SPINDLE SUBSTATION | XCEL | 70447 | 70592 | Xcel Owned | 5385_135Y_PKG-BF | SECONDARY_CURRENT_LIMITATION | VALM | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
VALM-SPIN-230.0-1 | 5385 | VALMONT SWITCHYARD SUBSTATION | XCEL | SPINDLE SUBSTATION | XCEL | 70447 | 70592 | Xcel Owned | 5382_246Y_PKG-BF | SECONDARY_CURRENT_LIMITATION | VALM | 1200 | 1200 | 1200 | 1200 | 478 | 478 | 478 | 478
WASH-JLGR-230.0-1 | 5527 | WASHINGTON SUBSTATION | XCEL | J. L. Green | FOREIGN | 70461 | 70529 | Xcel Owned | WASH-JLGR-230.0-1 | FACILITY |  | 1427 | 1570 | 1599 | 1600 | 569 | 625 | 637 | 637
WASH-JLGR-230.0-1 | 5527 | WASHINGTON SUBSTATION | XCEL | J. L. Green | FOREIGN | 70461 | 70529 | Xcel Owned | Narcissus | BUSBAR_SECTION | WASH | 1427 | 1570 | 1626 | 1789 | 569 | 625 | 648 | 713
WASH-JLGR-230.0-1 | 5527 | WASHINGTON SUBSTATION | XCEL | J. L. Green | FOREIGN | 70461 | 70529 | Xcel Owned | Foreign Ratings | Foreign Ratings | JLGR | 1599 | 1627 | 1599 | 1627 | 637 | 648 | 637 | 648
WASH-JLGR-230.0-1 | 5527 | WASHINGTON SUBSTATION | XCEL | J. L. Green | FOREIGN | 70461 | 70529 | Xcel Owned | 5527-3 | CIRCUIT_SWITCHER | WASH | 1600 | 1600 | 1600 | 1600 | 637 | 637 | 637 | 637
WATE-MART_TP-115.0-1 | 9337 | WATERTON SUBSTATION | XCEL | MARTIN TAP | XCEL | 70463 | 70484 | Xcel Owned | WATE-MART_TP-115.0-1 | FACILITY |  | 1200 | 1200 | 1200 | 1200 | 239 | 239 | 239 | 239
WATE-MART_TP-115.0-1 | 9337 | WATERTON SUBSTATION | XCEL | MARTIN TAP | XCEL | 70463 | 70484 | Xcel Owned | 9337_135Y_51B | SECONDARY_CURRENT_LIMITATION | WATE | 1200 | 1200 | 1200 | 1200 | 239 | 239 | 239 | 239
WELD-ARRL-115.0-1 | 9996 | WELD SUBSTATION | XCEL | ARROWHEAD SUBSTATION | XCEL | 70470 | 70475 | Xcel Owned | WELD-ARRL-115.0-1 | FACILITY |  | 800 | 880 | 910 | 1001 | 159 | 175 | 181 | 199
WELD-ARRL-115.0-1 | 9996 | WELD SUBSTATION | XCEL | ARROWHEAD SUBSTATION | XCEL | 70470 | 70475 | Xcel Owned | WELD-ARRL-115.0-1 | Transmission Line | 9996 | 800 | 880 | 910 | 1001 | 159 | 175 | 181 | 199
WOLC-FOID-230.0-1 | 5813 | WOLCOTT (HCEA) | FOREIGN | FOIDEL CREEK SUBSTATION | XCEL | 79069 | 79091 | Jointly Owned | WOLC-FOID-230.0-1 | FACILITY |  | 1402 | 1543 | 1599 | 1599 | 559 | 615 | 637 | 637
WOLC-FOID-230.0-1 | 5813 | WOLCOTT (HCEA) | FOREIGN | FOIDEL CREEK SUBSTATION | XCEL | 79069 | 79091 | Jointly Owned | Narcissus | BUSBAR_SECTION | FOID | 1402 | 1543 | 1600 | 1759 | 559 | 615 | 637 | 701
WOLC-FOID-230.0-1 | 5813 | WOLCOTT (HCEA) | FOREIGN | FOIDEL CREEK SUBSTATION | XCEL | 79069 | 79091 | Jointly Owned | Foreign Ratings | Foreign Ratings | WOLC | 1461 | 1599 | 1599 | 1599 | 582 | 637 | 637 | 637
WOOD-DIVI-115.0-1 | 8455 | WOODLAND PARK SUBSTATION | XCEL | DIVIDE SUBSTATION | XCEL | 70476 | 70157 | Xcel Owned | WOOD-DIVI-115.0-1 | FACILITY |  | 600 | 600 | 600 | 600 | 120 | 120 | 120 | 120
WOOD-DIVI-115.0-1 | 8455 | WOODLAND PARK SUBSTATION | XCEL | DIVIDE SUBSTATION | XCEL | 70476 | 70157 | Xcel Owned | 8455-1 | CIRCUIT_SWITCHER | WOOD | 600 | 600 | 600 | 600 | 120 | 120 | 120 | 120
WOOD-FLAK-115.0-1 | 8455 | WOODLAND PARK SUBSTATION | XCEL | FOREST LAKE | XCEL | 70476 | 73476 | Xcel Owned | WOOD-FLAK-115.0-1 | FACILITY |  | 600 | 600 | 600 | 600 | 120 | 120 | 120 | 120
WOOD-FLAK-115.0-1 | 8455 | WOODLAND PARK SUBSTATION | XCEL | FOREST LAKE | XCEL | 70476 | 73476 | Xcel Owned | 262_135X_W/VAR_XDCR | SECONDARY_CURRENT_LIMITATION | FLAK | 600 | 600 | 600 | 600 | 120 | 120 | 120 | 120
WOOD-FLAK-115.0-1 | 8455 | WOODLAND PARK SUBSTATION | XCEL | FOREST LAKE | XCEL | 70476 | 73476 | Xcel Owned | 8455-2 | CIRCUIT_SWITCHER | WOOD | 600 | 600 | 600 | 600 | 120 | 120 | 120 | 120

## Manually Rated
|  |  | FAC-008-5 Transmission Lines |  |  |  | OPCO: PSC |  |  | VALIDATION STATUS: VALID | [5 empty] | OWNERSHIP: Jointly Owned,Xcel Owned
[7 empty] | BES: Y |  |  | LIFE CYCLE STATUS: AS BUILT
FACILITY DESIGNATION | LINE NAME | FROM SUB | FROM SUB OWNER | TO SUB | TO SUB OWNER | FROM PSSE | TO PSSE | FACILITY OWNERSHIP | EQUIP NAME | EQUIP TYPE | EQUIP LOCATION | SN (AMPS) | SE (AMPS) | WN (AMPS) | WE (AMPS) | SN (MVA) | SE (MVA) | WN (MVA) | WE (MVA) | COMMENTS
BEAV-BEVW-115.0-1 | 9409 | BEAVER CREEK EAST SUBSTATION | XCEL | BEAVER CREEK (WAPA) | FOREIGN |  |  | Jointly Owned | BEAV-BEVW-115.0-1 | FACILITY |  | 1889 | 1920 | 1920 | 1920 | 376 | 382 | 382 | 382 | 115kV BUS TIE
BEAV-BEVW-115.0-1 | 9409 | BEAVER CREEK EAST SUBSTATION | XCEL | BEAVER CREEK (WAPA) | FOREIGN |  |  | Jointly Owned | 2-795 ACSR CONDUCTOR | BUSBAR_SECTION | BEAV | 1889 | 2202 | 2250 | 2505 | 376 | 439 | 439 | 439
BEAV-BEVW-115.0-1 | 9409 | BEAVER CREEK EAST SUBSTATION | XCEL | BEAVER CREEK (WAPA) | FOREIGN |  |  | Jointly Owned | 2-795 ACSR CONDUCTOR | BUSBAR_SECTION | BEVW | 1889 | 2202 | 2250 | 2505 | 376 | 439 | 439 | 439
BEAV-BEVW-115.0-1 | 9409 | BEAVER CREEK EAST SUBSTATION | XCEL | BEAVER CREEK (WAPA) | FOREIGN |  |  | Jointly Owned | KD41 21Z3 | SECONDARY_CURRENT_LIMITATION | BEAV | 1920 | 1920 | 1920 | 1920 | 382 | 382 | 382 | 382
MIDW-115.0-BKR-9641 | 9641-A | MIDWAY NODE A | XCEL | MIDWAY BANK #1 | XCEL |  |  | Xcel Owned | MIDW-115.0-BKR-9641 | FACILITY |  | 400 | 400 | 400 | 400 | 80 | 80 | 80 | 80
MIDW-115.0-BKR-9641 | 9641-A | MIDWAY NODE A | XCEL | MIDWAY BANK #1 | XCEL |  |  | Xcel Owned | Black Hills Relay | SECONDARY_CURRENT_LIMITATION | MIDW | 400 | 400 | 400 | 400 | 80 | 80 | 80 | 80
WELD-WEDW-230.0-1 | 5223 | WELD | XCEL | WELD (WAPA) | FOREIGN |  |  | Jointly Owned | WELD-WEDW-115.0-1 | FACILITY |  | 2157 | 2400 | 2400 | 2400 | 859 | 956 | 956 | 956
WELD-WEDW-230.0-1 | 5223 | WELD | XCEL | WELD (WAPA) | FOREIGN |  |  | Jointly Owned | 5220 | SWITCH | WELD | 2157 | 2533 | 2472 | 2761 | 859 | 1009.0755 | 984.7748 | 1099.9042
WELD-WEDW-230.0-1 | 5223 | WELD | XCEL | WELD (WAPA) | FOREIGN |  |  | Jointly Owned | 5223 135X | CURRENT_TRANSFORMER | WELD | 2400 | 2400 | 2400 | 2400 | 956 | 956 | 956 | 956
WELD-WEDW-230.0-1 | 5223 | WELD | XCEL | WELD (WAPA) | FOREIGN |  |  | Jointly Owned | 5223 135Y | CURRENT_TRANSFORMER | WELD | 2400 | 2400 | 2400 | 2400 | 956 | 956 | 956 | 956
WELD-WEDW-230.0-1 | 5223 | WELD | XCEL | WELD (WAPA) | FOREIGN |  |  | Jointly Owned | 5223 246X | CURRENT_TRANSFORMER | WELD | 2400 | 2400 | 2400 | 2400 | 956 | 956 | 956 | 956
WELD-WEDW-230.0-1 | 5223 | WELD | XCEL | WELD (WAPA) | FOREIGN |  |  | Jointly Owned | 5223 246Y | CURRENT_TRANSFORMER | WELD | 2400 | 2400 | 2400 | 2400 | 956 | 956 | 956 | 956
WELD-WEDW-230.0-1 | 5223 | WELD | XCEL | WELD (WAPA) | FOREIGN |  |  | Jointly Owned | 5221 135X | CURRENT_TRANSFORMER | WELD | 2400 | 2400 | 2400 | 2400 | 956 | 956 | 956 | 956
WELD-WEDW-230.0-1 | 5223 | WELD | XCEL | WELD (WAPA) | FOREIGN |  |  | Jointly Owned | 5221 135Y | CURRENT_TRANSFORMER | WELD | 2400 | 2400 | 2400 | 2400 | 956 | 956 | 956 | 956
WELD-WEDW-230.0-1 | 5223 | WELD | XCEL | WELD (WAPA) | FOREIGN |  |  | Jointly Owned | 5221 246X | CURRENT_TRANSFORMER | WELD | 2400 | 2400 | 2400 | 2400 | 956 | 956 | 956 | 956
WELD-WEDW-230.0-1 | 5223 | WELD | XCEL | WELD (WAPA) | FOREIGN |  |  | Jointly Owned | 5221 246Y | CURRENT_TRANSFORMER | WELD | 2400 | 2400 | 2400 | 2400 | 956 | 956 | 956 | 956
WELD-WEDW-230.0-1 | 5223 | WELD | XCEL | WELD (WAPA) | FOREIGN |  |  | Jointly Owned | Meter | CURRENT_TRANSFORMER | WELD | 2400 | 2400 | 2400 | 2400 | 956 | 956 | 956 | 956

## Line Ratings In Construction
|  |  | FAC-008-5 Transmission Lines |  |  |  | OPCO: PSC |  |  | VALIDATION STATUS: VALID | [5 empty] | OWNERSHIP: Jointly Owned,Xcel Owned
[7 empty] | BES: Y |  |  | LIFE CYCLE STATUS: IN CONSTRUCTION
FACILITY DESIGNATION | LINE NAME | FROM SUB | FROM SUB OWNER | TO SUB | TO SUB OWNER | FROM PSSE | TO PSSE | FACILITY OWNERSHIP | EQUIP NAME | EQUIP TYPE | EQUIP LOCATION | SN (AMPS) | SE (AMPS) | WN (AMPS) | WE (AMPS) | SN (MVA) | SE (MVA) | WN (MVA) | WE (MVA) | COMMENTS
COMA-TUND-345.0-1 | 7015 | COMANCHE SUBSTATION | XCEL | TUNDRA SUBSTATION | XCEL | 70654 | 70653 | Xcel Owned | COMA-TUND-345.0-1 | FACILITY |  | 2000 | 2000 | 2112 | 2112 | 1195 | 1195 | 1262 | 1262
COMA-TUND-345.0-1 | 7015 | COMANCHE SUBSTATION | XCEL | TUNDRA SUBSTATION | XCEL | 70654 | 70653 | Xcel Owned |  | LINE_TRAP | COMA | 2000 | 2000 | 2112 | 2112 | 1195 | 1195 | 1262 | 1262
DAKO-DTER-230.0-1 | 5623 | DAKOTA SUBSTATION | XCEL | DENVER TERMINAL SUBSTATION | XCEL | 70141 | 70149 | Xcel Owned | DAKO-DTER-230.0-1 | FACILITY |  | 1220 | 1427 | 1457 | 1600 | 486 | 568 | 580 | 637
DAKO-DTER-230.0-1 | 5623 | DAKOTA SUBSTATION | XCEL | DENVER TERMINAL SUBSTATION | XCEL | 70141 | 70149 | Xcel Owned | Narcissus | BUSBAR_SECTION | DTER | 1220 | 1427 | 1457 | 1626 | 486 | 568 | 580 | 648
DAKO-DTER-230.0-1 | 5623 | DAKOTA SUBSTATION | XCEL | DENVER TERMINAL SUBSTATION | XCEL | 70141 | 70149 | Xcel Owned | 5623-1 | BREAKER | DAKO | 1600 | 1600 | 1600 | 1600 | 637 | 637 | 637 | 637
DANI-PRAI-230.0-2 | 5707 | DANIELS PARK 115 & 230KV SUBSTATION | XCEL | PRAIRIE SUBSTATION | XCEL | 70139 | 70331 | Xcel Owned | DANI-PRAI-230.0-2 | FACILITY |  | 1445 | 1590 | 1600 | 1600 | 576 | 633 | 637 | 637
DANI-PRAI-230.0-2 | 5707 | DANIELS PARK 115 & 230KV SUBSTATION | XCEL | PRAIRIE SUBSTATION | XCEL | 70139 | 70331 | Xcel Owned | DANI-PRAI-230.0-2 | Transmission Line | 5707 | 1445 | 1590 | 1648 | 1813 | 576 | 633 | 657 | 722
DANI-PRAI-230.0-2 | 5707 | DANIELS PARK 115 & 230KV SUBSTATION | XCEL | PRAIRIE SUBSTATION | XCEL | 70139 | 70331 | Xcel Owned | 5707-1 | BREAKER | PRAI | 1600 | 1600 | 1600 | 1600 | 637 | 637 | 637 | 637
DTER-FEDC_TP-115.0-1 | 9122 | DENVER TERMINAL SUBSTATION | XCEL | FEDERAL CENTER TAP | XCEL | 70144 | 70173 | Xcel Owned | DTER-FEDC_TP-115.0-1 | FACILITY |  | 1200 | 1200 | 1200 | 1200 | 239 | 239 | 239 | 239
DTER-FEDC_TP-115.0-1 | 9122 | DENVER TERMINAL SUBSTATION | XCEL | FEDERAL CENTER TAP | XCEL | 70144 | 70173 | Xcel Owned | 9122 246X 67GP | SECONDARY_CURRENT_LIMITATION | DTER | 1200 | 1200 | 1200 | 1200 | 239 | 239 | 239 | 239
DTER-FEDC_TP-115.0-1 | 9122 | DENVER TERMINAL SUBSTATION | XCEL | FEDERAL CENTER TAP | XCEL | 70144 | 70173 | Xcel Owned | 9122 246X 21ZP | SECONDARY_CURRENT_LIMITATION | DTER | 1200 | 1200 | 1200 | 1200 | 239 | 239 | 239 | 239
DTER-FEDC_TP-115.0-1 | 9122 | DENVER TERMINAL SUBSTATION | XCEL | FEDERAL CENTER TAP | XCEL | 70144 | 70173 | Xcel Owned | 9122 246Y 21Z2 | SECONDARY_CURRENT_LIMITATION | DTER | 1200 | 1200 | 1200 | 1200 | 239 | 239 | 239 | 239
DTER-FEDC_TP-115.0-1 | 9122 | DENVER TERMINAL SUBSTATION | XCEL | FEDERAL CENTER TAP | XCEL | 70144 | 70173 | Xcel Owned | 9122 246Y 21Z1 | SECONDARY_CURRENT_LIMITATION | DTER | 1200 | 1200 | 1200 | 1200 | 239 | 239 | 239 | 239
DTER-FEDC_TP-115.0-1 | 9122 | DENVER TERMINAL SUBSTATION | XCEL | FEDERAL CENTER TAP | XCEL | 70144 | 70173 | Xcel Owned | Curlew | BUSBAR_SECTION | DTER | 1200 | 1392 | 1442 | 1586 | 239 | 277 | 287 | 316
DTER-FEDC_TP-115.0-1 | 9122 | DENVER TERMINAL SUBSTATION | XCEL | FEDERAL CENTER TAP | XCEL | 70144 | 70173 | Xcel Owned | DTER-FEDC_TP-115.0-1 | Transmission Line | 9122 | 1200 | 1392 | 1442 | 1586 | 239 | 277 | 287 | 316
DTER-FEDC_TP-115.0-1 | 9122 | DENVER TERMINAL SUBSTATION | XCEL | FEDERAL CENTER TAP | XCEL | 70144 | 70173 | Xcel Owned | 9122L | SWITCH | DTER | 1200 | 1549 | 1486 | 1780 | 239 | 309 | 296 | 355
DTER-FEDC_TP-115.0-1 | 9122 | DENVER TERMINAL SUBSTATION | XCEL | FEDERAL CENTER TAP | XCEL | 70144 | 70173 | Xcel Owned | 9122M | SWITCH | DTER | 1200 | 1549 | 1486 | 1780 | 239 | 309 | 296 | 355
DTER-GRAY-115.0-1 | 9008 | DENVER TERMINAL SUBSTATION | XCEL | GRAY STREET SUBSTATION | XCEL | 70148 | 70208 | Xcel Owned | DTER-GRAY-115.0-1 | FACILITY |  | 1200 | 1200 | 1200 | 1200 | 239 | 239 | 239 | 239
DTER-GRAY-115.0-1 | 9008 | DENVER TERMINAL SUBSTATION | XCEL | GRAY STREET SUBSTATION | XCEL | 70148 | 70208 | Xcel Owned | 9008_246Y_METER_W | SECONDARY_CURRENT_LIMITATION | GRAY | 1200 | 1200 | 1200 | 1200 | 239 | 239 | 239 | 239
DTER-GRAY-115.0-1 | 9008 | DENVER TERMINAL SUBSTATION | XCEL | GRAY STREET SUBSTATION | XCEL | 70148 | 70208 | Xcel Owned | 9008_246Y_XDCR_W | SECONDARY_CURRENT_LIMITATION | GRAY | 1200 | 1200 | 1200 | 1200 | 239 | 239 | 239 | 239
DTER-GRAY-115.0-1 | 9008 | DENVER TERMINAL SUBSTATION | XCEL | GRAY STREET SUBSTATION | XCEL | 70148 | 70208 | Xcel Owned | 9008_246Y_METER_VAR | SECONDARY_CURRENT_LIMITATION | GRAY | 1200 | 1200 | 1200 | 1200 | 239 | 239 | 239 | 239
DTER-GRAY-115.0-1 | 9008 | DENVER TERMINAL SUBSTATION | XCEL | GRAY STREET SUBSTATION | XCEL | 70148 | 70208 | Xcel Owned | 9008_246Y_METER_AMPSW | SECONDARY_CURRENT_LIMITATION | GRAY | 1200 | 1200 | 1200 | 1200 | 239 | 239 | 239 | 239
DTER-GRAY-115.0-1 | 9008 | DENVER TERMINAL SUBSTATION | XCEL | GRAY STREET SUBSTATION | XCEL | 70148 | 70208 | Xcel Owned | 9008_135Y_67GS | SECONDARY_CURRENT_LIMITATION | GRAY | 1200 | 1200 | 1200 | 1200 | 239 | 239 | 239 | 239
DTER-GRAY-115.0-1 | 9008 | DENVER TERMINAL SUBSTATION | XCEL | GRAY STREET SUBSTATION | XCEL | 70148 | 70208 | Xcel Owned | 9008_246Y_XDCR_VAR | SECONDARY_CURRENT_LIMITATION | GRAY | 1200 | 1200 | 1200 | 1200 | 239 | 239 | 239 | 239
DTER-GRAY-115.0-1 | 9008 | DENVER TERMINAL SUBSTATION | XCEL | GRAY STREET SUBSTATION | XCEL | 70148 | 70208 | Xcel Owned | 9008M | SWITCH | GRAY | 1200 | 1549 | 1486 | 1780 | 239 | 309 | 296 | 355
DTER-GRAY-115.0-1 | 9008 | DENVER TERMINAL SUBSTATION | XCEL | GRAY STREET SUBSTATION | XCEL | 70148 | 70208 | Xcel Owned | 9008M | SWITCH | DTER | 1200 | 1549 | 1486 | 1780 | 239 | 309 | 296 | 355
DTER-GRAY-115.0-1 | 9008 | DENVER TERMINAL SUBSTATION | XCEL | GRAY STREET SUBSTATION | XCEL | 70148 | 70208 | Xcel Owned | 9008L | SWITCH | GRAY | 1200 | 1549 | 1486 | 1780 | 239 | 309 | 296 | 355
DTER-WEST-230.0-1 | 5629 | DENVER TERMINAL SUBSTATION | XCEL | WEST SUBSTATION | XCEL | 70149 | 70480 | Xcel Owned | DTER-WEST-230.0-1 | FACILITY |  | 1263 | 1389 | 1439 | 1583 | 503 | 553 | 573 | 631
DTER-WEST-230.0-1 | 5629 | DENVER TERMINAL SUBSTATION | XCEL | WEST SUBSTATION | XCEL | 70149 | 70480 | Xcel Owned | DTER-WEST-230.0-1 | Transmission Line | 5629 | 1263 | 1389 | 1439 | 1583 | 503 | 553 | 573 | 631
EAST-CHAM-115.0-1 | 9175 | EAST SUBSTATION | XCEL | CHAMBERS SUBSTATION | XCEL | 70162 | 70538 | Xcel Owned | EAST-CHAM-115.0-1 | FACILITY |  | 798 | 878 | 908 | 998 | 159 | 175 | 181 | 199
EAST-CHAM-115.0-1 | 9175 | EAST SUBSTATION | XCEL | CHAMBERS SUBSTATION | XCEL | 70162 | 70538 | Xcel Owned | EAST-CHAM-115.0-1 | Transmission Line | 9175 | 798 | 878 | 908 | 998 | 159 | 175 | 181 | 199
EAST-FITZ-115.0-1 | 9178 | EAST SUBSTATION | XCEL | FITZSIMONS SUBSTATION | XCEL | 70162 | 70537 | Xcel Owned | EAST-FITZ-115.0-1 | FACILITY |  | 798 | 878 | 908 | 998 | 159 | 175 | 181 | 199
EAST-FITZ-115.0-1 | 9178 | EAST SUBSTATION | XCEL | FITZSIMONS SUBSTATION | XCEL | 70162 | 70537 | Xcel Owned | EAST-FITZ-115.0-1 | Transmission Line | 9178 | 798 | 878 | 908 | 998 | 159 | 175 | 181 | 199
EAST-SMOK-115.0-2 | 9866 | EAST SUBSTATION | XCEL | SMOKY HILL SUBSTATION | XCEL | 70171 | 70395 | Xcel Owned | EAST-SMOK-115.0-2 | FACILITY |  | 794 | 873 | 903 | 993 | 158 | 174 | 180 | 198
EAST-SMOK-115.0-2 | 9866 | EAST SUBSTATION | XCEL | SMOKY HILL SUBSTATION | XCEL | 70171 | 70395 | Xcel Owned | EAST-SMOK-115.0-2 | Transmission Line | 9866 | 794 | 873 | 903 | 993 | 158 | 174 | 180 | 198
FLUP-PVAL-115.0-1 | 9499 | FORT LUPTON SUBSTATION | XCEL | PLATTE VALLEY | XCEL | 70090 | 70307 | Xcel Owned | FLUP-PVAL-115.0-1 | FACILITY |  | 1200 | 1330 | 1377 | 1515 | 239 | 265 | 274 | 302
FLUP-PVAL-115.0-1 | 9499 | FORT LUPTON SUBSTATION | XCEL | PLATTE VALLEY | XCEL | 70090 | 70307 | Xcel Owned | 9499-5 | SWITCH | PVAL | 1200 | 1549 | 1486 | 1780 | 239 | 309 | 296 | 355
FLUP-PVAL-115.0-1 | 9499 | FORT LUPTON SUBSTATION | XCEL | PLATTE VALLEY | XCEL | 70090 | 70307 | Xcel Owned | 9499-6 | SWITCH | PVAL | 1200 | 1549 | 1486 | 1780 | 239 | 309 | 296 | 355
FLUP-PVAL-115.0-1 | 9499 | FORT LUPTON SUBSTATION | XCEL | PLATTE VALLEY | XCEL | 70090 | 70307 | Xcel Owned | Cardinal | BUSBAR_SECTION | PVAL | 1209 | 1330 | 1377 | 1515 | 241 | 265 | 274 | 302
FLUP-PVAL-115.0-1 | 9499 | FORT LUPTON SUBSTATION | XCEL | PLATTE VALLEY | XCEL | 70090 | 70307 | Xcel Owned | Cardinal | BUSBAR_SECTION | FLUP | 1209 | 1330 | 1377 | 1515 | 241 | 265 | 274 | 302
FLUP-PVAL-115.0-1 | 9499 | FORT LUPTON SUBSTATION | XCEL | PLATTE VALLEY | XCEL | 70090 | 70307 | Xcel Owned | FLUP-PVAL-115.0-1 | Transmission Line | 9499 | 1210 | 1331 | 1378 | 1515 | 241 | 265 | 274 | 302
FLUP-VASQ-115.0-1 | 9494 | FORT LUPTON SUBSTATION | XCEL | VASQUEZ SUBSTATION | XCEL | 70191 | 70450 | Xcel Owned | FLUP-VASQ-115.0-1 | FACILITY |  | 801 | 881 | 911 | 1002 | 160 | 175 | 181 | 200
FLUP-VASQ-115.0-1 | 9494 | FORT LUPTON SUBSTATION | XCEL | VASQUEZ SUBSTATION | XCEL | 70191 | 70450 | Xcel Owned | FLUP-VASQ-115.0-1 | Transmission Line | 9494 | 801 | 881 | 911 | 1002 | 160 | 175 | 181 | 200
GREE-PRAI-230.0-1 | 5707 | GREENWOOD SUBSTATION | XCEL | PRAIRIE SUBSTATION | XCEL | 70189 | 70323 | Xcel Owned | GREE-PRAI-230.0-1 | FACILITY |  | 1445 | 1590 | 1600 | 1600 | 576 | 633 | 637 | 637
GREE-PRAI-230.0-1 | 5707 | GREENWOOD SUBSTATION | XCEL | PRAIRIE SUBSTATION | XCEL | 70189 | 70323 | Xcel Owned | GREE-PRAI-230.0-1 | Transmission Line | 5707 | 1445 | 1590 | 1648 | 1813 | 576 | 633 | 657 | 722
GREE-PRAI-230.0-1 | 5707 | GREENWOOD SUBSTATION | XCEL | PRAIRIE SUBSTATION | XCEL | 70189 | 70323 | Xcel Owned | 5707-2 | BREAKER | PRAI | 1600 | 1600 | 1600 | 1600 | 637 | 637 | 637 | 637
GRVL-SPRU-230.0-1 | 5270 | GREEN VALLEY SUBSTATION | XCEL | SPRUCE SUBSTATION | XCEL | 70048 | 70528 | Xcel Owned | GRVL-SPRU-230.0-1 | FACILITY |  | 1800 | 1800 | 1800 | 1800 | 717 | 717 | 717 | 717
GRVL-SPRU-230.0-1 | 5270 | GREEN VALLEY SUBSTATION | XCEL | SPRUCE SUBSTATION | XCEL | 70048 | 70528 | Xcel Owned | TL5270_XDCR_AMP | SECONDARY_CURRENT_LIMITATION | GRVL | 1800 | 1800 | 1800 | 1800 | 717 | 717 | 717 | 717
HARS-TARR-230.0-1 | 5995 | HARTSEL (IREA) | XCEL | TARRYALL SUBSTATION | XCEL | 70927 | 70427 | Xcel Owned | HARS-TARR-230.0-1 | FACILITY |  | 1175 | 1188 | 1255 | 1255 | 468 | 473 | 500 | 500
HARS-TARR-230.0-1 | 5995 | HARTSEL (IREA) | XCEL | TARRYALL SUBSTATION | XCEL | 70927 | 70427 | Xcel Owned | Narcissus | BUSBAR_SECTION | TARR | 1175 | 1380 | 1408 | 1575 | 468 | 550 | 561 | 628
HARS-TARR-230.0-1 | 5995 | HARTSEL (IREA) | XCEL | TARRYALL SUBSTATION | XCEL | 70927 | 70427 | Xcel Owned |  | LINE_TRAP | TARR | 1188 | 1188 | 1255 | 1255 | 473 | 473 | 500 | 500
JEWE-LEET-230.0-1 | 5285 | JEWELL SUBSTATION | XCEL | LEETSDALE SUBSTATION | XCEL | 70239 | 70260 | Xcel Owned | JEWE-LEET-230.0-1 | FACILITY |  | 1217 | 1393 | 1443 | 1587 | 485 | 555 | 575 | 632
JEWE-LEET-230.0-1 | 5285 | JEWELL SUBSTATION | XCEL | LEETSDALE SUBSTATION | XCEL | 70239 | 70260 | Xcel Owned | Narcissus | BUSBAR_SECTION | LEET | 1217 | 1424 | 1454 | 1622 | 485 | 567 | 579 | 646
JEWE-LEET-230.0-1 | 5285 | JEWELL SUBSTATION | XCEL | LEETSDALE SUBSTATION | XCEL | 70239 | 70260 | Xcel Owned | JEWE-LEET-230.0-1 | Transmission Line | 5285 | 1266 | 1393 | 1443 | 1587 | 504 | 555 | 575 | 632
KEST-SPRU-230.0-1 | 5185 | KESTREL SWITCHING STATION | XCEL | SPRUCE SUBSTATION | XCEL | 70536 | 70528 | Xcel Owned | KEST-SPRU-230.0-1 | FACILITY |  | 1894 | 2101 | 2173 | 2391 | 755 | 837 | 866 | 953
KEST-SPRU-230.0-1 | 5185 | KESTREL SWITCHING STATION | XCEL | SPRUCE SUBSTATION | XCEL | 70536 | 70528 | Xcel Owned | 2½" (AL 40) | BUSBAR_SECTION | SPRU | 1894 | 2252 | 2290 | 2581 | 755 | 897 | 912 | 1028
KEST-SPRU-230.0-1 | 5185 | KESTREL SWITCHING STATION | XCEL | SPRUCE SUBSTATION | XCEL | 70536 | 70528 | Xcel Owned | KEST-SPRU-230.0-1 | Transmission Line | 5185 | 1910 | 2101 | 2173 | 2391 | 761 | 837 | 866 | 953
MARC-WATE-230.0-1 | 5085 | MARCY SUBSTATION | XCEL | WATERTON SUBSTATION | XCEL | 70278 | 70959 | Xcel Owned | MARC-WATE-230.0-1 | FACILITY |  | 1261 | 1387 | 1437 | 1580 | 502 | 553 | 572 | 629
MARC-WATE-230.0-1 | 5085 | MARCY SUBSTATION | XCEL | WATERTON SUBSTATION | XCEL | 70278 | 70959 | Xcel Owned | MARC-WATE-230.0-1 | Transmission Line | 5085 | 1261 | 1387 | 1437 | 1580 | 502 | 553 | 572 | 629
RECY-FLUP-115.0-1 | 9053 | RECYCLING - COORS | XCEL | FORT LUPTON SUBSTATION | XCEL | 70127 | 70191 | Xcel Owned | RECY-FLUP-115.0-1 | FACILITY |  | 1200 | 1520 | 1483 | 1657 | 239 | 303 | 295 | 330
RECY-FLUP-115.0-1 | 9053 | RECYCLING - COORS | XCEL | FORT LUPTON SUBSTATION | XCEL | 70127 | 70191 | Xcel Owned | 9053-7 | SWITCH | RECY | 1200 | 1549 | 1486 | 1780 | 239 | 309 | 296 | 355
RECY-FLUP-115.0-1 | 9053 | RECYCLING - COORS | XCEL | FORT LUPTON SUBSTATION | XCEL | 70127 | 70191 | Xcel Owned | 9053M | SWITCH | FLUP | 1200 | 1549 | 1486 | 1780 | 239 | 309 | 296 | 355
RECY-FLUP-115.0-1 | 9053 | RECYCLING - COORS | XCEL | FORT LUPTON SUBSTATION | XCEL | 70127 | 70191 | Xcel Owned | 9053L | SWITCH | FLUP | 1294 | 1520 | 1483 | 1657 | 258 | 303 | 295 | 330

## Removed Line Facilities
|  |  | FAC-008-5 Transmission Lines | OPCO: PSC | VALIDATION STATUS: VALID | OWNERSHIP: Jointly Owned,Xcel Owned
|  |  |  | BES: Y | LIFE CYCLE STATUS: REMOVED
FACILITY DESIGNATION | LINE NAME | DATE OF REMOVAL | COMMENTS
CHER-THTN-115.0-1 | 9548 | 2025-08-21 | Metro Water Recovery substation added. Facility replaced by CHER-METO-115.0-1 LN-9548 and METO-THTN-115.0-1 LN-9737.
CHYW-SHOR-345.0-1 | 7199 | 2025-05-02 | Goose Creek substation added. Facility replaced by GOOS-SHOR-345.0-1 LN-7199 and CHYW-GOOS-345.0-1 LN-7261.
CLIM-SUMM-115.0-1 | 9188 | 2025-02-03 | Facility BES status changed to E1 Radial.
SANT_TP-SANT-230.0-1 | 5107 | 2025-02-03 | Sante Fe Tap removed. Facility replaced by ARAP-SANT-230.0-1 LN-5107.

## Transformer Ratings
|  | FAC-008-5 Transformer |  |  |  | OPCO: PSC |  |  |  |  | VALIDATION STATUS: VALID
[6 empty] | BES: Y |  |  |  |  | LIFE CYCLE STATUS: AS BUILT
FACILITY DESIGNATION | SUBSTATION | HIGH SIDE PSSE | LOWSIDE PSSE | EQUIPMENT NAME | EQUIPMENT TYPE | VOLTAGE (kV) | SN (MVA) | SE8 (MVA) | SE4 (MVA) | SE2 (MVA) | SE30 (MVA) | WN (MVA) | WE8 (MVA) | WE4 (MVA) | WE2 (MVA) | WE30 (MVA) | COMMENTS
ARAP-TR05-230.0-115.0-13.8-HX | ARAPAHOE SUBSTATION | 70038 | 70036 | ARAP-TR05-230.0-115.0-13.8-HX | FACILITY |  | 272 | 272 | 312 | 319 | 319 | 299 | 299 | 319 | 319 | 319
ARAP-TR05-230.0-115.0-13.8-HX | ARAPAHOE SUBSTATION | 70038 | 70036 | TR05 | TRANSFORMER | 115 | 271 | 271 | 312 | 319 | 319 | 299 | 299 | 319 | 319 | 319
ARAP-TR05-230.0-115.0-13.8-HX | ARAPAHOE SUBSTATION | 70038 | 70036 | TR05 | TRANSFORMER | 230 | 272 | 272 | 312 | 326 | 339 | 299 | 299 | 339 | 353 | 367
ARAP-TR05-230.0-115.0-13.8-HX | ARAPAHOE SUBSTATION | 70038 | 70036 | TR05_H-SA_MW | SECONDARY_CURRENT_LIMITATION | 230 | 319 | 319 | 319 | 319 | 319 | 319 | 319 | 319 | 319 | 319
ARAP-TR05-230.0-115.0-13.8-HX | ARAPAHOE SUBSTATION | 70038 | 70036 | TR05_H-SA_MVAR | SECONDARY_CURRENT_LIMITATION | 230 | 319 | 319 | 319 | 319 | 319 | 319 | 319 | 319 | 319 | 319
ARAP-TR05-230.0-115.0-13.8-HX | ARAPAHOE SUBSTATION | 70038 | 70036 | TR05_H-SA_AMPS | SECONDARY_CURRENT_LIMITATION | 230 | 319 | 319 | 319 | 319 | 319 | 319 | 319 | 319 | 319 | 319
ARAP-TR05-230.0-115.0-13.8-HX | ARAPAHOE SUBSTATION | 70038 | 70036 | BK05 BCT H-SA | CURRENT_TRANSFORMER | 230 | 319 | 319 | 319 | 319 | 319 | 319 | 319 | 319 | 319 | 319
BASA-TR01-230.0-115.0-13.8-HX | BASALT SUBSTATION | 79004 | 79003 | BASA-TR01-230.0-115.0-13.8-HX | FACILITY |  | 114 | 114 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
BASA-TR01-230.0-115.0-13.8-HX | BASALT SUBSTATION | 79004 | 79003 | TR01 | TRANSFORMER | 230 | 114 | 114 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
BASA-TR01-230.0-115.0-13.8-HX | BASALT SUBSTATION | 79004 | 79003 | TR01 | TRANSFORMER | 115 | 114 | 114 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
BASA-TR01-230.0-115.0-13.8-HX | BASALT SUBSTATION | 79004 | 79003 | BK01 X 14 15 16 | CURRENT_TRANSFORMER | 115 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
BASA-TR02-230.0-115.0-13.8-HX | BASALT SUBSTATION | 79004 | 79003 | BASA-TR02-230.0-115.0-13.8-HX | FACILITY |  | 168 | 168 | 190 | 190 | 190 | 185 | 185 | 190 | 190 | 190
BASA-TR02-230.0-115.0-13.8-HX | BASALT SUBSTATION | 79004 | 79003 | TR02 | TRANSFORMER | 115 | 168 | 168 | 193 | 202 | 210 | 185 | 185 | 210 | 218 | 227
BASA-TR02-230.0-115.0-13.8-HX | BASALT SUBSTATION | 79004 | 79003 | TR02 | TRANSFORMER | 230 | 168 | 168 | 193 | 202 | 210 | 185 | 185 | 210 | 218 | 227
BASA-TR02-230.0-115.0-13.8-HX | BASALT SUBSTATION | 79004 | 79003 |  | CABLE_TERMINATOR | 115 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190
BASA-TR02-230.0-115.0-13.8-HX | BASALT SUBSTATION | 79004 | 79003 | Jessamine | BUSBAR_SECTION | 115 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190
BEAV-TR01-230.0-115.0-13.8-HX | BEAVER CREEK EAST SUBSTATION | 70399 | 70397 | BEAV-TR01-230.0-115.0-13.8-HX | FACILITY |  | 209 | 209 | 239 | 239 | 239 | 239 | 239 | 239 | 239 | 239
BEAV-TR01-230.0-115.0-13.8-HX | BEAVER CREEK EAST SUBSTATION | 70399 | 70397 | Cardinal | BUSBAR_SECTION | 115 | 209 | 209 | 243 | 243 | 243 | 249 | 249 | 276 | 276 | 276
BEAV-TR01-230.0-115.0-13.8-HX | BEAVER CREEK EAST SUBSTATION | 70399 | 70397 | TR01 | TRANSFORMER | 115 | 221 | 254 | 265 | 276 | 298 | 243 | 276 | 287 | 298 | 319
BEAV-TR01-230.0-115.0-13.8-HX | BEAVER CREEK EAST SUBSTATION | 70399 | 70397 | TR01 | TRANSFORMER | 230 | 221 | 254 | 265 | 276 | 298 | 243 | 276 | 287 | 298 | 319
BEAV-TR01-230.0-115.0-13.8-HX | BEAVER CREEK EAST SUBSTATION | 70399 | 70397 | TR01 X 11 12 13 | CURRENT_TRANSFORMER | 115 | 239 | 239 | 239 | 239 | 239 | 239 | 239 | 239 | 239 | 239
BEAV-TR01-230.0-115.0-13.8-HX | BEAVER CREEK EAST SUBSTATION | 70399 | 70397 | DG-2 115KV | SECONDARY_CURRENT_LIMITATION | 115 | 239 | 239 | 239 | 239 | 239 | 239 | 239 | 239 | 239 | 239
BEAV-TR01-230.0-115.0-13.8-HX | BEAVER CREEK EAST SUBSTATION | 70399 | 70397 | TR01 AMP XDCR | SECONDARY_CURRENT_LIMITATION | 115 | 239 | 239 | 239 | 239 | 239 | 239 | 239 | 239 | 239 | 239
BEAV-TR01-230.0-115.0-13.8-HX | BEAVER CREEK EAST SUBSTATION | 70399 | 70397 | TR01 X 8 9 10 | CURRENT_TRANSFORMER | 115 | 239 | 239 | 239 | 239 | 239 | 239 | 239 | 239 | 239 | 239
BLUE-TR01-230.0-115.0-13.8-HX | BLUE RIVER SUBSTATION | 70053 | 70052 | BLUE-TR01-230.0-115.0-13.8-HX | FACILITY |  | 163 | 176 | 196 | 204 | 206 | 180 | 204 | 212 | 220 | 235
BLUE-TR01-230.0-115.0-13.8-HX | BLUE RIVER SUBSTATION | 70053 | 70052 | TR01 | TRANSFORMER | 230 | 163 | 188 | 196 | 204 | 220 | 180 | 204 | 212 | 220 | 245
BLUE-TR01-230.0-115.0-13.8-HX | BLUE RIVER SUBSTATION | 70053 | 70052 | TR01 | TRANSFORMER | 115 | 163 | 188 | 196 | 204 | 220 | 180 | 204 | 212 | 220 | 245
BLUE-TR01-230.0-115.0-13.8-HX | BLUE RIVER SUBSTATION | 70053 | 70052 | Arbutus | BUSBAR_SECTION | 115 | 176 | 176 | 206 | 206 | 206 | 210 | 210 | 235 | 235 | 235
BOON-TR01-230.0-115.0-13.8-HX | BOONE SUBSTATION | 70061 | 70060 | BOON-TR01-230.0-115.0-13.8-HX | FACILITY |  | 147 | 147 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159
BOON-TR01-230.0-115.0-13.8-HX | BOONE SUBSTATION | 70061 | 70060 | TR01 | TRANSFORMER | 115 | 147 | 147 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159
BOON-TR01-230.0-115.0-13.8-HX | BOONE SUBSTATION | 70061 | 70060 | TR01 | TRANSFORMER | 230 | 147 | 147 | 169 | 184 | 191 | 176 | 176 | 191 | 206 | 214
BRIC-TR01-230.0-115.0-15.0-HX | BRICK CENTER | 70545 | 70546 | BRIC-TR01-230.0-115.0-15.0-HX | FACILITY |  | 226 | 239 | 239 | 239 | 239 | 239 | 239 | 239 | 239 | 239
BRIC-TR01-230.0-115.0-15.0-HX | BRICK CENTER | 70545 | 70546 | TR01 | TRANSFORMER | 115 | 226 | 260 | 271 | 282 | 305 | 249 | 282 | 294 | 305 | 339
BRIC-TR01-230.0-115.0-15.0-HX | BRICK CENTER | 70545 | 70546 | TR01 | TRANSFORMER | 230 | 226 | 260 | 271 | 283 | 305 | 249 | 283 | 294 | 305 | 339
BRIC-TR01-230.0-115.0-15.0-HX | BRICK CENTER | 70545 | 70546 | 9971 MU B | CURRENT_TRANSFORMER | 115 | 239 | 239 | 239 | 239 | 239 | 239 | 239 | 239 | 239 | 239
BRIC-TR01-230.0-115.0-15.0-HX | BRICK CENTER | 70545 | 70546 | 9971 MU A | CURRENT_TRANSFORMER | 115 | 239 | 239 | 239 | 239 | 239 | 239 | 239 | 239 | 239 | 239
BRIC-TR01-230.0-115.0-15.0-HX | BRICK CENTER | 70545 | 70546 | 9971 | BREAKER | 115 | 239 | 239 | 239 | 239 | 239 | 239 | 239 | 239 | 239 | 239
BRIC-TR01-230.0-115.0-15.0-HX | BRICK CENTER | 70545 | 70546 | 9971 MU C | CURRENT_TRANSFORMER | 115 | 239 | 239 | 239 | 239 | 239 | 239 | 239 | 239 | 239 | 239
CABI-TR01-230.0-115.0-11.5-HX | CABIN CREEK HYDRO SUBSTATION | 70072 | 70071 | CABI-TR01-230.0-115.0-11.5-HX | FACILITY |  | 54 | 54 | 62 | 65 | 68 | 60 | 60 | 68 | 71 | 73
CABI-TR01-230.0-115.0-11.5-HX | CABIN CREEK HYDRO SUBSTATION | 70072 | 70071 | TR01 | TRANSFORMER | 115 | 54 | 54 | 62 | 65 | 68 | 60 | 60 | 68 | 71 | 73
CABI-TR01-230.0-115.0-11.5-HX | CABIN CREEK HYDRO SUBSTATION | 70072 | 70071 | TR01 | TRANSFORMER | 230 | 54 | 54 | 62 | 65 | 68 | 60 | 60 | 68 | 71 | 73
CABI-TR02-230.0-115.0-11.5-HX | CABIN CREEK HYDRO SUBSTATION | 70072 | 70071 | CABI-TR02-230.0-115.0-11.5-HX | FACILITY |  | 60 | 60 | 69 | 72 | 75 | 66 | 66 | 75 | 78 | 81
CABI-TR02-230.0-115.0-11.5-HX | CABIN CREEK HYDRO SUBSTATION | 70072 | 70071 | TR02 | TRANSFORMER | 230 | 60 | 60 | 69 | 72 | 75 | 66 | 66 | 75 | 78 | 81
CABI-TR02-230.0-115.0-11.5-HX | CABIN CREEK HYDRO SUBSTATION | 70072 | 70071 | TR02 | TRANSFORMER | 115 | 60 | 60 | 69 | 72 | 75 | 66 | 66 | 75 | 78 | 81
CHAM-TR01-230.0-115.0-13.8-HX | CHAMBERS SUBSTATION | 70539 | 70538 | CHAM-TR01-230.0-115.0-13.8-HX | FACILITY |  | 280 | 319 | 319 | 319 | 319 | 308 | 319 | 319 | 319 | 319
CHAM-TR01-230.0-115.0-13.8-HX | CHAMBERS SUBSTATION | 70539 | 70538 | TR01 | TRANSFORMER | 115 | 280 | 322 | 336 | 350 | 378 | 308 | 350 | 364 | 378 | 420
CHAM-TR01-230.0-115.0-13.8-HX | CHAMBERS SUBSTATION | 70539 | 70538 | TR01 | TRANSFORMER | 230 | 280 | 322 | 336 | 350 | 378 | 308 | 350 | 364 | 378 | 420
CHAM-TR01-230.0-115.0-13.8-HX | CHAMBERS SUBSTATION | 70539 | 70538 | 9544_246X_PK-2-1 | SECONDARY_CURRENT_LIMITATION | 115 | 319 | 319 | 319 | 319 | 319 | 319 | 319 | 319 | 319 | 319
CHAM-TR01-230.0-115.0-13.8-HX | CHAMBERS SUBSTATION | 70539 | 70538 | 9544 246X | CURRENT_TRANSFORMER | 115 | 319 | 319 | 319 | 319 | 319 | 319 | 319 | 319 | 319 | 319
CHAM-TR01-230.0-115.0-13.8-HX | CHAMBERS SUBSTATION | 70539 | 70538 | 9543_246X_PK-2-1 | SECONDARY_CURRENT_LIMITATION | 115 | 319 | 319 | 319 | 319 | 319 | 319 | 319 | 319 | 319 | 319
CHAM-TR01-230.0-115.0-13.8-HX | CHAMBERS SUBSTATION | 70539 | 70538 | 9543 246Y | CURRENT_TRANSFORMER | 115 | 319 | 319 | 319 | 319 | 319 | 319 | 319 | 319 | 319 | 319
CHAM-TR01-230.0-115.0-13.8-HX | CHAMBERS SUBSTATION | 70539 | 70538 | 9544_246Y_PK-2-2 | SECONDARY_CURRENT_LIMITATION | 115 | 319 | 319 | 319 | 319 | 319 | 319 | 319 | 319 | 319 | 319
CHAM-TR01-230.0-115.0-13.8-HX | CHAMBERS SUBSTATION | 70539 | 70538 | 9543 246X | CURRENT_TRANSFORMER | 115 | 319 | 319 | 319 | 319 | 319 | 319 | 319 | 319 | 319 | 319
CHAM-TR01-230.0-115.0-13.8-HX | CHAMBERS SUBSTATION | 70539 | 70538 | 9543_246Y_PK-2-2 | SECONDARY_CURRENT_LIMITATION | 115 | 319 | 319 | 319 | 319 | 319 | 319 | 319 | 319 | 319 | 319
CHAM-TR01-230.0-115.0-13.8-HX | CHAMBERS SUBSTATION | 70539 | 70538 | 9544 246Y | CURRENT_TRANSFORMER | 115 | 319 | 319 | 319 | 319 | 319 | 319 | 319 | 319 | 319 | 319
CHAM-TR02-230.0-115.0-13.8-HX | CHAMBERS SUBSTATION | 70539 | 70538 | CHAM-TR02-230.0-115.0-13.8-HX | FACILITY |  | 280 | 319 | 319 | 319 | 319 | 308 | 319 | 319 | 319 | 319
CHAM-TR02-230.0-115.0-13.8-HX | CHAMBERS SUBSTATION | 70539 | 70538 | TR02 | TRANSFORMER | 230 | 280 | 322 | 336 | 350 | 378 | 308 | 350 | 364 | 378 | 420
CHAM-TR02-230.0-115.0-13.8-HX | CHAMBERS SUBSTATION | 70539 | 70538 | TR02 | TRANSFORMER | 115 | 280 | 322 | 336 | 350 | 378 | 308 | 350 | 364 | 378 | 420
CHAM-TR02-230.0-115.0-13.8-HX | CHAMBERS SUBSTATION | 70539 | 70538 | 9175 135Y | CURRENT_TRANSFORMER | 115 | 319 | 319 | 319 | 319 | 319 | 319 | 319 | 319 | 319 | 319
CHAM-TR02-230.0-115.0-13.8-HX | CHAMBERS SUBSTATION | 70539 | 70538 | 9178_135X_PK-2-4 | SECONDARY_CURRENT_LIMITATION | 115 | 319 | 319 | 319 | 319 | 319 | 319 | 319 | 319 | 319 | 319
CHAM-TR02-230.0-115.0-13.8-HX | CHAMBERS SUBSTATION | 70539 | 70538 | 9178_135Y_PK-2-3 | SECONDARY_CURRENT_LIMITATION | 115 | 319 | 319 | 319 | 319 | 319 | 319 | 319 | 319 | 319 | 319
CHAM-TR02-230.0-115.0-13.8-HX | CHAMBERS SUBSTATION | 70539 | 70538 | 9175_135X_PK-2-4 | SECONDARY_CURRENT_LIMITATION | 115 | 319 | 319 | 319 | 319 | 319 | 319 | 319 | 319 | 319 | 319
CHAM-TR02-230.0-115.0-13.8-HX | CHAMBERS SUBSTATION | 70539 | 70538 | 9178 135X | CURRENT_TRANSFORMER | 115 | 319 | 319 | 319 | 319 | 319 | 319 | 319 | 319 | 319 | 319
CHAM-TR02-230.0-115.0-13.8-HX | CHAMBERS SUBSTATION | 70539 | 70538 | 9178 135Y | CURRENT_TRANSFORMER | 115 | 319 | 319 | 319 | 319 | 319 | 319 | 319 | 319 | 319 | 319
CHAM-TR02-230.0-115.0-13.8-HX | CHAMBERS SUBSTATION | 70539 | 70538 | 9175 135X | CURRENT_TRANSFORMER | 115 | 319 | 319 | 319 | 319 | 319 | 319 | 319 | 319 | 319 | 319
CHAM-TR02-230.0-115.0-13.8-HX | CHAMBERS SUBSTATION | 70539 | 70538 | 9175_135Y_PK-2-3 | SECONDARY_CURRENT_LIMITATION | 115 | 319 | 319 | 319 | 319 | 319 | 319 | 319 | 319 | 319 | 319
CHER-TR01-230.0-115.0-13.8-HX | CHEROKEE SWITCHYARD SUBSTATION | 70107 | 70108 | CHER-TR01-230.0-115.0-13.8-HX | FACILITY |  | 280 | 280 | 317 | 317 | 317 | 308 | 308 | 350 | 361 | 361
CHER-TR01-230.0-115.0-13.8-HX | CHEROKEE SWITCHYARD SUBSTATION | 70107 | 70108 | TR01 | TRANSFORMER | 230 | 280 | 280 | 322 | 336 | 350 | 308 | 308 | 350 | 364 | 378
CHER-TR01-230.0-115.0-13.8-HX | CHEROKEE SWITCHYARD SUBSTATION | 70107 | 70108 | TR01 | TRANSFORMER | 115 | 280 | 280 | 322 | 336 | 350 | 308 | 308 | 350 | 364 | 378
CHER-TR01-230.0-115.0-13.8-HX | CHEROKEE SWITCHYARD SUBSTATION | 70107 | 70108 | Bittern | BUSBAR_SECTION | 115 | 288 | 288 | 317 | 317 | 317 | 328 | 328 | 361 | 361 | 361
CHER-TR02-230.0-115.0-13.8-HX | CHEROKEE SWITCHYARD SUBSTATION | 70107 | 70108 | CHER-TR02-230.0-115.0-13.8-HX | FACILITY |  | 280 | 280 | 322 | 336 | 350 | 308 | 308 | 350 | 364 | 378
CHER-TR02-230.0-115.0-13.8-HX | CHEROKEE SWITCHYARD SUBSTATION | 70107 | 70108 | TR02 | TRANSFORMER | 230 | 280 | 280 | 322 | 336 | 350 | 308 | 308 | 350 | 364 | 378
CHER-TR02-230.0-115.0-13.8-HX | CHEROKEE SWITCHYARD SUBSTATION | 70107 | 70108 | TR02 | TRANSFORMER | 115 | 280 | 280 | 322 | 336 | 350 | 308 | 308 | 350 | 364 | 378
COMA-TR01-230.0-115.0-13.8-HX | COMANCHE SUBSTATION | 70122 | 70121 | COMA-TR01-230.0-115.0-13.8-HX | FACILITY |  | 280 | 319 | 319 | 319 | 319 | 308 | 319 | 319 | 319 | 319
COMA-TR01-230.0-115.0-13.8-HX | COMANCHE SUBSTATION | 70122 | 70121 | TR01 | TRANSFORMER | 230 | 280 | 322 | 336 | 350 | 378 | 308 | 350 | 364 | 378 | 420
COMA-TR01-230.0-115.0-13.8-HX | COMANCHE SUBSTATION | 70122 | 70121 | TR01 | TRANSFORMER | 115 | 280 | 322 | 336 | 350 | 378 | 308 | 350 | 364 | 378 | 420
COMA-TR01-230.0-115.0-13.8-HX | COMANCHE SUBSTATION | 70122 | 70121 | 5405XDCRAMP | SECONDARY_CURRENT_LIMITATION | 230 | 319 | 319 | 319 | 319 | 319 | 319 | 319 | 319 | 319 | 319
COMA-TR01-230.0-115.0-13.8-HX | COMANCHE SUBSTATION | 70122 | 70121 | 5405W/VAR | SECONDARY_CURRENT_LIMITATION | 230 | 319 | 319 | 319 | 319 | 319 | 319 | 319 | 319 | 319 | 319
COMA-TR02-230.0-115.0-13.8-HX | COMANCHE SUBSTATION | 70122 | 70121 | COMA-TR02-230.0-115.0-13.8-HX | FACILITY |  | 280 | 322 | 336 | 350 | 378 | 308 | 350 | 364 | 378 | 420
COMA-TR02-230.0-115.0-13.8-HX | COMANCHE SUBSTATION | 70122 | 70121 | TR02 | TRANSFORMER | 115 | 280 | 322 | 336 | 350 | 378 | 308 | 350 | 364 | 378 | 420
COMA-TR02-230.0-115.0-13.8-HX | COMANCHE SUBSTATION | 70122 | 70121 | TR02 | TRANSFORMER | 230 | 280 | 322 | 336 | 350 | 378 | 308 | 350 | 364 | 378 | 420
COMA-TR03-345.0-230.0-13.8-HX | COMANCHE SUBSTATION | 70654 | 70122 | COMA-TR03-345.0-230.0-13.8-HX | FACILITY |  | 560 | 644 | 672 | 700 | 756 | 616 | 700 | 728 | 756 | 840
COMA-TR03-345.0-230.0-13.8-HX | COMANCHE SUBSTATION | 70654 | 70122 | TR03 | TRANSFORMER | 345 | 560 | 644 | 672 | 700 | 756 | 616 | 700 | 728 | 756 | 840
COMA-TR03-345.0-230.0-13.8-HX | COMANCHE SUBSTATION | 70654 | 70122 | TR03 | TRANSFORMER | 230 | 560 | 644 | 672 | 700 | 756 | 616 | 700 | 728 | 756 | 840
COMA-TR04-345.0-230.0-13.8-HX | COMANCHE SUBSTATION | 70654 | 70122 | COMA-TR04-345.0-230.0-13.8-HX | FACILITY |  | 560 | 644 | 672 | 700 | 756 | 616 | 700 | 728 | 756 | 765
COMA-TR04-345.0-230.0-13.8-HX | COMANCHE SUBSTATION | 70654 | 70122 | TR04 | TRANSFORMER | 345 | 560 | 644 | 672 | 700 | 756 | 616 | 700 | 728 | 756 | 840
COMA-TR04-345.0-230.0-13.8-HX | COMANCHE SUBSTATION | 70654 | 70122 | TR04 | TRANSFORMER | 230 | 560 | 644 | 672 | 700 | 756 | 616 | 700 | 728 | 756 | 840
COMA-TR04-345.0-230.0-13.8-HX | COMANCHE SUBSTATION | 70654 | 70122 | 5402 PKG-BF | SECONDARY_CURRENT_LIMITATION | 230 | 765 | 765 | 765 | 765 | 765 | 765 | 765 | 765 | 765 | 765
CRAI-TR02-345.0-230.0-13.8-HX | CRAIG SW YARD | -1 | 70009 | CRAI-TR02-345.0-230.0-13.8-HX | FACILITY |  | 535 | 610 | 615 | 637 | 637 | 589 | 637 | 637 | 637 | 637
CRAI-TR02-345.0-230.0-13.8-HX | CRAIG SW YARD | -1 | 70009 | TR02 | TRANSFORMER | 345 | 535 | 610 | 615 | 637 | 637 | 589 | 637 | 637 | 637 | 637
CRAI-TR02-345.0-230.0-13.8-HX | CRAIG SW YARD | -1 | 70009 | TR02 | TRANSFORMER | 230 | 535 | 610 | 615 | 637 | 637 | 589 | 637 | 637 | 637 | 637
CRAI-TR02-345.0-230.0-13.8-HX | CRAIG SW YARD | -1 | 70009 | TR2_X_C2 | CURRENT_TRANSFORMER | 230 | 637 | 637 | 637 | 637 | 637 | 637 | 637 | 637 | 637 | 637
DANI-TR01-230.0-115.0-13.8-HX | DANIELS PARK 115 & 230KV SUBSTATION | 70139 | 70138 | DANI-TR01-230.0-115.0-13.8-HX | FACILITY |  | 280 | 322 | 336 | 350 | 378 | 308 | 350 | 364 | 378 | 420
DANI-TR01-230.0-115.0-13.8-HX | DANIELS PARK 115 & 230KV SUBSTATION | 70139 | 70138 | TR01 | TRANSFORMER | 230 | 280 | 322 | 336 | 350 | 378 | 308 | 350 | 364 | 378 | 420
DANI-TR01-230.0-115.0-13.8-HX | DANIELS PARK 115 & 230KV SUBSTATION | 70139 | 70138 | TR01 | TRANSFORMER | 115 | 280 | 322 | 336 | 350 | 378 | 308 | 350 | 364 | 378 | 420
DANI-TR03-345.0-230.0-13.8-HX | DANIELS PARK 115 & 230KV SUBSTATION | 70601 | 70139 | DANI-TR03-345.0-230.0-13.8-HX | FACILITY |  | 560 | 644 | 672 | 700 | 756 | 616 | 700 | 728 | 756 | 797
DANI-TR03-345.0-230.0-13.8-HX | DANIELS PARK 115 & 230KV SUBSTATION | 70601 | 70139 | TR03 | TRANSFORMER | 230 | 560 | 644 | 672 | 700 | 756 | 616 | 700 | 728 | 756 | 840
DANI-TR03-345.0-230.0-13.8-HX | DANIELS PARK 115 & 230KV SUBSTATION | 70601 | 70139 | TR03 | TRANSFORMER | 345 | 560 | 644 | 672 | 700 | 756 | 616 | 700 | 728 | 756 | 840
DANI-TR03-345.0-230.0-13.8-HX | DANIELS PARK 115 & 230KV SUBSTATION | 70601 | 70139 | 5103 | BREAKER | 230 | 797 | 797 | 797 | 797 | 797 | 797 | 797 | 797 | 797 | 797
DANI-TR04-345.0-230.0-13.8-HX | DANIELS PARK 115 & 230KV SUBSTATION | 70601 | 70139 | DANI-TR04-345.0-230.0-13.8-HX | FACILITY |  | 560 | 644 | 672 | 700 | 754 | 616 | 685 | 728 | 754 | 754
DANI-TR04-345.0-230.0-13.8-HX | DANIELS PARK 115 & 230KV SUBSTATION | 70601 | 70139 | TR04 | TRANSFORMER | 345 | 560 | 644 | 672 | 700 | 756 | 616 | 700 | 728 | 756 | 840
DANI-TR04-345.0-230.0-13.8-HX | DANIELS PARK 115 & 230KV SUBSTATION | 70601 | 70139 | TR04 | TRANSFORMER | 230 | 560 | 644 | 672 | 700 | 756 | 616 | 700 | 728 | 756 | 840
DANI-TR04-345.0-230.0-13.8-HX | DANIELS PARK 115 & 230KV SUBSTATION | 70601 | 70139 |  | CABLE_TERMINATOR | 230 | 685 | 685 | 754 | 754 | 754 | 685 | 685 | 754 | 754 | 754
DANI-TR04-345.0-230.0-13.8-HX | DANIELS PARK 115 & 230KV SUBSTATION | 70601 | 70139 |  | INSULATED_CABLE | 230 | 685 | 685 | 754 | 754 | 754 | 685 | 685 | 754 | 754 | 754
DANI-TR05-345.0-230.0-13.8-HX | DANIELS PARK 115 & 230KV SUBSTATION | 70601 | 70139 | DANI-TR05-345.0-230.0-13.8-HX | FACILITY |  | 560 | 644 | 672 | 700 | 754 | 616 | 685 | 728 | 754 | 754
DANI-TR05-345.0-230.0-13.8-HX | DANIELS PARK 115 & 230KV SUBSTATION | 70601 | 70139 | TR05 | TRANSFORMER | 345 | 560 | 644 | 672 | 700 | 756 | 616 | 700 | 728 | 756 | 840
DANI-TR05-345.0-230.0-13.8-HX | DANIELS PARK 115 & 230KV SUBSTATION | 70601 | 70139 | TR05 | TRANSFORMER | 230 | 560 | 644 | 672 | 700 | 756 | 616 | 700 | 728 | 756 | 840
DANI-TR05-345.0-230.0-13.8-HX | DANIELS PARK 115 & 230KV SUBSTATION | 70601 | 70139 |  | INSULATED_CABLE | 230 | 685 | 685 | 754 | 754 | 754 | 685 | 685 | 754 | 754 | 754
DANI-TR05-345.0-230.0-13.8-HX | DANIELS PARK 115 & 230KV SUBSTATION | 70601 | 70139 |  | CABLE_TERMINATOR | 230 | 685 | 685 | 754 | 754 | 754 | 685 | 685 | 754 | 754 | 754
DILL-TR02-230.0-115.0-13.2-HX | DILLON SUBSTATION | 70156 | 70155 | DILL-TR02-230.0-115.0-13.2-HX | FACILITY |  | 91 | 91 | 104 | 113 | 118 | 109 | 109 | 118 | 120 | 120
DILL-TR02-230.0-115.0-13.2-HX | DILLON SUBSTATION | 70156 | 70155 | TR02 | TRANSFORMER | 115 | 91 | 91 | 104 | 113 | 118 | 109 | 109 | 118 | 127 | 131
DILL-TR02-230.0-115.0-13.2-HX | DILLON SUBSTATION | 70156 | 70155 | TR02 | TRANSFORMER | 230 | 91 | 91 | 104 | 114 | 118 | 109 | 109 | 118 | 127 | 131
DILL-TR02-230.0-115.0-13.2-HX | DILLON SUBSTATION | 70156 | 70155 | 8182 135X | CURRENT_TRANSFORMER | 115 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
DILL-TR02-230.0-115.0-13.2-HX | DILLON SUBSTATION | 70156 | 70155 | 8182_246X_50BF | SECONDARY_CURRENT_LIMITATION | 115 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
DILL-TR02-230.0-115.0-13.2-HX | DILLON SUBSTATION | 70156 | 70155 | 8182_246X_50/69TL | SECONDARY_CURRENT_LIMITATION | 115 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
DILL-TR02-230.0-115.0-13.2-HX | DILLON SUBSTATION | 70156 | 70155 | 8182 246X | CURRENT_TRANSFORMER | 115 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
DTER-TR02-230.0-115.0-13.8-HX | DENVER TERMINAL SUBSTATION | 70149 | 70148 | DTER-TR02-230.0-115.0-13.8-HX | FACILITY |  | 272 | 272 | 313 | 326 | 340 | 299 | 299 | 340 | 353 | 367
DTER-TR02-230.0-115.0-13.8-HX | DENVER TERMINAL SUBSTATION | 70149 | 70148 | TR02 | TRANSFORMER | 115 | 272 | 272 | 313 | 326 | 340 | 299 | 299 | 340 | 353 | 367
DTER-TR02-230.0-115.0-13.8-HX | DENVER TERMINAL SUBSTATION | 70149 | 70148 | TR02 | TRANSFORMER | 230 | 272 | 272 | 313 | 326 | 340 | 299 | 299 | 340 | 353 | 367
FLUP-TR03-230.0-115.0-13.8-HX | FORT LUPTON SUBSTATION | 70192 | 70191 | FLUP-TR03-230.0-115.0-13.8-HX | FACILITY |  | 273 | 273 | 314 | 319 | 319 | 300 | 300 | 319 | 319 | 319
FLUP-TR03-230.0-115.0-13.8-HX | FORT LUPTON SUBSTATION | 70192 | 70191 | TR03 | TRANSFORMER | 115 | 273 | 273 | 314 | 319 | 319 | 300 | 300 | 319 | 319 | 319
FLUP-TR03-230.0-115.0-13.8-HX | FORT LUPTON SUBSTATION | 70192 | 70191 | TR03 | TRANSFORMER | 230 | 273 | 273 | 314 | 327 | 341 | 300 | 300 | 341 | 355 | 368
FLUP-TR03-230.0-115.0-13.8-HX | FORT LUPTON SUBSTATION | 70192 | 70191 | TR03 X 14 15 16 | CURRENT_TRANSFORMER | 115 | 319 | 319 | 319 | 319 | 319 | 319 | 319 | 319 | 319 | 319
HMIL-TR01-345.0-230.0-13.8-HX | HARVEST MILE | 70597 | 70596 | HMIL-TR01-345.0-230.0-13.8-HX | FACILITY |  | 560 | 644 | 672 | 700 | 756 | 616 | 700 | 728 | 756 | 840
HMIL-TR01-345.0-230.0-13.8-HX | HARVEST MILE | 70597 | 70596 | TR01 | TRANSFORMER | 230 | 560 | 644 | 672 | 700 | 756 | 616 | 700 | 728 | 756 | 840
HMIL-TR01-345.0-230.0-13.8-HX | HARVEST MILE | 70597 | 70596 | TR01 | TRANSFORMER | 345 | 560 | 644 | 672 | 700 | 756 | 616 | 700 | 728 | 756 | 840
HOPK-TR02-230.0-115.0-13.8-HX | HOPKINS SUBSTATION | 70232 | 70231 | HOPK-TR02-230.0-115.0-13.8-HX | FACILITY |  | 99 | 114 | 118 | 123 | 133 | 109 | 123 | 128 | 133 | 148
HOPK-TR02-230.0-115.0-13.8-HX | HOPKINS SUBSTATION | 70232 | 70231 | TR02 | TRANSFORMER | 115 | 99 | 114 | 118 | 123 | 133 | 109 | 123 | 128 | 133 | 148
HOPK-TR02-230.0-115.0-13.8-HX | HOPKINS SUBSTATION | 70232 | 70231 | TR02 | TRANSFORMER | 230 | 99 | 114 | 118 | 123 | 133 | 109 | 123 | 128 | 133 | 148
HOPK-TR03-230.0-115.0-13.8-HX | HOPKINS SUBSTATION | 70232 | 70231 | HOPK-TR03-230.0-115.0-13.8-HX | FACILITY |  | 94 | 94 | 108 | 117 | 120 | 112 | 112 | 120 | 120 | 120
HOPK-TR03-230.0-115.0-13.8-HX | HOPKINS SUBSTATION | 70232 | 70231 | TR03 | TRANSFORMER | 230 | 94 | 94 | 108 | 117 | 120 | 112 | 112 | 120 | 120 | 120
HOPK-TR03-230.0-115.0-13.8-HX | HOPKINS SUBSTATION | 70232 | 70231 | TR03 | TRANSFORMER | 115 | 94 | 94 | 108 | 117 | 120 | 113 | 113 | 120 | 120 | 120
HOPK-TR03-230.0-115.0-13.8-HX | HOPKINS SUBSTATION | 70232 | 70231 | 9713 135X | CURRENT_TRANSFORMER | 115 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
HSKY-TR04-230.0-115.0-13.8-HX | HUSKY SUBSTATION | 70898 | 70901 | HSKY-TR04-230.0-115.0-13.8-HX | FACILITY |  | 280 | 322 | 336 | 350 | 378 | 308 | 350 | 364 | 378 | 420
HSKY-TR04-230.0-115.0-13.8-HX | HUSKY SUBSTATION | 70898 | 70901 | TR04 | TRANSFORMER | 230 | 280 | 322 | 336 | 350 | 378 | 308 | 350 | 364 | 378 | 420
HSKY-TR04-230.0-115.0-13.8-HX | HUSKY SUBSTATION | 70898 | 70901 | TR04 | TRANSFORMER | 115 | 280 | 322 | 336 | 350 | 378 | 308 | 350 | 364 | 378 | 420
LEET-TR04-230.0-115.0-13.8-HX | LEETSDALE SUBSTATION | 70260 | 70259 | LEET-TR04-230.0-115.0-13.8-HX | FACILITY |  | 271 | 271 | 312 | 325 | 339 | 298 | 298 | 339 | 352 | 366
LEET-TR04-230.0-115.0-13.8-HX | LEETSDALE SUBSTATION | 70260 | 70259 | TR04 | TRANSFORMER | 115 | 271 | 271 | 312 | 325 | 339 | 298 | 298 | 339 | 352 | 366
LEET-TR04-230.0-115.0-13.8-HX | LEETSDALE SUBSTATION | 70260 | 70259 | TR04 | TRANSFORMER | 230 | 271 | 271 | 312 | 325 | 339 | 298 | 298 | 339 | 352 | 366
LEET-TR05-230.0-115.0-13.8-HX | LEETSDALE SUBSTATION | 70260 | 70259 | LEET-TR05-230.0-115.0-13.8-HX | FACILITY |  | 280 | 322 | 336 | 350 | 378 | 308 | 350 | 364 | 378 | 420
LEET-TR05-230.0-115.0-13.8-HX | LEETSDALE SUBSTATION | 70260 | 70259 | TR05 | TRANSFORMER | 230 | 280 | 322 | 336 | 350 | 378 | 308 | 350 | 364 | 378 | 420
LEET-TR05-230.0-115.0-13.8-HX | LEETSDALE SUBSTATION | 70260 | 70259 | TR05 | TRANSFORMER | 115 | 280 | 322 | 336 | 350 | 378 | 308 | 350 | 364 | 378 | 420
LOOK-TR01-230.0-115.0-13.8-HX | LOOKOUT SUBSTATION | 70266 | 70265 | LOOK-TR01-230.0-115.0-13.8-HX | FACILITY |  | 144 | 144 | 166 | 180 | 187 | 173 | 173 | 187 | 191 | 191
LOOK-TR01-230.0-115.0-13.8-HX | LOOKOUT SUBSTATION | 70266 | 70265 | TR01 | TRANSFORMER | 230 | 144 | 144 | 166 | 180 | 187 | 173 | 173 | 187 | 202 | 209
LOOK-TR01-230.0-115.0-13.8-HX | LOOKOUT SUBSTATION | 70266 | 70265 | TR01 | TRANSFORMER | 115 | 144 | 144 | 166 | 180 | 187 | 173 | 173 | 187 | 202 | 209
LOOK-TR01-230.0-115.0-13.8-HX | LOOKOUT SUBSTATION | 70266 | 70265 | 1_21Z3-TL | SECONDARY_CURRENT_LIMITATION | 115 | 191 | 191 | 191 | 191 | 191 | 191 | 191 | 191 | 191 | 191
LOOK-TR02-230.0-115.0-13.8-HX | LOOKOUT SUBSTATION | 70266 | 70265 | LOOK-TR02-230.0-115.0-13.8-HX | FACILITY |  | 150 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159
LOOK-TR02-230.0-115.0-13.8-HX | LOOKOUT SUBSTATION | 70266 | 70265 | TR02 | TRANSFORMER | 230 | 150 | 172 | 180 | 188 | 203 | 165 | 188 | 195 | 203 | 225
LOOK-TR02-230.0-115.0-13.8-HX | LOOKOUT SUBSTATION | 70266 | 70265 | TR02 | TRANSFORMER | 115 | 150 | 173 | 180 | 187 | 203 | 165 | 187 | 195 | 203 | 225
LOOK-TR02-230.0-115.0-13.8-HX | LOOKOUT SUBSTATION | 70266 | 70265 | 9792 135X | CURRENT_TRANSFORMER | 115 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159
MALT-TR01-230.0-115.0-13.8-HX | MALTA SUBSTATION | 70274 | 70273 | MALT-TR01-230.0-115.0-13.8-HX | FACILITY |  | 98 | 98 | 112 | 122 | 127 | 117 | 117 | 127 | 137 | 142
MALT-TR01-230.0-115.0-13.8-HX | MALTA SUBSTATION | 70274 | 70273 | TR01 | TRANSFORMER | 230 | 98 | 98 | 112 | 122 | 127 | 118 | 118 | 127 | 137 | 142
MALT-TR01-230.0-115.0-13.8-HX | MALTA SUBSTATION | 70274 | 70273 | TR01 | TRANSFORMER | 115 | 98 | 98 | 113 | 122 | 127 | 117 | 117 | 127 | 137 | 142
MALT-TR02-230.0-115.0-13.8-HX | MALTA SUBSTATION | 70274 | 70273 | MALT-TR02-230.0-115.0-13.8-HX | FACILITY |  | 100 | 115 | 120 | 125 | 135 | 110 | 125 | 130 | 135 | 150
MALT-TR02-230.0-115.0-13.8-HX | MALTA SUBSTATION | 70274 | 70273 | TR02 | TRANSFORMER | 115 | 100 | 115 | 120 | 125 | 135 | 110 | 125 | 130 | 135 | 150
MALT-TR02-230.0-115.0-13.8-HX | MALTA SUBSTATION | 70274 | 70273 | TR02 | TRANSFORMER | 230 | 100 | 115 | 120 | 125 | 135 | 110 | 125 | 130 | 135 | 150
MIDW-TR01-230.0-115.0-13.8-HX | MIDWAY SUBSTATION | 70286 | 70285 | MIDW-TR01-230.0-115.0-13.8-HX | FACILITY |  | 172 | 172 | 200 | 200 | 200 | 204 | 204 | 227 | 227 | 227
MIDW-TR01-230.0-115.0-13.8-HX | MIDWAY SUBSTATION | 70286 | 70285 | 500 - 37 | BUSBAR_SECTION | 115 | 172 | 172 | 200 | 200 | 200 | 204 | 204 | 227 | 227 | 227
MIDW-TR01-230.0-115.0-13.8-HX | MIDWAY SUBSTATION | 70286 | 70285 | TR01 | TRANSFORMER | 115 | 280 | 322 | 336 | 350 | 378 | 308 | 350 | 364 | 378 | 420
MIDW-TR01-230.0-115.0-13.8-HX | MIDWAY SUBSTATION | 70286 | 70285 | TR01 | TRANSFORMER | 230 | 280 | 322 | 336 | 350 | 378 | 308 | 350 | 364 | 378 | 420
MIDW-TR03-345.0-230.0-13.8-HX | MIDWAY SUBSTATION | 70465 | 70286 | MIDW-TR03-345.0-230.0-13.8-HX | FACILITY |  | 560 | 644 | 672 | 700 | 756 | 616 | 700 | 728 | 756 | 797
MIDW-TR03-345.0-230.0-13.8-HX | MIDWAY SUBSTATION | 70465 | 70286 | TR03 | TRANSFORMER | 230 | 560 | 644 | 672 | 700 | 756 | 616 | 700 | 728 | 756 | 840
MIDW-TR03-345.0-230.0-13.8-HX | MIDWAY SUBSTATION | 70465 | 70286 | TR03 | TRANSFORMER | 345 | 560 | 644 | 672 | 700 | 756 | 616 | 700 | 728 | 756 | 840
MIDW-TR03-345.0-230.0-13.8-HX | MIDWAY SUBSTATION | 70465 | 70286 | 5128 | BREAKER | 230 | 797 | 797 | 797 | 797 | 797 | 797 | 797 | 797 | 797 | 797
MSST-TR01-345.0-230.0-13.8-HX | MISSILE SITE | 70624 | 70623 | MSST-TR01-345.0-230.0-13.8-HX | FACILITY |  | 560 | 644 | 672 | 700 | 756 | 616 | 700 | 728 | 756 | 840
MSST-TR01-345.0-230.0-13.8-HX | MISSILE SITE | 70624 | 70623 | TR01 | TRANSFORMER | 230 | 560 | 644 | 672 | 700 | 756 | 616 | 700 | 728 | 756 | 840
MSST-TR01-345.0-230.0-13.8-HX | MISSILE SITE | 70624 | 70623 | TR01 | TRANSFORMER | 345 | 560 | 644 | 672 | 700 | 756 | 616 | 700 | 728 | 756 | 840
PAWN-TR02-345.0-230.0-13.8-HX | PAWNEE 345KV | 70598 | 70311 | PAWN-TR02-345.0-230.0-13.8-HX | FACILITY |  | 560 | 644 | 672 | 700 | 756 | 616 | 700 | 728 | 756 | 840
PAWN-TR02-345.0-230.0-13.8-HX | PAWNEE 345KV | 70598 | 70311 | TR02 | TRANSFORMER | 230 | 560 | 644 | 672 | 700 | 756 | 616 | 700 | 728 | 756 | 840
PAWN-TR02-345.0-230.0-13.8-HX | PAWNEE 345KV | 70598 | 70311 | TR02 | TRANSFORMER | 345 | 560 | 644 | 672 | 700 | 756 | 616 | 700 | 728 | 756 | 840
PAWN-TR03-345.0-230.0-13.8-HX | PAWNEE 345KV | 70598 | 70311 | PAWN-TR03-345.0-230.0-13.8-HX | FACILITY |  | 560 | 644 | 672 | 700 | 756 | 616 | 700 | 728 | 756 | 840
PAWN-TR03-345.0-230.0-13.8-HX | PAWNEE 345KV | 70598 | 70311 | TR03 | TRANSFORMER | 230 | 560 | 644 | 672 | 700 | 756 | 616 | 700 | 728 | 756 | 840
PAWN-TR03-345.0-230.0-13.8-HX | PAWNEE 345KV | 70598 | 70311 | TR03 | TRANSFORMER | 345 | 560 | 644 | 672 | 700 | 756 | 616 | 700 | 728 | 756 | 840
PONC-TR04-230.0-115.0-13.8-HX | PONCHA JUNCTION SUBSTATION | 70393 | 70327 | PONC-TR04-230.0-115.0-13.8-HX | FACILITY |  | 276 | 317 | 331 | 345 | 372 | 303 | 345 | 359 | 372 | 414
PONC-TR04-230.0-115.0-13.8-HX | PONCHA JUNCTION SUBSTATION | 70393 | 70327 | TR04 | TRANSFORMER | 115 | 276 | 317 | 331 | 345 | 372 | 303 | 345 | 359 | 372 | 414
PONC-TR04-230.0-115.0-13.8-HX | PONCHA JUNCTION SUBSTATION | 70393 | 70327 | TR04 | TRANSFORMER | 230 | 276 | 317 | 331 | 345 | 372 | 303 | 345 | 359 | 372 | 414
RIDG-TR02-230.0-115.0-13.8-HX | RIDGE SUBSTATION | 70355 | 70354 | RIDG-TR02-230.0-115.0-13.8-HX | FACILITY |  | 239 | 239 | 305 | 305 | 305 | 296 | 296 | 347 | 347 | 347
RIDG-TR02-230.0-115.0-13.8-HX | RIDGE SUBSTATION | 70355 | 70354 | 9686M | SWITCH | 115 | 239 | 239 | 309 | 309 | 309 | 296 | 296 | 355 | 355 | 355
RIDG-TR02-230.0-115.0-13.8-HX | RIDGE SUBSTATION | 70355 | 70354 | 9686L | SWITCH | 115 | 239 | 239 | 309 | 309 | 309 | 296 | 296 | 355 | 355 | 355
RIDG-TR02-230.0-115.0-13.8-HX | RIDGE SUBSTATION | 70355 | 70354 | 1000 - 61 | BUSBAR_SECTION | 115 | 260 | 260 | 305 | 305 | 305 | 311 | 311 | 347 | 347 | 347
RIDG-TR02-230.0-115.0-13.8-HX | RIDGE SUBSTATION | 70355 | 70354 | TR02 | TRANSFORMER | 115 | 285 | 327 | 342 | 356 | 384 | 313 | 356 | 370 | 384 | 427
RIDG-TR02-230.0-115.0-13.8-HX | RIDGE SUBSTATION | 70355 | 70354 | TR02 | TRANSFORMER | 230 | 285 | 327 | 342 | 356 | 384 | 313 | 356 | 370 | 384 | 427
SMOK-TR01-230.0-115.0-13.8-HX | SMOKY HILL SUBSTATION | 70396 | 70395 | SMOK-TR01-230.0-115.0-13.8-HX | FACILITY |  | 144 | 144 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159
SMOK-TR01-230.0-115.0-13.8-HX | SMOKY HILL SUBSTATION | 70396 | 70395 | TR01 | TRANSFORMER | 115 | 144 | 144 | 166 | 180 | 187 | 173 | 173 | 187 | 202 | 209
SMOK-TR01-230.0-115.0-13.8-HX | SMOKY HILL SUBSTATION | 70396 | 70395 | TR01 | TRANSFORMER | 230 | 144 | 144 | 166 | 180 | 187 | 173 | 173 | 187 | 202 | 209
SMOK-TR01-230.0-115.0-13.8-HX | SMOKY HILL SUBSTATION | 70396 | 70395 | 9860 135Y WATT XDCR | SECONDARY_CURRENT_LIMITATION | 115 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159
SMOK-TR01-230.0-115.0-13.8-HX | SMOKY HILL SUBSTATION | 70396 | 70395 | 9860 135Y AMP XDCR | SECONDARY_CURRENT_LIMITATION | 115 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159
SMOK-TR01-230.0-115.0-13.8-HX | SMOKY HILL SUBSTATION | 70396 | 70395 | 9860 246Y | CURRENT_TRANSFORMER | 115 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159
SMOK-TR01-230.0-115.0-13.8-HX | SMOKY HILL SUBSTATION | 70396 | 70395 | 9860 135Y | CURRENT_TRANSFORMER | 115 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159
SMOK-TR01-230.0-115.0-13.8-HX | SMOKY HILL SUBSTATION | 70396 | 70395 | 9860 135Y VAR XDCR | SECONDARY_CURRENT_LIMITATION | 115 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159
SMOK-TR02-230.0-115.0-13.8-HX | SMOKY HILL SUBSTATION | 70396 | 70395 | SMOK-TR02-230.0-115.0-13.8-HX | FACILITY |  | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159
SMOK-TR02-230.0-115.0-13.8-HX | SMOKY HILL SUBSTATION | 70396 | 70395 | 9860 135Y AMP XDCR | SECONDARY_CURRENT_LIMITATION | 115 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159
SMOK-TR02-230.0-115.0-13.8-HX | SMOKY HILL SUBSTATION | 70396 | 70395 | 9860 135Y VAR XDCR | SECONDARY_CURRENT_LIMITATION | 115 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159
SMOK-TR02-230.0-115.0-13.8-HX | SMOKY HILL SUBSTATION | 70396 | 70395 | 9860 135Y | CURRENT_TRANSFORMER | 115 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159
SMOK-TR02-230.0-115.0-13.8-HX | SMOKY HILL SUBSTATION | 70396 | 70395 | 9860 135Y WATT XDCR | SECONDARY_CURRENT_LIMITATION | 115 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159
SMOK-TR02-230.0-115.0-13.8-HX | SMOKY HILL SUBSTATION | 70396 | 70395 | 9860 246Y | CURRENT_TRANSFORMER | 115 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159
SMOK-TR02-230.0-115.0-13.8-HX | SMOKY HILL SUBSTATION | 70396 | 70395 | TR02 | TRANSFORMER | 230 | 168 | 168 | 193 | 202 | 210 | 185 | 185 | 210 | 218 | 227
SMOK-TR02-230.0-115.0-13.8-HX | SMOKY HILL SUBSTATION | 70396 | 70395 | TR02 | TRANSFORMER | 115 | 168 | 168 | 193 | 202 | 210 | 185 | 185 | 210 | 218 | 227
SMOK-TR04-345.0-230.0-13.8-HX | SMOKY HILL SUBSTATION | 70599 | 70396 | SMOK-TR04-345.0-230.0-13.8-HX | FACILITY |  | 560 | 644 | 672 | 700 | 756 | 616 | 700 | 728 | 756 | 840
SMOK-TR04-345.0-230.0-13.8-HX | SMOKY HILL SUBSTATION | 70599 | 70396 | TR04 | TRANSFORMER | 230 | 560 | 644 | 672 | 700 | 756 | 616 | 700 | 728 | 756 | 840
SMOK-TR04-345.0-230.0-13.8-HX | SMOKY HILL SUBSTATION | 70599 | 70396 | TR04 | TRANSFORMER | 345 | 560 | 644 | 672 | 700 | 756 | 616 | 700 | 728 | 756 | 840
SMOK-TR05-345.0-230.0-13.8-HX | SMOKY HILL SUBSTATION | 70599 | 70396 | SMOK-TR05-345.0-230.0-13.8-HX | FACILITY |  | 560 | 644 | 672 | 700 | 756 | 616 | 700 | 728 | 756 | 797
SMOK-TR05-345.0-230.0-13.8-HX | SMOKY HILL SUBSTATION | 70599 | 70396 | TR05 | TRANSFORMER | 345 | 560 | 644 | 672 | 700 | 756 | 616 | 700 | 728 | 756 | 840
SMOK-TR05-345.0-230.0-13.8-HX | SMOKY HILL SUBSTATION | 70599 | 70396 | TR05 | TRANSFORMER | 230 | 560 | 644 | 672 | 700 | 756 | 616 | 700 | 728 | 756 | 840
SMOK-TR05-345.0-230.0-13.8-HX | SMOKY HILL SUBSTATION | 70599 | 70396 | 5175 | BREAKER | 230 | 797 | 797 | 797 | 797 | 797 | 797 | 797 | 797 | 797 | 797
SODA-TR02-230.0-115.0-13.8-HX | SODA LAKES SUBSTATION | 70018 | 70400 | SODA-TR02-230.0-115.0-13.8-HX | FACILITY |  | 283 | 326 | 340 | 354 | 383 | 312 | 354 | 368 | 383 | 425
SODA-TR02-230.0-115.0-13.8-HX | SODA LAKES SUBSTATION | 70018 | 70400 | TR02 | TRANSFORMER | 230 | 283 | 326 | 340 | 354 | 383 | 312 | 354 | 368 | 383 | 425
SODA-TR02-230.0-115.0-13.8-HX | SODA LAKES SUBSTATION | 70018 | 70400 | TR02 | TRANSFORMER | 115 | 283 | 326 | 340 | 354 | 383 | 312 | 354 | 368 | 383 | 425
SULP-TR01-230.0-115.0-13.8-HX | SULPHUR SUBSTATION | 70524 | 70523 | SULP-TR01-230.0-115.0-13.8-HX | FACILITY |  | 170 | 170 | 195 | 204 | 212 | 187 | 187 | 212 | 221 | 229
SULP-TR01-230.0-115.0-13.8-HX | SULPHUR SUBSTATION | 70524 | 70523 | TR01 | TRANSFORMER | 115 | 170 | 170 | 195 | 204 | 212 | 187 | 187 | 212 | 221 | 229
SULP-TR01-230.0-115.0-13.8-HX | SULPHUR SUBSTATION | 70524 | 70523 | TR01 | TRANSFORMER | 230 | 170 | 170 | 195 | 204 | 212 | 187 | 187 | 212 | 221 | 229
SULP-TR02-230.0-115.0-13.8-HX | SULPHUR SUBSTATION | 70524 | 70523 | SULP-TR02-230.0-115.0-13.8-HX | FACILITY |  | 165 | 189 | 198 | 206 | 222 | 181 | 206 | 214 | 222 | 247
SULP-TR02-230.0-115.0-13.8-HX | SULPHUR SUBSTATION | 70524 | 70523 | TR02 | TRANSFORMER | 230 | 165 | 189 | 198 | 206 | 222 | 181 | 206 | 214 | 222 | 247
SULP-TR02-230.0-115.0-13.8-HX | SULPHUR SUBSTATION | 70524 | 70523 | TR02 | TRANSFORMER | 115 | 165 | 189 | 198 | 206 | 222 | 181 | 206 | 214 | 222 | 247
TARR-TR01-230.0-115.0-13.8-HX | TARRYALL SUBSTATION | 70427 | 70426 | TARR-TR01-230.0-115.0-13.8-HX | FACILITY |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
TARR-TR01-230.0-115.0-13.8-HX | TARRYALL SUBSTATION | 70427 | 70426 | TR01 X BCT SB | CURRENT_TRANSFORMER | 115 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
TARR-TR01-230.0-115.0-13.8-HX | TARRYALL SUBSTATION | 70427 | 70426 | TR01 | TRANSFORMER | 230 | 172 | 198 | 206 | 215 | 232 | 189 | 215 | 223 | 232 | 258
TARR-TR01-230.0-115.0-13.8-HX | TARRYALL SUBSTATION | 70427 | 70426 | TR01 | TRANSFORMER | 115 | 172 | 198 | 206 | 215 | 232 | 189 | 215 | 223 | 232 | 258
UTEG-TR01-345.0-230.0-13.8-HX | UTE GRAND JUNCTION SUBSTATION | 79036 | 70205 | UTEG-TR01-345.0-230.0-13.8-HX | FACILITY |  | 273 | 273 | 314 | 328 | 341 | 300 | 300 | 341 | 355 | 359
UTEG-TR01-345.0-230.0-13.8-HX | UTE GRAND JUNCTION SUBSTATION | 79036 | 70205 | TR01 | TRANSFORMER | 230 | 273 | 273 | 314 | 328 | 341 | 300 | 300 | 341 | 355 | 369
UTEG-TR01-345.0-230.0-13.8-HX | UTE GRAND JUNCTION SUBSTATION | 79036 | 70205 | TR01 | TRANSFORMER | 345 | 273 | 273 | 314 | 328 | 341 | 301 | 301 | 341 | 355 | 369
UTEG-TR01-345.0-230.0-13.8-HX | UTE GRAND JUNCTION SUBSTATION | 79036 | 70205 | TR01 H123 | CURRENT_TRANSFORMER | 345 | 359 | 359 | 359 | 359 | 359 | 359 | 359 | 359 | 359 | 359
UTEG-TR02-138.0-115.0-13.8-HX | UTE GRAND JUNCTION SUBSTATION | 79035 | 79034 | UTEG-TR02-138.0-115.0-13.8-HX | FACILITY |  | 100 | 115 | 120 | 125 | 135 | 110 | 125 | 130 | 135 | 150
UTEG-TR02-138.0-115.0-13.8-HX | UTE GRAND JUNCTION SUBSTATION | 79035 | 79034 | TR02 | TRANSFORMER | 115 | 100 | 115 | 120 | 125 | 135 | 110 | 125 | 130 | 135 | 150
UTEG-TR02-138.0-115.0-13.8-HX | UTE GRAND JUNCTION SUBSTATION | 79035 | 79034 | TR02 | TRANSFORMER | 138 | 100 | 115 | 120 | 125 | 135 | 110 | 125 | 130 | 135 | 150
UTER-TR03-230.0-138.0-13.8-HX | RIFLE UTE 230/345KV SUBSTATION | 79057 | 79056 | UTER-TR03-230.0-138.0-13.8-HX | FACILITY |  | 143 | 143 | 143 | 143 | 143 | 143 | 143 | 143 | 143 | 143
UTER-TR03-230.0-138.0-13.8-HX | RIFLE UTE 230/345KV SUBSTATION | 79057 | 79056 | R811 246X | CURRENT_TRANSFORMER | 138 | 143 | 143 | 143 | 143 | 143 | 143 | 143 | 143 | 143 | 143
UTER-TR03-230.0-138.0-13.8-HX | RIFLE UTE 230/345KV SUBSTATION | 79057 | 79056 | R814 | SWITCH | 138 | 143 | 143 | 185 | 185 | 185 | 178 | 178 | 213 | 213 | 213
UTER-TR03-230.0-138.0-13.8-HX | RIFLE UTE 230/345KV SUBSTATION | 79057 | 79056 | R812 | SWITCH | 138 | 143 | 143 | 185 | 185 | 185 | 178 | 178 | 213 | 213 | 213
UTER-TR03-230.0-138.0-13.8-HX | RIFLE UTE 230/345KV SUBSTATION | 79057 | 79056 | TR03 | TRANSFORMER | 230 | 145 | 145 | 167 | 174 | 181 | 159 | 159 | 181 | 188 | 196
UTER-TR03-230.0-138.0-13.8-HX | RIFLE UTE 230/345KV SUBSTATION | 79057 | 79056 | TR03 | TRANSFORMER | 138 | 145 | 145 | 167 | 174 | 181 | 159 | 159 | 181 | 189 | 196
UTER-TR04A-345.0-230.0-13.8-HX | RIFLE UTE 230/345KV SUBSTATION | 79058 | 79057 | UTER-TR04A-345.0-230.0-13.8-HX | FACILITY |  | 478 | 478 | 617 | 617 | 617 | 592 | 592 | 637 | 637 | 637
UTER-TR04A-345.0-230.0-13.8-HX | RIFLE UTE 230/345KV SUBSTATION | 79058 | 79057 | 55134E | SWITCH | 230 | 478 | 478 | 617 | 617 | 617 | 592 | 592 | 709 | 709 | 709
UTER-TR04A-345.0-230.0-13.8-HX | RIFLE UTE 230/345KV SUBSTATION | 79058 | 79057 | 55134W | SWITCH | 230 | 478 | 478 | 617 | 617 | 617 | 592 | 592 | 709 | 709 | 709
UTER-TR04A-345.0-230.0-13.8-HX | RIFLE UTE 230/345KV SUBSTATION | 79058 | 79057 | TR04A | TRANSFORMER | 230 | 542 | 542 | 624 | 637 | 637 | 596 | 596 | 637 | 637 | 637
UTER-TR04A-345.0-230.0-13.8-HX | RIFLE UTE 230/345KV SUBSTATION | 79058 | 79057 | TR04A | TRANSFORMER | 345 | 543 | 543 | 624 | 651 | 660 | 596 | 596 | 660 | 660 | 660
UTER-TR04A-345.0-230.0-13.8-HX | RIFLE UTE 230/345KV SUBSTATION | 79058 | 79057 | 55134 | BREAKER | 230 | 637 | 637 | 637 | 637 | 637 | 637 | 637 | 637 | 637 | 637
VALM-TR07-230.0-115.0-13.8-HX | VALMONT SWITCHYARD SUBSTATION | 70447 | 70444 | VALM-TR07-230.0-115.0-13.8-HX | FACILITY |  | 280 | 318 | 318 | 318 | 318 | 308 | 318 | 318 | 318 | 318
VALM-TR07-230.0-115.0-13.8-HX | VALMONT SWITCHYARD SUBSTATION | 70447 | 70444 | TR07 | TRANSFORMER | 115 | 280 | 319 | 319 | 319 | 319 | 308 | 319 | 319 | 319 | 319
VALM-TR07-230.0-115.0-13.8-HX | VALMONT SWITCHYARD SUBSTATION | 70447 | 70444 | TR07 | TRANSFORMER | 230 | 280 | 322 | 336 | 350 | 378 | 308 | 350 | 364 | 378 | 420
VALM-TR07-230.0-115.0-13.8-HX | VALMONT SWITCHYARD SUBSTATION | 70447 | 70444 | BK07 BCT X-SC | CURRENT_TRANSFORMER | 115 | 318 | 318 | 318 | 318 | 318 | 318 | 318 | 318 | 318 | 318
VALM-TR08-230.0-115.0-13.8-HX | VALMONT SWITCHYARD SUBSTATION | 70447 | 70444 | VALM-TR08-230.0-115.0-13.8-HX | FACILITY |  | 280 | 322 | 336 | 350 | 359 | 308 | 350 | 359 | 359 | 359
VALM-TR08-230.0-115.0-13.8-HX | VALMONT SWITCHYARD SUBSTATION | 70447 | 70444 | TR08 | TRANSFORMER | 230 | 280 | 322 | 336 | 350 | 378 | 308 | 350 | 364 | 378 | 420
VALM-TR08-230.0-115.0-13.8-HX | VALMONT SWITCHYARD SUBSTATION | 70447 | 70444 | TR08 | TRANSFORMER | 115 | 280 | 322 | 336 | 350 | 378 | 308 | 350 | 364 | 378 | 420
VALM-TR08-230.0-115.0-13.8-HX | VALMONT SWITCHYARD SUBSTATION | 70447 | 70444 | 9058 XDCR AMP A | SECONDARY_CURRENT_LIMITATION | 115 | 359 | 359 | 359 | 359 | 359 | 359 | 359 | 359 | 359 | 359
VALM-TR08-230.0-115.0-13.8-HX | VALMONT SWITCHYARD SUBSTATION | 70447 | 70444 | 9058 XDCR AMP BC | SECONDARY_CURRENT_LIMITATION | 115 | 359 | 359 | 359 | 359 | 359 | 359 | 359 | 359 | 359 | 359
WATE-TR01-230.0-115.0-13.8-HX | WATERTON SUBSTATION | 70464 | 70463 | WATE-TR01-230.0-115.0-13.8-HX | FACILITY |  | 284 | 327 | 341 | 355 | 384 | 313 | 355 | 369 | 384 | 426
WATE-TR01-230.0-115.0-13.8-HX | WATERTON SUBSTATION | 70464 | 70463 | TR01 | TRANSFORMER | 230 | 284 | 327 | 341 | 355 | 384 | 312 | 355 | 369 | 384 | 426
WATE-TR01-230.0-115.0-13.8-HX | WATERTON SUBSTATION | 70464 | 70463 | TR01 | TRANSFORMER | 115 | 284 | 327 | 341 | 355 | 384 | 312 | 355 | 369 | 384 | 426
WATE-TR02-230.0-115.0-13.8-HX | WATERTON SUBSTATION | 70464 | 70463 | WATE-TR02-230.0-115.0-13.8-HX | FACILITY |  | 284 | 327 | 341 | 355 | 384 | 313 | 355 | 369 | 384 | 426
WATE-TR02-230.0-115.0-13.8-HX | WATERTON SUBSTATION | 70464 | 70463 | TR02 | TRANSFORMER | 115 | 284 | 327 | 341 | 355 | 384 | 312 | 355 | 369 | 384 | 426
WATE-TR02-230.0-115.0-13.8-HX | WATERTON SUBSTATION | 70464 | 70463 | TR02 | TRANSFORMER | 230 | 284 | 327 | 341 | 355 | 384 | 312 | 355 | 369 | 384 | 426
WATE-TR03-345.0-230.0-13.8-HX | WATERTON SUBSTATION | 70466 | 70464 | WATE-TR03-345.0-230.0-13.8-HX | FACILITY |  | 560 | 644 | 672 | 700 | 756 | 616 | 700 | 728 | 756 | 840
WATE-TR03-345.0-230.0-13.8-HX | WATERTON SUBSTATION | 70466 | 70464 | TR03 | TRANSFORMER | 345 | 560 | 644 | 672 | 700 | 756 | 616 | 700 | 728 | 756 | 840
WATE-TR03-345.0-230.0-13.8-HX | WATERTON SUBSTATION | 70466 | 70464 | TR03 | TRANSFORMER | 230 | 560 | 644 | 672 | 700 | 756 | 616 | 700 | 728 | 756 | 840
WELD-TR01-230.0-115.0-13.8-HX | WELD SUBSTATION | 70471 | 70470 | WELD-TR01-230.0-115.0-13.8-HX | FACILITY |  | 280 | 322 | 336 | 350 | 378 | 308 | 350 | 364 | 378 | 420
WELD-TR01-230.0-115.0-13.8-HX | WELD SUBSTATION | 70471 | 70470 | TR01 | TRANSFORMER | 115 | 280 | 322 | 336 | 350 | 378 | 308 | 350 | 364 | 378 | 420
WELD-TR01-230.0-115.0-13.8-HX | WELD SUBSTATION | 70471 | 70470 | TR01 | TRANSFORMER | 230 | 280 | 322 | 336 | 350 | 378 | 308 | 350 | 364 | 378 | 420

## Transformer In Construction
|  | FAC-008-5 Transformer |  |  |  | OPCO: PSC |  |  |  |  | VALIDATION STATUS: VALID
[6 empty] | BES: Y |  |  |  |  | LIFE CYCLE STATUS: IN CONSTRUCTION
FACILITY DESIGNATION | SUBSTATION | HIGH SIDE PSSE | LOWSIDE PSSE | EQUIPMENT NAME | EQUIPMENT TYPE | VOLTAGE (kV) | SN (MVA) | SE8 (MVA) | SE4 (MVA) | SE2 (MVA) | SE30 (MVA) | WN (MVA) | WE8 (MVA) | WE4 (MVA) | WE2 (MVA) | WE30 (MVA) | COMMENTS
RIDG-TR02-230.0-115.0-13.8-HX | RIDGE SUBSTATION | 70355 | 70354 | RIDG-TR02-230.0-115.0-13.8-HX | FACILITY |  | 260 | 260 | 305 | 305 | 305 | 311 | 311 | 347 | 347 | 347
RIDG-TR02-230.0-115.0-13.8-HX | RIDGE SUBSTATION | 70355 | 70354 | 1000 - 61 | BUSBAR_SECTION | 115 | 260 | 260 | 305 | 305 | 305 | 311 | 311 | 347 | 347 | 347
RIDG-TR02-230.0-115.0-13.8-HX | RIDGE SUBSTATION | 70355 | 70354 | TR02 | TRANSFORMER | 115 | 285 | 327 | 342 | 356 | 384 | 313 | 356 | 370 | 384 | 427
RIDG-TR02-230.0-115.0-13.8-HX | RIDGE SUBSTATION | 70355 | 70354 | TR02 | TRANSFORMER | 230 | 285 | 327 | 342 | 356 | 384 | 313 | 356 | 370 | 384 | 427
SMOK-TR01-230.0-115.0-13.8-HX | SMOKY HILL SUBSTATION | 70396 | 70395 | SMOK-TR01-230.0-115.0-13.8-HX | FACILITY |  | 150 | 173 | 180 | 188 | 203 | 165 | 188 | 195 | 203 | 225
SMOK-TR01-230.0-115.0-13.8-HX | SMOKY HILL SUBSTATION | 70396 | 70395 | TR01 | TRANSFORMER | 230 | 150 | 172 | 180 | 188 | 203 | 165 | 188 | 195 | 203 | 225
SMOK-TR01-230.0-115.0-13.8-HX | SMOKY HILL SUBSTATION | 70396 | 70395 | TR01 | TRANSFORMER | 115 | 150 | 173 | 180 | 187 | 203 | 165 | 187 | 195 | 203 | 225
SMOK-TR02-230.0-115.0-13.8-HX | SMOKY HILL SUBSTATION | 70396 | 70395 | SMOK-TR02-230.0-115.0-13.8-HX | FACILITY |  | 168 | 168 | 193 | 202 | 210 | 185 | 185 | 210 | 218 | 227
SMOK-TR02-230.0-115.0-13.8-HX | SMOKY HILL SUBSTATION | 70396 | 70395 | TR02 | TRANSFORMER | 115 | 168 | 168 | 193 | 202 | 210 | 185 | 185 | 210 | 218 | 227
SMOK-TR02-230.0-115.0-13.8-HX | SMOKY HILL SUBSTATION | 70396 | 70395 | TR02 | TRANSFORMER | 230 | 168 | 168 | 193 | 202 | 210 | 185 | 185 | 210 | 218 | 227
TARR-TR01-230.0-115.0-13.8-HX | TARRYALL SUBSTATION | 70427 | 70426 | TARR-TR01-230.0-115.0-13.8-HX | FACILITY |  | 172 | 198 | 206 | 215 | 219 | 189 | 215 | 219 | 219 | 219
TARR-TR01-230.0-115.0-13.8-HX | TARRYALL SUBSTATION | 70427 | 70426 | TR01 | TRANSFORMER | 115 | 172 | 198 | 206 | 215 | 232 | 189 | 215 | 223 | 232 | 258
TARR-TR01-230.0-115.0-13.8-HX | TARRYALL SUBSTATION | 70427 | 70426 | TR01 | TRANSFORMER | 230 | 172 | 198 | 206 | 215 | 232 | 189 | 215 | 223 | 232 | 258
TARR-TR01-230.0-115.0-13.8-HX | TARRYALL SUBSTATION | 70427 | 70426 | TR01 X BCT SB | CURRENT_TRANSFORMER | 115 | 219 | 219 | 219 | 219 | 219 | 219 | 219 | 219 | 219 | 219

## Lamar DC Tie
LAMAR DC TIE AMBIENT ADJUSTED FACILITY EQUIPMENT RATINGS FAC-008-5
REVISED 4/27/2021
Element | Rating | Ambient Temp (°C) | Ambient Temp (°F) | - | Limit (MW) | Overload (P.U.) | Comments | References
Inverter | Normal | N/A | N/A | - | 210 | N/A |  | Section 6.1 of Main Circuit Parameters Document.
| Continuous Overload | < 0 | < 32 | - | 252 | 1.2 | Overload values were interpolated from the "with out redundant cooling" line in the reference figure given by the manufacturer. | Figure 2 in Section 6.3.1 of Main Main Circuit Parameters Document.
|  | 10 | 50 | - | 242.4545 | 1.1545
|  | 20 | 68 | - | 232.9091 | 1.1091
|  | 30 | 86 | - | 223.3636 | 1.0636
|  | 40 | 104 | - | 213.8182 | 1.0182
|  | 44 | 111.2 | - | 210 | 1
| 2 Hour Overload | < 15 | < 59 | - | 252 | 1.2 | Overload values were interpolated from the "with out redundant cooling" line in the reference figure given by the manufacturer. | Figure 3 in Section 6.3.2 of Main Main Circuit Parameters Document.
|  | 20 | 68 | - | 244.7586 | 1.1655
|  | 30 | 86 | - | 230.2759 | 1.0966
|  | 40 | 104 | - | 215.7931 | 1.0276
|  | 44 | 111.2 | - | 210 | 1
Element | Rating | Ambient Temp (°C) | Ambient Temp (°F) | High Side Limit (Amps) | Limit (MVA) | Overload (P.U.) | Comments | References
230kV Transformer | Normal | N/A | N/A | 564.7992 | 225 | N/A |  | Transformer Nameplate
| Continuous Overload | < 0 | < 32 | 713 | 284.039 | 1.2624 | Overload values shown for the two transformers are slightly different based on the High Side Limits given by the manufacturer. | Section 5.3 of Pole Control Design Specification Document
|  | 10 | 50 | 688 | 274.0797 | 1.2181
|  | 20 | 68 | 664 | 264.5188 | 1.1756
|  | 30 | 86 | 639 | 254.5595 | 1.1314
|  | 40 | 104 | 615 | 244.9986 | 1.0889
|  | 44 | 111.2 | 605 | 241.0149 | 1.0712
| 2 Hour Overload | < 0 | < 32 | 713 | 284.039 | 1.2624 | Overload values shown for the two transformers are slightly different based on the High Side Limits given by the manufacturer. | Section 5.3 of Pole Control Design Specification Document
|  | 10 | 50 | 713 | 284.039 | 1.2624
|  | 20 | 68 | 694 | 276.4699 | 1.2288
|  | 30 | 86 | 657 | 261.7302 | 1.1632
|  | 40 | 104 | 620 | 246.9904 | 1.0977
|  | 44 | 111.2 | 605 | 241.0149 | 1.0712
Element | Rating | Ambient Temp (°C) | Ambient Temp (°F) | High Side Limit (Amps) | Limit (MVA) | Overload (P.U.) | Comments | References
345kV Transformer | Normal | N/A | N/A | 376.5328 | 225 | N/A |  | Transformer Nameplate
| Continuous Overload | < 0 | < 32 | 475 | 283.8398 | 1.2615 | Overload values shown for the two transformers are slightly different based on the High Side Limits given by the manufacturer. | Section 5.3 of Pole Control Design Specification Document
|  | 10 | 50 | 459 | 274.2789 | 1.219
|  | 20 | 68 | 442 | 264.1204 | 1.1739
|  | 30 | 86 | 426 | 254.5595 | 1.1314
|  | 40 | 104 | 410 | 244.9986 | 1.0889
|  | 44 | 111.2 | 403 | 240.8157 | 1.0703
| 2 Hour Overload | < 0 | < 32 | 475 | 283.8398 | 1.2615 | Overload values shown for the two transformers are slightly different based on the High Side Limits given by the manufacturer. | Section 5.3 of Pole Control Design Specification Document
|  | 10 | 50 | 475 | 283.8398 | 1.2615
|  | 20 | 68 | 463 | 276.6691 | 1.2296
|  | 30 | 86 | 438 | 261.7302 | 1.1632
|  | 40 | 104 | 413 | 246.7913 | 1.0969
|  | 44 | 111.2 | 403 | 240.8157 | 1.0703
REFERENCES |  | PROJECTWISE LINK
Main Circuit Parameters |  | 030808_T01_01_05_001_MainCircuitParametersRev1
Pole Control Design Specification |  | Pole control_design spec_rev2.pdf
345kV Transformer nameplate |  | A736 - Lamar HVDC 345kV 75MVA 1PH
230kV Transofmer nameplate |  | A735 - Lamar HVDC 230kV 75MVA 1PH

## Ambient Adjusted Ratings
SUBSTATION / TRANSMISSION AMBIENT ADJUSTED FACILITY EQUIPMENT RATINGS FAC-008-5
NUMERICAL LISTING BY CIRCUIT NUMBER
Bus Rating
SUBSTATION / TRANSMISSION FACILITY EQUIPMENT RATINGS FAC-008-3 Revision 2018-04 August, 2018 |  |  |  |  | Transmission & Substation Equipment Rating for T-line | [11 empty] | Next Limiting Element | [11 empty] | Substation | Bus / Line Breaker Rating | [9 empty] | Breaker 2 Rating | [9 empty] | Breaker 3 Rating
Line # | kV | From | To | Ambient Outside Temperature ( °F ) | Source Of Limiting Element | Limiting Element | Summer |  |  |  | Source Of Limiting Element | Limiting Element | Winter |  |  |  | Source Of Limiting Element | Limiting Element | Summer |  |  |  | Source Of Limiting Element | Limiting Element | Winter |  |  |  |  | Line Bkr # | Limiting Element | Summer |  | Winter |  | Summer |  | Winter |  | Bkr # | Limiting Element | Summer |  | Winter |  | Summer |  | Winter |  | Bkr # | Limiting Element | Summer |  | Winter |  | Summer |  | Winter |  | Jointly Owned
[7 empty] | Normal Rating MVA | Emerg. Rating MVA | Normal Rating Amps | Emerg. Rating Amps |  |  | Normal Rating MVA | Emerg. Rating MVA | Normal Rating Amps | Emerg. Rating Amps |  |  | Normal Rating MVA | Emerg. Rating MVA | Normal Rating Amps | Emerg. Rating Amps |  |  | Normal Rating MVA | Emerg. Rating MVA | Normal Rating Amps | Emerg. Rating Amps |  |  |  | Normal Rating MVA | Emerg. Rating MVA | Normal Rating MVA | Emerg. Rating MVA | Normal Rating Amps | Emerg. Rating Amps | Normal Rating Amps | Emerg. Rating Amps |  |  | Normal Rating MVA | Emerg. Rating MVA | Normal Rating MVA | Emerg. Rating MVA | Normal Rating Amps | Emerg. Rating Amps | Normal Rating Amps | Emerg. Rating Amps |  |  | Normal Rating MVA | Emerg. Rating MVA | Normal Rating MVA | Emerg. Rating MVA | Normal Rating Amps | Emerg. Rating Amps | Normal Rating Amps | Emerg. Rating Amps | PSCo | PRPA | TSGT | WAPA | Other | Comments | Revision Date
9255 | 115 | Malta Sub. | Twin Lakes Tap | 104 | Transmission Line | T-Line Conductor | 111.5441 | 111.5441 | 560 | 560 | [49 empty] | X |  |  |  |  | Converted to GIST2 | 2016-05-30
|  |  |  | 100 | Transmission Line | T-Line Conductor | 117.3205 | 117.3205 | 589 | 589
|  |  |  | 90 | Transmission Line | T-Line Conductor | 130.8651 | 130.8651 | 657 | 657
|  |  |  | 80 | Transmission Line | T-Line Conductor | 143.2146 | 143.2146 | 719 | 719
|  |  |  | 75 | Transmission Line | T-Line Conductor | 148.7918 | 148.7918 | 747 | 747 | Transmission Line | T-Line Conductor | 149.3894 | 149.3894 | 750 | 750
|  |  |  | 70 | Transmission Line | T-Line Conductor | 154.369 | 154.369 | 775 | 775 | Transmission Line | T-Line Conductor | 154.7674 | 154.7674 | 777 | 777
|  |  |  | 60 | Transmission Line | T-Line Conductor | 164.7267 | 164.7267 | 827 | 827 | Transmission Line | T-Line Conductor | 165.1251 | 165.1251 | 829 | 829
|  |  |  | 50 | Transmission Line | T-Line Conductor | 174 | 174.4868 | 876 | 876 | Transmission Line | T-Line Conductor | 174.8852 | 174.8852 | 878 | 878
|  |  |  | 40 | Transmission Line | T-Line Conductor | 184 | 183.6493 | 922 | 922 | Transmission Line | T-Line Conductor | 184.0477 | 184.0477 | 924 | 924
|  |  |  | 30 | Transmission Line | T-Line Conductor | 192 | 192.4135 | 966 | 966 | Transmission Line | T-Line Conductor | 192.8119 | 192.8119 | 968 | 968
|  |  |  | 20 | Transmission Line | T-Line Conductor | 201 | 201 | 1007 | 1007 | Transmission Line | T-Line Conductor | 201 | 201 | 1009 | 1009
|  |  |  | 10 | Transmission Line | T-Line Conductor | 209 | 209 | 1047 | 1047 | Transmission Line | T-Line Conductor | 209 | 209 | 1049 | 1049
|  |  |  | 0 | Transmission Line | T-Line Conductor | 216 | 216 | 1085 | 1085 | Transmission Line | T-Line Conductor | 217 | 217 | 1087 | 1087
9255 | 115 | Otero Pumping Station Tap | Buena Vista Tap | 104 | Transmission Line | T-Line Conductor | 121.5034 | 121.5034 | 610 | 610 | [49 empty] | X |  |  |  |  | New Rating From Transmission | 2013-01-09
|  |  |  | 100 | Transmission Line | T-Line Conductor | 126.8814 | 126.8814 | 637 | 637
|  |  |  | 90 | Transmission Line | T-Line Conductor | 139.0317 | 139.0317 | 698 | 698
|  |  |  | 80 | Transmission Line | T-Line Conductor | 150.3853 | 150.3853 | 755 | 755
|  |  |  | 75 | Transmission Line | T-Line Conductor | 155.5641 | 155.5641 | 781 | 781 | Transmission Line | T-Line Conductor | 156.1617 | 156.1617 | 784 | 784
|  |  |  | 70 | Transmission Line | T-Line Conductor | 160.743 | 160.743 | 807 | 807 | Transmission Line | T-Line Conductor | 161.1413 | 161.1413 | 809 | 809
|  |  |  | 60 | Transmission Line | T-Line Conductor | 170.5031 | 170.5031 | 856 | 856 | Transmission Line | T-Line Conductor | 170.9015 | 170.9015 | 858 | 858
|  |  |  | 50 | Transmission Line | T-Line Conductor | 179.6656 | 179.6656 | 902 | 902 | Transmission Line | T-Line Conductor | 180.064 | 180.064 | 904 | 904
|  |  |  | 40 | Transmission Line | T-Line Conductor | 188.2306 | 188.2306 | 945 | 945 | Transmission Line | T-Line Conductor | 188.629 | 188.629 | 947 | 947
|  |  |  | 30 | Transmission Line | T-Line Conductor | 196.5964 | 196.5964 | 987 | 987 | Transmission Line | T-Line Conductor | 196.9948 | 196.9948 | 989 | 989
|  |  |  | 20 | Transmission Line | T-Line Conductor | 204.3647 | 204.3647 | 1026 | 1026 | Transmission Line | T-Line Conductor | 204.763 | 204.763 | 1028 | 1028
|  |  |  | 10 | Transmission Line | T-Line Conductor | 211.9337 | 211.9337 | 1064 | 1064 | Transmission Line | T-Line Conductor | 212.3321 | 212.3321 | 1066 | 1066
|  |  |  | 0 | Transmission Line | T-Line Conductor | 219.3036 | 219 | 1101 | 1101 | Transmission Line | T-Line Conductor | 219.702 | 219.702 | 1103 | 1103
9255 | 115 | Buena Vista Tap | Ray Lewis Sub. | 104 | Transmission Line | T-Line Conductor | 91.4263 | 91.4263 | 459 | 459 | [49 empty] | X |  |  |  |  | Converted to GIST2 | 2016-05-30
|  |  |  | 100 | Transmission Line | T-Line Conductor | 98.7962 | 98.7962 | 496 | 496
|  |  |  | 90 | Transmission Line | T-Line Conductor | 115.3286 | 115.3286 | 579 | 579
|  |  |  | 80 | Transmission Line | T-Line Conductor | 129.67 | 129.67 | 651 | 651
|  |  |  | 75 | Transmission Line | T-Line Conductor | 136.2431 | 136.2431 | 684 | 684 | Transmission Line | T-Line Conductor | 136.8407 | 136.8407 | 687 | 687
|  |  |  | 70 | Transmission Line | T-Line Conductor | 142.6171 | 142.6171 | 716 | 716 | Transmission Line | T-Line Conductor | 143.0154 | 143.0154 | 718 | 718
|  |  |  | 60 | Transmission Line | T-Line Conductor | 154.1698 | 154.1698 | 774 | 774 | Transmission Line | T-Line Conductor | 154.7674 | 154.7674 | 777 | 777
|  |  |  | 50 | Transmission Line | T-Line Conductor | 165.1251 | 165.1251 | 829 | 829 | Transmission Line | T-Line Conductor | 165.5234 | 165.5234 | 831 | 831
|  |  |  | 40 | Transmission Line | T-Line Conductor | 175.2835 | 175.2835 | 880 | 880 | Transmission Line | T-Line Conductor | 175.6819 | 175.6819 | 882 | 882
|  |  |  | 30 | Transmission Line | T-Line Conductor | 184.8445 | 184.8445 | 928 | 928 | Transmission Line | T-Line Conductor | 185.2428 | 185.2428 | 930 | 930
|  |  |  | 20 | Ray Lewis Sub. / Transmission Line | 636 ACSR Jumper / T-Line Conductor | 185.2428 | 193.8078 | 930 | 973 | Transmission Line | T-Line Conductor | 194.2062 | 194.2062 | 975 | 975
|  |  |  | 10 | Ray Lewis Sub. / Transmission Line | 636 ACSR Jumper / T-Line Conductor | 185.2428 | 202.572 | 930 | 1017 | Transmission Line | T-Line Conductor | 202.9704 | 202.9704 | 1019 | 1019
|  |  |  | 0 | Ray Lewis Sub. | 636 ACSR Jumper | 185.2428 | 203.7671 | 930 | 1023 | Ray Lewis/ Transmission Line | 636 ACSR Jumper / T-Line Conductor | 210.9378 | 211.137 | 1059 | 1060
9255 | 115 | Ray Lewis Sub. | Poncha Junction Sub. | 104 | Poncha Jct Sub. / Transmission Line | Switch / T-Line Conductor | 119.5115 | 123.8936 | 600 | 622 | [49 empty] | X |  |  |  |  | Converted to GIST2 | 2016-05-30
|  |  |  | 100 | Poncha Jct Sub. / Transmission Line | Switch / T-Line Conductor | 119.5115 | 129.0724 | 600 | 648
|  |  |  | 90 | Poncha Jct Sub. / Transmission Line | Switch / T-Line Conductor | 119.5115 | 129.0724 | 600 | 648
|  |  |  | 80 | Poncha Jct Sub. / Transmission Line | Switch / T-Line Conductor | 119.5115 | 129.0724 | 600 | 648
|  |  |  | 75 | Poncha Jct Sub. / Transmission Line | Switch / T-Line Conductor | 119.5115 | 129.0724 | 600 | 648 | [5 empty] | 792
|  |  |  | 70 | Poncha Jct Sub. / Transmission Line | Switch / T-Line Conductor | 119.5115 | 129.0724 | 600 | 648 | [5 empty] | 817
|  |  |  | 60 | Poncha Junction Sub. | Switch / Switch | 119.5115 | 154.369 | 600 | 775 | Poncha Jct Sub. / Transmission Line | Switch / T-Line Conductor | 147.9951 | 172.2958 | 743 | 865
|  |  |  | 50 | Poncha Junction Sub. | Switch / Switch | 119.5115 | 154.369 | 600 | 775 | Poncha Junction Sub. | Switch / Switch | 147.9951 | 177.2754 | 743 | 890
|  |  |  | 40 | Poncha Junction Sub. | Switch / Switch | 119.5115 | 154.369 | 600 | 775 | Poncha Junction Sub. | Switch / Switch | 147.9951 | 177.2754 | 743 | 890
|  |  |  | 30 | Poncha Junction Sub. | Switch / Switch | 119.5115 | 154.369 | 600 | 775 | Poncha Junction Sub. | Switch / Switch | 147.9951 | 177.2754 | 743 | 890
|  |  |  | 20 | Poncha Junction Sub. | Switch / Switch | 119.5115 | 154.369 | 600 | 775 | Poncha Junction Sub. | Switch / Switch | 147.9951 | 177.2754 | 743 | 890
|  |  |  | 10 | Poncha Junction Sub. | Switch / Switch | 119.5115 | 154.369 | 600 | 775 | Poncha Junction Sub. | Switch / Switch | 147.9951 | 177.2754 | 743 | 890
|  |  |  | 0 | Poncha Junction Sub. | Switch / Switch | 119.5115 | 154.369 | 600 | 775 | Poncha Junction Sub. | Switch / Switch | 147.9951 | 177.2754 | 743 | 890

## E.S. Generation
PSCo Region Energy Supply Facility Equipment Ratings
BES Plant |  | Name Plate Data | [22 empty] | Most Limiting Equipment | [14 empty] | Next Most Limiting Equipment
[7 empty] | Gen | GSU |  |  |  | LS GSU | LS GSU | HS GSU | LS Value | LS Gen | LS Gen |  | Limiting I Hi Side of GSU to Transmission | LS Value Lmt I Hi Side of GSU to Trans |  |  | Series/Shunt |  | HS of GSU | LS of GSU | Limiting |  |  |  | Gen | LS GSU | LS Value | LS Gen | LS Gen | LS Value |  |  | Series/Shunt | HS of GSU | LS of GSU | Limiting
|  | Gen | Gen | Gen | Gen CT | Gen Bus | Disconnect | Subs ID | GSU TR | GSU HS | GSU LS | Disconnect | CT | CT | HS GSU | Bkr | Bkr CTs | GSU TR |  |  | LS GSU TR | Relay Trip | Compensation | HS GSU TR | Limiting | Limiting | Electrical | Gen | Gen CT | Gen Bus | Disconnect | CT | HS GSU | Bkr | Bkr CTs | Hi Side of GSU to Yard | GSU TR | Relay Trip | Compensation | Limiting | Limiting | Electrical
Plant | Unit | MVA | KV | Amps | Amps | Amps | Amps | A number | MVA | kVolt | kVolt | Amps | Amps | Amps | CT Amps | Amps | Amps | Ratio |  |  | Amps | Amps | Devices | Amps | Current | Current | Equipment | Amps | Amps | Amps | Amps | Amps | CT Amps | Amps | Amps | (Info from Trans) | Amps | Amps | Devices | Current | Current | Equipment
Alamosa - Summer | 2 | 20.8056 | 13.8 | 870.4415 | 2000 | 1584.806 | NA | A48601 | 28 | 115 | 13.2 | NA | 1200 | 400 | 3484.8485 | 1200 | 2000 | 8.7121 | 921 | 8023.8636 | 1224.6824 | 2600.5508 | NA | 140.5722 | 99.9115 | 870.4415 | Generator | 870.4415 | 2000 | 1584.806 | NA | 1200 | 3484.8485 | 1200 | 2000 | 8023.8636 | 1224.6824 | 2600.5508 | NA | 137.7391 | 1200 | Generator Breaker*
Alamosa - Winter | 2 | 30.1389 | 13.8 | 1260.92 | 2000 | 2354.502 | NA | A48601 | 28 | 115 | 13.2 | NA | 1200 | 400 | 3484.8485 | 1200 | 2000 | 8.7121 | 1100 | 9583.3333 | 1224.6824 | 2600.5508 | NA | 140.5722 | 137.7391 | 1200 | Generator Breaker* | 1260.92 | 2000 | 2354.502 | NA | 1200 | 3484.8485 | 1200 | 2000 | 9583.3333 | 1224.6824 | 2600.5508 | NA | 137.7391 | 1200 | GSU Low Side CT*
Blue Spruce - Summer | 1 | 234 | 18 | 7506 | 10000 | 8000 | NA |  | 235 | 235.75 | 18 | NA | 8000 | 2000 | 26194.4444 | NA | NA | 13.0972 | 800 | 10477.7778 | 7540 | 14148 | NA | 576 | 573.0986 | 7506 | Generator | 7506 | 10000 | 8000 | NA | 8000 | 26194.4444 | NA | NA | 10477.7778 | 7540 | 14148 | NA | 575.6946 | 7540 | GSU
Blue Spruce - Winter | 1 | 234 | 18 | 7506 | 10000 | 8000 | NA |  | 235 | 235.75 | 18 | NA | 8000 | 2000 | 26194.4444 | NA | NA | 13.0972 | 800 | 10477.7778 | 7540 | 14148 | NA | 576 | 573.0986 | 7506 | Generator | 7506 | 10000 | 8000 | NA | 8000 | 26194.4444 | NA | NA | 10477.7778 | 7540 | 14148 | NA | 575.6946 | 7540 | GSU
Blue Spruce - Summer | 2 | 234 | 18 | 7506 | 10000 | 8000 | NA |  | 235 | 235.75 | 18 | NA | 8000 | 2000 | 26194.4444 | NA | NA | 13.0972 | 800 | 10477.7778 | 7540 | 14148 | NA | 576 | 573.0986 | 7506 | Generator | 7506 | 10000 | 8000 | NA | 8000 | 26194.4444 | NA | NA | 10477.7778 | 7540 | 14148 | NA | 575.6946 | 7540 | GSU
Blue Spruce - Winter | 2 | 234 | 18 | 7506 | 10000 | 8000 | NA |  | 235 | 235.75 | 18 | NA | 8000 | 2000 | 26194.4444 | NA | NA | 13.0972 | 800 | 10477.7778 | 7540 | 14148 | NA | 576 | 573.0986 | 7506 | Generator | 7506 | 10000 | 8000 | NA | 8000 | 26194.4444 | NA | NA | 10477.7778 | 7540 | 14148 | NA | 575.6946 | 7540 | GSU
Blue Spruce 230 kV- Summer | C | 468 | 18 | 15012 | 20000 | 16000 | NA |  | 470 | 235.75 | 18 | NA | 16000 | 4000 | 52388.8889 | NA | NA | 13.0972 | 1500 | 19645.8333 | 15080 | NA | NA | NA | 1146.1972 | 15012 | Generators | 15012 | 20000 | 16000 | NA | 16000 | 52388.8889 | NA | NA | 19645.8333 | 15080 | NA | NA | 1151.3892 | 15080 | GSU Transformers
Blue Spruce 230 kV - Winter | C | 468 | 18 | 15012 | 20000 | 16000 | NA |  | 470 | 235.75 | 18 | NA | 16000 | 4000 | 52388.8889 | NA | NA | 13.0972 | 1500 | 19645.8333 | 15080 | NA | NA | NA | 1146.1972 | 15012 | Generators | 15012 | 20000 | 16000 | NA | 16000 | 52388.8889 | NA | NA | 19645.8333 | 15080 | NA | NA | 1151.3892 | 15080 | GSU Transformers
Cabin Creek | A | 187 | 13.8 | 7824 | 10000 | 9000 | 9000 | A35401, 2, 3 | 219.9 | 241.5 | 13.8 | NA | 10000 | 1200 | 21000 | NA | NA | 17.5 | 640 | 11200 | 9199.951 | NA | NA | 526 | 447.0857 | 7824 | Generator | 7824 | 10000 | 9000 | 9000 | 10000 | 21000 | NA | NA | 11200 | 9199.951 | NA | NA | 514.2857 | 9000 | Gen Bus *
| B | 187 | 13.8 | 7824 | 10000 | 9000 | 9000 | A35404, 5, 6 | 219.9 | 241.5 | 13.8 | NA | 10000 | 1200 | 21000 | NA | NA | 17.5 | 640 | 11200 | 9199.951 | NA | NA | 526 | 447.0857 | 7824 | Generator | 7824 | 10000 | 9000 | 9000 | 10000 | 21000 | NA | NA | 11200 | 9199.951 | NA | NA | 514.2857 | 9000 | Gen Bus *
Cherokee | SC | 116.0172 | 15.5 | 4321.4571 | 7000 | 6500 | NA | A72401 | 141 | 112.13 | 14.8 | NA | 8000 | NA | NA | NA | NA | 7.5764 | 860 | 6515.6622 | 5504.4575 | 8265 | NA | 727 | 570.3876 | 4321.4571 | Generator | 4321.4571 | 7000 | 6500 | NA | 8000 | NA | NA | NA | 6515.6622 | 5504.4575 | 8265 | NA | 726.5314 | 5504.4575 | GSU
Cherokee | 4 | 448 | 22 | 11757 | 14000 | 12000 | NA | A55601 | 504 | 115 | 21 | NA | NA | 3000 | 16428.5714 | NA | NA | 5.4762 | 2000 | 10952.381 | 13855 | NA | NA | 2530 | 2000 | 10952.381 | Yard Switches | 11757 | 14000 | 12000 | NA | NA | 16428.5714 | NA | NA | 10952.381 | 13855 | NA | NA | 2146.9304 | 11757 | Gen Bus
Cherokee - Summer | 5 | 218 | 18 | 6992 | 8000 | 7500 | 7500 |  | 210 | 115 | 17.55 | NA | 8000 | 1600 | 10484.3305 | 7500 | 8000 | 6.5527 | 1028 | 6736.1823 | 6908.5 | 13978 | NA | 1054.3 | 1028 | 6736.1823 | 954 kCML Conductor | 6992 | 8000 | 7500 | 7500 | 8000 | 10484.3305 | 7500 | 8000 | 6736.1823 | 6908.5 | 13978 | NA | 1054.2972 | 6908.5 | GSU
Cherokee - Winter | 5 | 218 | 18 | 6992 | 8000 | 7500 | 7500 |  | 210 | 115 | 17.55 | NA | 8000 | 1600 | 10484.3305 | 7500 | 8000 | 6.5527 | 1227 | 8040.1709 | 6908.5 | 13978 | NA | 1054.3 | 1054.2972 | 6908.5 | GSU | 6992 | 8000 | 7500 | 7500 | 8000 | 10484.3305 | 7500 | 8000 | 8040.1709 | 6908.5 | 13978 | NA | 1067.04 | 6992 | Generator
Cherokee - Summer | 6 | 218 | 18 | 6992 | 8000 | 7500 | 7500 |  | 210 | 115 | 17.55 | NA | 8000 | 1600 | 10484.3305 | 7500 | 8000 | 6.5527 | 1028 | 6736.1823 | 6908.5 | 13978 | NA | 1054.3 | 1028 | 6736.1823 | 954 kCML Conductor | 6992 | 8000 | 7500 | 7500 | 8000 | 10484.3305 | 7500 | 8000 | 6736.1823 | 6908.5 | 13978 | NA | 1054.2972 | 6908.5 | GSU
Cherokee - Winter | 6 | 218 | 18 | 6992 | 8000 | 7500 | 7500 |  | 210 | 115 | 17.55 | NA | 8000 | 1600 | 10484.3305 | 7500 | 8000 | 6.5527 | 1227 | 8040.1709 | 6908.5 | 13978 | NA | 1054.3 | 1054.2972 | 6908.5 | GSU | 6992 | 8000 | 7500 | 7500 | 8000 | 10484.3305 | 7500 | 8000 | 8040.1709 | 6908.5 | 13978 | NA | 1067.04 | 6992 | Generator
Cherokee - Summer | 7 | 300 | 18 | 9623 | 12000 | 12000 | NA |  | 300 | 115 | 17.55 | NA | 15000 | 2400 | 15726.4957 | NA | NA | 6.5527 | 2000 | 13105.4131 | 9869.2354 | 17718 | NA | 1545 | 1468.5535 | 9623 | Generator | 9623 | 12000 | 12000 | NA | 15000 | 15726.4957 | NA | NA | 13105.4131 | 9869.2354 | 17718 | NA | 1506.1311 | 9869.2354 | GSU
Cherokee - Winter | 7 | 300 | 18 | 9623 | 12000 | 12000 | NA |  | 300 | 115 | 17.55 | NA | 15000 | 2400 | 15726.4957 | NA | NA | 6.5527 | 2000 | 13105.4131 | 9869.2354 | 17718 | NA | 1545 | 1468.5535 | 9623 | Generator | 9623 | 12000 | 12000 | NA | 15000 | 15726.4957 | NA | NA | 13105.4131 | 9869.2354 | 17718 | NA | 1506.1311 | 9869.2354 | GSU
Comanche | 2 | 440 | 24 | 10585 | 12000 | 12000 | NA | A625 | 470 | 230 | 23 | NA | NA | 1200 | 12000 | NA | NA | 10 | 1200 | 12000 | 11798.0272 | 22190 | NA | 1179 | 1058.5 | 10585 | Generator | 10585 | 12000 | 12000 | NA | NA | 12000 | NA | NA | 12000 | 11798.0272 | 22190 | NA | 1179.8027 | 11798.0272 | GSU
Summer | 3 | 1008 | 27 | 21554 | 27000 | 22689 | NA |  | 1008 | 353.625 | 27 | NA | 27713 | 2000 | 26194.4444 | NA | NA | 13.0972 | 2000 | 26194.4444 | 21554.41 | 43072.8 | NA | 1645.7 | 1645.6925 | 21554 | Generator* | 21554 | 27000 | 22689 | NA | 27713 | 26194.4444 | NA | NA | 26194.4444 | 21554.41 | 43072.8 | NA | 1645.7238 | 21554.41 | GSU*
Winter | 3 | 1008 | 27 | 21554 | 27000 | 22689 | NA |  | 1008 | 353.625 | 27 | NA | 27713 | 2000 | 26194.4444 | NA | NA | 13.0972 | 2000 | 26194.4444 | 21554.41 | 43072.8 | NA | 1645.7 | 1645.6925 | 21554 | Generator* | 21554 | 27000 | 22689 | NA | 27713 | 26194.4444 | NA | NA | 26194.4444 | 21554.41 | 43072.8 | NA | 1645.7238 | 21554.41 | GSU*
Fort St Vrain - Summer | 1 | 403 | 22 | 10576 | 12000 | 11300 | NA | A38401 | 451.36 | 230 | 21 | NA | NA | 3300 | 36142.8571 | NA | NA | 10.9524 | 1200 | 13142.8571 | 12409.1818 | 21593.4 | NA | 1133.242 | 965.6348 | 10576 | Generator | 10576 | 12000 | 11300 | NA | NA | 36142.8571 | NA | NA | 13142.8571 | 12409.1818 | 21593.4 | NA | 1031.7391 | 11300 | Gen Bus
Fort St Vrain - Winter | 1 | 403 | 22 | 10576 | 12000 | 11300 | NA | A38401 | 451.36 | 230 | 21 | NA | NA | 3300 | 36142.8571 | NA | NA | 10.9524 | 1200 | 13142.8571 | 12409.1818 | 21593.4 | NA | 1133.242 | 965.6348 | 10576 | Generator | 10576 | 12000 | 11300 | NA | NA | 36142.8571 | NA | NA | 13142.8571 | 12409.1818 | 21593.4 | NA | 1031.7391 | 11300 | Gen Bus
Fort St Vrain - Summer | 2 | 206 | 18 | 6607 | 8000 | 8000 | 8000 | A63001 | 232 | 235.75 | 17.55 | NA | 15200 | 1250 | 16791.3105 | 8000 | 8000 | 13.433 | 1200 | 16119.6581 | 7632.2087 | 13537 | NA | 569 | 491.8467 | 6607 | Generator | 6607 | 8000 | 8000 | 8000 | 15200 | 16791.3105 | 8000 | 8000 | 16119.6581 | 7632.2087 | 13537 | NA | 568.1665 | 7632.2087 | GSU
Fort St Vrain - Winter | 2 | 206 | 18 | 6607 | 8000 | 8000 | 8000 | A63001 | 232 | 235.75 | 17.55 | NA | 15200 | 1250 | 16791.3105 | 8000 | 8000 | 13.433 | 1200 | 16119.6581 | 7632.2087 | 13537 | NA | 569 | 491.8467 | 6607 | Generator | 6607 | 8000 | 8000 | 8000 | 15200 | 16791.3105 | 8000 | 8000 | 16119.6581 | 7632.2087 | 13537 | NA | 568.1665 | 7632.2087 | GSU
Fort St Vrain - Summer | 3 | 206 | 18 | 6607 | 8000 | 8000 | 8000 | A66301 | 192.64 | 235.75 | 17.55 | NA | NA | 1200 | 16119.6581 | 8000 | 8000 | 13.433 | 800 | 10746.4387 | 6335 | 13537 | NA | 472 | 471.5981 | 6335 | GSU | 6607 | 8000 | 8000 | 8000 | NA | 16119.6581 | 8000 | 8000 | 10746.4387 | 6335 | 13537 | NA | 491.8467 | 6607 | Generator
Fort St Vrain - Winter | 3 | 206 | 18 | 6607 | 8000 | 8000 | 8000 | A66301 | 192.64 | 235.75 | 17.55 | NA | NA | 1200 | 16119.6581 | 8000 | 8000 | 13.433 | 800 | 10746.4387 | 6335 | 13537 | NA | 472 | 471.5981 | 6335 | GSU | 6607 | 8000 | 8000 | 8000 | NA | 16119.6581 | 8000 | 8000 | 10746.4387 | 6335 | 13537 | NA | 491.8467 | 6607 | Generator
Fort St Vrain - Summer | 4 | 206 | 18 | 6706 | 8000 | 7000 | 8000 | A69801 | 206 | 235.75 | 17.55 | NA | NA | 550 | 7388.1766 | 8000 | 8000 | 13.433 | 1200 | 16119.6581 | 6776.875 | 13537 | NA | 505 | 499.2165 | 6706 | Generator | 6706 | 8000 | 7000 | 8000 | NA | 7388.1766 | 8000 | 8000 | 16119.6581 | 6776.875 | 13537 | NA | 504.4927 | 6776.875 | GSU
Fort St Vrain - Winter | 4 | 206 | 18 | 6706 | 8000 | 7000 | 8000 | A69801 | 206 | 235.75 | 17.55 | NA | NA | 550 | 7388.1766 | 8000 | 8000 | 13.433 | 1200 | 16119.6581 | 6776.875 | 13537 | NA | 505 | 499.2165 | 6706 | Generator | 6706 | 8000 | 7000 | 8000 | NA | 7388.1766 | 8000 | 8000 | 16119.6581 | 6776.875 | 13537 | NA | 504.4927 | 6776.875 | GSU
Fort St Vrain - Summer | 5 | 165 | 18 | 5292 | 8000 | 7000 | 8000 |  | 230 | 241.5 | 18 | NA | 7380 | 800 | 10733.3333 | 8000 | 8000 | 13.4167 | 800 | 10733.3333 | 7377.2534 | 11850 | NA | 550 | 394.4348 | 5292 | Generator | 5292 | 8000 | 7000 | 8000 | 7380 | 10733.3333 | 8000 | 8000 | 10733.3333 | 7377.2534 | 11850 | NA | 521.7391 | 7000 | Gen Bus
Fort St Vrain - Winter | 5 | 165 | 18 | 5292 | 8000 | 7000 | 8000 |  | 230 | 241.5 | 18 | NA | 7380 | 800 | 10733.3333 | 8000 | 8000 | 13.4167 | 800 | 10733.3333 | 7377.2534 | 11850 | NA | 550 | 394.4348 | 5292 | Generator | 5292 | 8000 | 7000 | 8000 | 7380 | 10733.3333 | 8000 | 8000 | 10733.3333 | 7377.2534 | 11850 | NA | 521.7391 | 7000 | Gen Bus
Fort St Vrain - Summer | 6 | 165 | 18 | 5292 | 8000 | 7000 | 8000 |  | 200 | 235.75 | 17.55 | NA | 8000 | 600 | 8059.8291 | 8000 | 8000 | 13.433 | 800 | 10746.4387 | 6580 | 11859 | NA | 490 | 393.9538 | 5292 | Generator | 5292 | 8000 | 7000 | 8000 | 8000 | 8059.8291 | 8000 | 8000 | 10746.4387 | 6580 | 11859 | NA | 489.8367 | 6580 | GSU
Fort St Vrain - Winter | 6 | 165 | 18 | 5292 | 8000 | 7000 | 8000 |  | 200 | 235.75 | 17.55 | NA | 8000 | 600 | 8059.8291 | 8000 | 8000 | 13.433 | 800 | 10746.4387 | 6580 | 11859 | NA | 490 | 393.9538 | 5292 | Generator | 5292 | 8000 | 7000 | 8000 | 8000 | 8059.8291 | 8000 | 8000 | 10746.4387 | 6580 | 11859 | NA | 489.8367 | 6580 | GSU
Ft Lupton - Summer | 1 | 44.65 | 13.8 | 1868.021 | 4000 | 3850 | 3850 | A45001 | 123.2 | 118.25 | 13.2 | NA | NA | NA | NA | 3000 | 4000 | 8.9583 | 867 | 7766.875 | 5388.6025 | 10465 | NA | NA | 208.5233 | 1868.021 | Generator | 1868.021 | 4000 | 3850 | 3850 | NA | NA | 3000 | 4000 | 7766.875 | 5388.6025 | 10465 | NA | 334.8837 | 3000 | Gen Breaker
Ft Lupton - Winter | 1 | 69.4556 | 13.8 | 2905.8104 | 4000 | 4632 | 4632 | A45001 | 123.2 | 118.25 | 13.2 | NA | NA | NA | NA | 3000 | 4000 | 8.9583 | 960 | 8600 | 5388.6025 | 10465 | NA | NA | 324.3695 | 2905.8104 | Generator | 2905.8104 | 4000 | 4632 | 4632 | NA | NA | 3000 | 4000 | 8600 | 5388.6025 | 10465 | NA | 334.8837 | 3000 | Gen Breaker
Ft Lupton - Summer | 2 | 44.65 | 13.8 | 1868.021 | 4000 | 3850 | 3850 | A45001 | 123.2 | 118.25 | 13.2 | NA | NA | NA | NA | 3000 | 4000 | 8.9583 | 867 | 7766.875 | 5388.6025 | 10465 | NA | NA | 208.5233 | 1868.021 | Generator | 1868.021 | 4000 | 3850 | 3850 | NA | NA | 3000 | 4000 | 7766.875 | 5388.6025 | 10465 | NA | 334.8837 | 3000 | Gen Breaker
Ft Lupton - Winter | 2 | 69.4556 | 13.8 | 2905.8104 | 4000 | 4632 | 4632 | A45001 | 123.2 | 118.25 | 13.2 | NA | NA | NA | NA | 3000 | 4000 | 8.9583 | 960 | 8600 | 5388.6025 | 10465 | NA | NA | 324.3695 | 2905.8104 | Generator | 2905.8104 | 4000 | 4632 | 4632 | NA | NA | 3000 | 4000 | 8600 | 5388.6025 | 10465 | NA | 334.8837 | 3000 | Gen Breaker
Ft Lupton GSU Summer | C | 89.3 | 13.8 | 3736.042 | 8000 | 4626 | 7700 | A45001 | 123.2 | 118.25 | 13.2 | NA | NA | NA | NA | 6000 | 8000 | 8.9583 | 867 | 7766.875 | 5388.6025 | 10465 | NA | 601.5184 | 417.0465 | 3736.042 | Generator | 3736.042 | 8000 | 4626 | 7700 | NA | NA | 6000 | 8000 | 7766.875 | 5388.6025 | 10465 | NA | 516.3907 | 4626 | LS GSU Bus
Ft Lupton GSU Winter | C | 138.9111 | 13.8 | 5811.6208 | 8000 | 5577 | 9264 | A45001 | 123.2 | 118.25 | 13.2 | NA | NA | NA | NA | 6000 | 8000 | 8.9583 | 960 | 8600 | 5388.6025 | 10465 | NA | 601.5184 | 601.5184 | 5388.6025 | Generator | 5811.6208 | 8000 | 5577 | 9264 | NA | NA | 6000 | 8000 | 8600 | 5388.6025 | 10465 | NA | 622.5488 | 5577 | GSU
Hayden | 1 | 202.656 | 18 | 6500 | 7000 | 6500 | NA | A62101 | 235 | 224.25 | 17.1 | NA | NA | 1200 | 15736.8421 | NA | NA | 13.114 | 900 | 11802.6316 | 7934.3458 | 13718 | NA | 605 | 495.6522 | 6500 | Generator * | 6500 | 7000 | 6500 | NA | NA | 15736.8421 | NA | NA | 11802.6316 | 7934.3458 | 13718 | NA | 495.6522 | 6500 | Gen Bus *
Hayden | 2 | 306 | 22 | 8030 | 10000 | 9000 | NA | A59701 | 306 | 235.75 | 22 | NA | NA | 1000 | 10715.9091 | NA | NA | 10.7159 | 800 | 8572.7273 | 8030.4 | 16543 | NA | 749.4 | 749.3531 | 8030 | Generator * | 8030 | 10000 | 9000 | NA | NA | 10715.9091 | NA | NA | 8572.7273 | 8030.4 | 16543 | NA | 749.3905 | 8030.4 | GSU *
ManChief - Summer | 11 | 150 | 16 | 5413 | 8000 | 8000 | NA |  | 200 | 224.25 | 15.2 | NA | 8000 | 600 | 8851.9737 | NA | NA | 14.7533 | 500 | 7376.6447 | 7596.7141 | 6400 | NA | 515 | 366.9012 | 5413 | Generator | 5413 | 8000 | 8000 | NA | 8000 | 8851.9737 | NA | NA | 7376.6447 | 7596.7141 | 6400 | NA | 433.8016 | 6400 | Relay Overcurrent
ManChief - Winter | 11 | 150 | 16 | 5413 | 8000 | 8000 | NA |  | 200 | 224.25 | 15.2 | NA | 8000 | 600 | 8851.9737 | NA | NA | 14.7533 | 500 | 7376.6447 | 7596.7141 | 6400 | NA | 515 | 366.9012 | 5413 | Generator | 5413 | 8000 | 8000 | NA | 8000 | 8851.9737 | NA | NA | 7376.6447 | 7596.7141 | 6400 | NA | 433.8016 | 6400 | Relay Overcurrent
ManChief - Summer | 12 | 150 | 16 | 5413 | 8000 | 8000 | NA |  | 200 | 224.25 | 15.2 | NA | 8000 | 600 | 8851.9737 | NA | NA | 14.7533 | 500 | 7376.6447 | 7596.7141 | 6400 | NA | 515 | 366.9012 | 5413 | Generator | 5413 | 8000 | 8000 | NA | 8000 | 8851.9737 | NA | NA | 7376.6447 | 7596.7141 | 6400 | NA | 433.8016 | 6400 | Relay Overcurrent
ManChief - Winter | 12 | 150 | 16 | 5413 | 8000 | 8000 | NA |  | 200 | 224.25 | 15.2 | NA | 8000 | 600 | 8851.9737 | NA | NA | 14.7533 | 500 | 7376.6447 | 7596.7141 | 6400 | NA | 515 | 366.9012 | 5413 | Generator | 5413 | 8000 | 8000 | NA | 8000 | 8851.9737 | NA | NA | 7376.6447 | 7596.7141 | 6400 | NA | 433.8016 | 6400 | Relay Overcurrent
ManChief Common - Summer | C | 300 | 16 | 10826 | 16000 | 16000 | NA |  | 400 | 224.25 | 15.2 | NA | 16000 | 1200 | 17703.9474 | NA | NA | 14.7533 | 1200 | 17703.9474 | 15193.4281 | 12800 | NA | NA | 733.8025 | 10826 | Generators | 10826 | 16000 | 16000 | NA | 16000 | 17703.9474 | NA | NA | 17703.9474 | 15193.4281 | 12800 | NA | 867.6031 | 12800 | Relay Overcurrent
ManChief Common - Winter | C | 300 | 16 | 10826 | 16000 | 16000 | NA |  | 400 | 224.25 | 15.2 | NA | 16000 | 1200 | 17703.9474 | NA | NA | 14.7533 | 1200 | 17703.9474 | 15193.4281 | 12800 | NA | NA | 733.8025 | 10826 | Generators | 10826 | 16000 | 16000 | NA | 16000 | 17703.9474 | NA | NA | 17703.9474 | 15193.4281 | 12800 | NA | 867.6031 | 12800 | Relay Overcurrent
Pawnee | 1 | 613.7 | 22 | 16105 | 22000 | 18000 | NA | A49001 A49101 | 728 | 230 | 21 | NA | NA | NA | NA | NA | NA | 10.9524 | 1578 | 17282.8571 | 20014.8093 | 33901 | NA | 1827.4391 | 1470.4565 | 16105 | Generator | 16105 | 22000 | 18000 | NA | NA | NA | NA | NA | 17282.8571 | 20014.8093 | 33901 | NA | 1578 | 17282.8571 | Yard Conductor
RMEC - Summer | 1 | 206 | 15 | 7929 | 12000 | 9000 | 10500 |  | 250 | 237.8 | 15 | NA | 12000 | 1200 | 19024 | 10500 | 12000 | 15.8533 | 1240 | 19658.1333 | 9620 | 15977 | NA | 606 | 500.1472 | 7929 | Generator | 7929 | 12000 | 9000 | 10500 | 12000 | 19024 | 10500 | 12000 | 19658.1333 | 9620 | 15977 | NA | 567.704 | 9000 | Gen Bus
RMEC - Winter | 1 | 206 | 15 | 7929 | 12000 | 9000 | 10500 |  | 250 | 237.8 | 15 | NA | 12000 | 1200 | 19024 | 10500 | 12000 | 15.8533 | 1484 | 23526.3467 | 9620 | 15977 | NA | 606 | 500.1472 | 7929 | Generator | 7929 | 12000 | 9000 | 10500 | 12000 | 19024 | 10500 | 12000 | 23526.3467 | 9620 | 15977 | NA | 567.704 | 9000 | Gen Bus
RMEC - Summer | 2 | 206 | 15 | 7929 | 12000 | 9000 | 10500 |  | 250 | 237.8 | 15 | NA | 12000 | 1200 | 19024 | 10500 | 12000 | 15.8533 | 1240 | 19658.1333 | 9620 | 15977 | NA | 606 | 500.1472 | 7929 | Generator | 7929 | 12000 | 9000 | 10500 | 12000 | 19024 | 10500 | 12000 | 19658.1333 | 9620 | 15977 | NA | 567.704 | 9000 | Gen Bus
RMEC - Winter | 2 | 206 | 15 | 7929 | 12000 | 9000 | 10500 |  | 250 | 237.8 | 15 | NA | 12000 | 1200 | 19024 | 10500 | 12000 | 15.8533 | 1484 | 23526.3467 | 9620 | 15977 | NA | 606 | 500.1472 | 7929 | Generator | 7929 | 12000 | 9000 | 10500 | 12000 | 19024 | 10500 | 12000 | 23526.3467 | 9620 | 15977 | NA | 567.704 | 9000 | Gen Bus
RMEC - Summer | 3 | 394 | 23 | 9890 | 12000 | 10000 | NA |  | 430 | 243.6 | 23 | NA | 12000 | 1125 | 11915.2174 | NA | NA | 10.5913 | 1240 | 13133.2174 | 10794 | 20409 | NA | 1019 | 933.7849 | 9890 | Generator | 9890 | 12000 | 10000 | NA | 12000 | 11915.2174 | NA | NA | 13133.2174 | 10794 | 20409 | NA | 944.1708 | 10000 | Gen Bus
RMEC - Winter | 3 | 394 | 23 | 9890 | 12000 | 10000 | NA |  | 430 | 243.6 | 23 | NA | 12000 | 1125 | 11915.2174 | NA | NA | 10.5913 | 1484 | 15717.4957 | 10794 | 20409 | NA | 1019 | 933.7849 | 9890 | Generator | 9890 | 12000 | 10000 | NA | 12000 | 11915.2174 | NA | NA | 15717.4957 | 10794 | 20409 | NA | 944.1708 | 10000 | Gen Bus
Valmont -Summer | 6 | 49.41 | 13.8 | 2067.165 | 4000 | 3000 | 3000 | A45701 | 67.2 | 115 | 13.2 | NA | 3000 | 600 | 5227.2727 | 3000 | 4000 | 8.7121 | 300 | 2613.6364 | 2939.2377 | 5922.5 | NA | 337 | 237.2746 | 2067.165 | Generator | 2067.165 | 4000 | 3000 | 3000 | 3000 | 5227.2727 | 3000 | 4000 | 2613.6364 | 2939.2377 | 5922.5 | NA | 300 | 2613.6364 | Yard Bkr CT
Valmont - Winter | 6 | 74.725 | 13.8 | 3126.268 | 4000 | 3000 | 3000 | A45701 | 67.2 | 115 | 13.2 | NA | 3000 | 600 | 5227.2727 | 3000 | 4000 | 8.7121 | 300 | 2613.6364 | 2939.2377 | 5922.5 | NA | 337 | 300 | 2613.6364 | Yard Bkr CT | 3126.268 | 4000 | 3000 | 3000 | 3000 | 5227.2727 | 3000 | 4000 | 2613.6364 | 2939.2377 | 5922.5 | NA | 337.3734 | 2939.2377 | GSU
Valmont-Summer | 7 | 51.4688 | 13.8 | 2153.2969 | 3000 | 2717 | NA |  | 50 | 115 | 13.2 | NA | 3000 | 1200 | 10454.5455 | 3000 | 3000 | 8.7121 | 600 | 5227.2727 | 2186.9328 | 5488.6364 | NA | NA | 247.161 | 2153.2969 | Generator | 2153.2969 | 3000 | 2717 | NA | 3000 | 10454.5455 | 3000 | 3000 | 5227.2727 | 2186.9328 | 5488.6364 | NA | 251.0219 | 2186.9328 | GSU
Valmont-Winter | 7 | 78.0292 | 13.8 | 3264.5044 | 3000 | 3237 | NA |  | 50 | 115 | 13.2 | NA | 3000 | 1200 | 10454.5455 | 3000 | 3000 | 8.7121 | 600 | 5227.2727 | 2186.9328 | 5488.6364 | NA | NA | 251.0219 | 2186.9328 | GSU | 3264.5044 | 3000 | 3237 | NA | 3000 | 10454.5455 | 3000 | 3000 | 5227.2727 | 2186.9328 | 5488.6364 | NA | 344.3478 | 3000 | Gen CT Amps*
Valmont-Summer | 8 | 51.4688 | 13.8 | 2153.2969 | 3000 | 2717 | NA |  | 50 | 115 | 13.2 | NA | 3000 | 1200 | 10454.5455 | 3000 | 3000 | 8.7121 | 600 | 5227.2727 | 2186.9328 | 5488.6364 | NA | NA | 247.161 | 2153.2969 | Generator | 2153.2969 | 3000 | 2717 | NA | 3000 | 10454.5455 | 3000 | 3000 | 5227.2727 | 2186.9328 | 5488.6364 | NA | 251.0219 | 2186.9328 | GSU
Valmont-Winter | 8 | 78.0292 | 13.8 | 3264.5044 | 3000 | 3237 | NA |  | 50 | 115 | 13.2 | NA | 3000 | 1200 | 10454.5455 | 3000 | 3000 | 8.7121 | 600 | 5227.2727 | 2186.9328 | 5488.6364 | NA | NA | 251.0219 | 2186.9328 | GSU | 3264.5044 | 3000 | 3237 | NA | 3000 | 10454.5455 | 3000 | 3000 | 5227.2727 | 2186.9328 | 5488.6364 | NA | 344.3478 | 3000 | Gen CT Amps*
Valmont 7&8 GSU-S | C | 102.9375 | 13.8 | 4306.5937 | NA | NA | NA |  | 100 | 115 | 13.2 | NA | NA | 1199 | 10445.8333 | NA | NA | 8.7121 | 600 | 5227.2727 | 4373.8657 | 5488.6364 | NA | 502 | 494.3221 | 4306.5937 | Generators | 4306.5937 | NA | NA | NA | NA | 10445.8333 | NA | NA | 5227.2727 | 4373.8657 | 5488.6364 | NA | 502.0437 | 4373.8657 | GSU
Valmont 7&8 GSU-W | C | 156.0583 | 13.8 | 6529.0088 | NA | NA | NA |  | 100 | 115 | 13.2 | NA | NA | 1200 | 10454.5455 | NA | NA | 8.7121 | 600 | 5227.2727 | 4373.8657 | 5488.6364 | NA | 502 | 502.0437 | 4373.8657 | GSU | 6529.0088 | NA | NA | NA | NA | 10454.5455 | NA | NA | 5227.2727 | 4373.8657 | 5488.6364 | NA | 600 | 5227.2727 | Metering CT
[21 empty] | Date | Revision | Change
[21 empty] | 7/9/2025 | 7-25 | Reversion to date format
[21 empty] | 9/17/2024 | 29.3 | Change of gang switch at Manchief
Methodology | Refer to EPR 5.200 and EPR 5.220P01 | [19 empty] | 7/20/2024 | 29.2 | Updated Cherokee 2 MVA rating to match Synchronous condenser operation
Generator | Manufacturer nameplate value at rated coolant conditions, air cooled units use 104F for summer temperatures | [19 empty] | 7/20/2023 | 29.1 | Column added for GSU High Side ampacity nameplate data LS GSU TR Amps calculation constant changed to "SQRT(3)" instead of approximation, changed ratings highlighted Where nameplate ratings have been available for LS GSU TR Amps they have been provided. Set ratings for Valmont 6, Fort Lupton, and Alamosa to 104F summer temperature ratings. Fort lupton winter rating changed from peak capability to base Added ratings for Alamosa and Fort Lupton generator bus based on construction drawings and material. Set Rocky Mountain CT generator ampacity to manufacturer given ratings
Winter ratings for air cooled CTs taken at 0F
Isophase Bus | Manufacturer nameplate value if available, else used generator current rating.
Transformer | Manufacturer nameplate value at 65° C rise or next highest rating given
Generator ratings combined to rate shared GSU transformers or other shared equipment
Limiting I Hi Side of GSU to Transmission | Value is a combination of ES ratings and Subs Engineering Ratings as determined from rating demarcation agreement
Notes
Gray highlighted values are used to determine the limiting component. | [20 empty] | 4/4/2023 | 29.0 | Added summer and winter ratings for Valmont 7&8 Corrected Valmont 7&8 ratings for altitude
Emergency ratings have not been supplied by Equipment Manufactures therefore, only normal ratings are used
* Indicates multiple equipment at this rating.
Diesel generators are included if they are part of a black start sequence | [20 empty] | 2/21/2023 | 28.3 | Comanche 1 has been retired and will not appear on later versions of this document. Retained here to indicate change. Updated Cabin creek to reflect isophase upgrade Relay Upgrade at Manchief changed trip set points
[21 empty] | 2022-08-14 | 28.2 | Removed Cherokee 4 derate
[21 empty] | 2022-07-22 | 28.1 | Temporary Cherokee 4 derate
[21 empty] | 2022-05-02 | 28 | Added ManChief Units 11 and 12
[21 empty] | 2021-12-07 | 27 | Revised facility ratings to reflect updated Foreign Utility Connections.xls spreadsheet.
[21 empty] | 2021-09-30 | 26 | Cherokee, Ft Lupton, Valmont, Comanche, Pawnee GSU HS ratings updated per Subs Engineering data (Foreign Utility Connections.xls spreadsheet)
[21 empty] | 2021-08-24 | 25.2 | Updated Blue Spruce breaker ratings. No change in limiting equipment ratings.
[21 empty] | 2020-05-29 | 25.1 | Removed "Future" tag from Valmont units 7, 8, and common.
[21 empty] | 2020-04-06 | 25 | Added Valmont units 7 and 8 to the spreadsheet. Updated CCH Unit A equipment changes.
[21 empty] | 2019-01-17 | 24.1 | Updated Cherokee Synchronous Condenser (unit 2) GSU tap postion [Note: corrected date stamp on 9/13/2019 to 1/17/2019]
[21 empty] | 2018-09-28 | 24 | Added a combined unit at BSP to standardize approach with Subs Engineering. Corrected typo for BSP1 winter rating 4" bus. Updated FSV5 and FSV6 relay trip info. Updated Comanche 3 value provided by Subs Engineering, Limiting and Next Most Limiting Elements changed.
[21 empty] | 2018-06-07 | 23 | Removed Valmont 5 as unit was retired. Updated FSV5 GSU ratio to correspond to tap change. Corrected typo in revision block for Rev 22 - Date corrected to 9/22/2017
[21 empty] | 2017-09-22 | 22 | Updated to reflect new relay settings at Alamosa, VAL 6, CHR 5,6 &7, COM 1,2, &3, FSV 1-4, FLP 1&2, PAW and RMEC. Corrected rounding error at FSV1. Corrected CT ratios at CHR7, FSV2, FSV5, HAY1-2, and RMEC3. Added a combined unit at FLP to standardize methodology with other regions.
[21 empty] | 2016-09-13 | 21.1 | Updated to reflect new values provided by Subs Engineering. Removed orange and blue highlights. No limiting elements changed.
[21 empty] | 2016-07-14 | 21 | Corrected Hayden 2 GSU low side voltage. Revised Comanche 1&2 transformer ratios due to tap change. Modified to correspond to demarcation with Subs and added CH 5, 6 & 7 values
[21 empty] | 2015-08-28 | 20 | Revised "Limiting I from Hi Side of GSU to Yard" data for Cherokee 5, 6 & 7. Removed Cherokee 3, unit retired.
[21 empty] | 2015-06-18 | 19 | Added Cherokee 5, 6 and 7. Updated relay trip amps for units.
[21 empty] | 2014-08-27 | 18 | Removed Arapahoe 3 & 4 as units were retired. Updated column T with new info from Transmission.
[21 empty] | 2013-10-18 | 17 | Corrected values for CO3 HS GSU CT, AR3 LS GSU CT and AR3 Gen Bus. At the request of Substation Eng Design added columns for GSU Subs ID, Nominal GSU HS kV value and HS current values for limiting equipment
[21 empty] | 2013-07-29 | 16 | Added Values for Gen Disonnects for FSV 2-6, RMEC 1 & 2, and Valmont 6
[21 empty] | 2012-10-01 | 15 | Formatted sheet to reflect changes to EPR 5.220_P01.
[21 empty] | 2012-05-03 | 14.1 | Changed designation for Cherokee 2 to SC
[21 empty] | 2012-05-01 | 14 | Added CH2 Synchronous Condenser. Removed CH1, unit decommisioned
[21 empty] | 2012-01-05 | 13 | Updated data to correlate with the 2012 Capacity Ratings issued by Performance Testing. Removed Cherokee 2 as it is retired.
[21 empty] | 2011-11-29 | 12 | Updated column R with new information from Transmission
[21 empty] | 2011-03-29 | 11.2 | Rearranged columns to clarify limiting electrical equipment. Highlighted the column and added note describing the highlight. Added note that tested MVAR comes from D curve
[21 empty] | 2011-03-14 | 11.1 | Updated column R with new information from Transmission
[21 empty] | 2011-01-24 | 11 | Added columns for Gen Disconnect and GSU CTs. Rplaced components from high side of GSU w/ info from Transmission. Removed Craig units from sheet. Added RMEC and Blue Spruce units. Correlated with 2011 Generation Data
[21 empty] | 2010-10-28 | 10 | Updated data sheet to correlate with the 2010 Generation Data issued by Performance Testing
[21 empty] | 2010-09-21 | 9 | Added Series/Shunt Device column and note on emergency ratings
[21 empty] | 2010-03-05 | 8 | Added ampacity rating for GSU-Switchyard condutors
[21 empty] | 2010-02-26 | 7 | Removed Zuni 1, unit retired. Added low side and high side generator breakers values. Note, these values did not change results. Corrected Gen CT Amps for CC A&B, CH 2, FL 1&2 and VA 5&6.
[21 empty] | 2009-11-09 | 6 | Updated data sheet to correlate with the 2009 Generation Data issued by Performance Testing
[21 empty] | 2009-06-08 | 5 | Added FSV 5 & 6. Modified CT summer and winter ratings.
[21 empty] | 2008-10-31 | 4 | Corrected Gen MVA ratings to max H2 pressure
[21 empty] | 2008-06-22 | 3 | Updated Net MW from test data for AR 3 &4, HA 2 & ZU 1
[21 empty] | 2007-06-21 | 2 | Added revision block, added winter and summer ratings to CTs and added Craig units.
[21 empty] | 2007-06-04 | 1 | Origional Issue
Note on C6: Author: Generator Data sheet, generator output as a function of inlet air temperature for 104F corrected for altitude. 7546' (.875)
Note on D6: Author: Info from Generator Data sheet, corrected for altitude.
Note on E6: Author: From Summer capability corrected for altitude. 104F corrected for altitude. 7546' (.875)
Note on F6: Author: See K14-76T-E5091
Note on G6: Author: Drawing 20-6.23 sh1 Unit Bus bars are 3" AL with 2X500Kcmil cable (insulated) connections. The connections will be the most limiting element. Value calculated from PLS CADD Model, absorbtivity and Emissivity of .97 used for black plastic insulation. reference file Alamosa U2 GSU Low Side Connection. Although insulated cable is used, the NEC allowable ampacity does not apply in this application)
Note on J6: Author: See nameplate picture
Note on K6: Author: See nameplate picture
Note on L6: Author: See nameplate picture
Note on N6: Author: See nameplate picture
Note on O6: Author: See nameplate picture KBS - Tapped at 400:5 (dwg 20-8.1 sh1)
Note on Q6: Author: See K14-76T-E5091
Note on R6: Author: See K14-76T-E5091
Note on S6: Author: Tap 3
Note on T6: Author: Value from Subs Eng FAC-008-3 Spreadsheet. Limiting Element: 795 ACSR Conductor
Note on V6: Author: Nameplate rating is at 25MVA instead of the 28MVA for 65 degree rise, so a calculation is used
Note on W6: Brady Nunn: Verified from relay settings - 21 Zone 2 is set to PRC-025 criteria. HS 51 pickup value provided
Note on Y6: Author: Calculated, nameplate has lower transformer rating printed
Note on AC6: Author: Info from Generator Data sheet, corrected for altitude.
Note on AD6: Author: See K14-76T-E5091
Note on C7: Author: Generator Data sheet, generator output as a function of inlet air temperature for 0F corrected for altitude. 7546' (.875) Winter rating taken from max value on D curve.
Note on D7: Author: Info from Generator Data sheet, corrected for altitude.
Note on E7: Author: Generator Data sheet, 0F corrected for altitude. 7546' (.875)
Note on F7: Author: See K14-76T-E5091
Note on G7: Author: Drawing 20-6.23 sh1 Unit Bus bars are 3" AL with 2X500Kcmil cable (insulated) connections. The connections will be the most limiting element. Value calculated from PLS CADD Model, absorbtivity and Emissivity of .97 used for black plastic insulation. reference file Alamosa U2 GSU Low Side Connection. Although insulated cable is used, the NEC allowable ampacity does not apply in this application)
Note on J7: Author: See nameplate picture
Note on K7: Author: See nameplate picture
Note on L7: Author: See nameplate picture
Note on N7: Author: See nameplate picture
Note on O7: Author: See nameplate picture KBS - Tapped at 400:5
Note on Q7: Author: See K14-76T-E5091
Note on R7: Author: See K14-76T-E5091
Note on S7: Author: Tap 3
Note on T7: Author: Value from Subs Eng FAC-008-3 Spreadsheet. Limiting Element: 795 ACSR Conductor
Note on V7: Author: Nameplate rating is at 25MVA so a calculation is used
Note on W7: Brady Nunn: Verified from relay settings - 21 Zone 2 is set to PRC-025 criteria. HS 51 pickup value provided
Note on Y7: Author: Calculated, nameplate has lower transformer rating printed
Note on AC7: Author: Info from Generator Data sheet, corrected for altitude.
Note on AD7: Author: See K14-76T-E5091
Note on C8: Author: See BS 1 Gen Nameplate
Note on D8: Author: See BS 1 Gen Nameplate
Note on E8: Author: See BS 1 Gen Nameplate
Note on F8: Author: See 207D1578
Note on G8: Author: See E150
Note on J8: Author: See nameplate picture
Note on L8: Author: See nameplate picture
Note on N8: Author: See nameplate picture
Note on O8: Author: See nameplate picture
Note on S8: Author: Tap 3
Note on T8: Author: See sheet 2
Note on V8: Author: GSU Nameplate
Note on W8: Author: 50 Relay setting set at 13A on 230kV 1200:5 CT = 3120A Primary =40872A Secondary. 51 function is set to 4.5 Amps on 230kV 1200:5 = 1080A Primary = 14148A Secondary. 21 function has been evaluated to PRC-025.
Note on Y8: Author: GSU Nameplate
Note on AC8: Author: Info from Generator Data sheet, corrected for altitude.
Note on AD8: Author: See K14-76T-E5091
Note on C9: Author: See BS 1 Gen Nameplate
Note on D9: Author: See BS 1 Gen Nameplate
Note on E9: Author: See BS 1 Gen Nameplate
Note on F9: Author: See 207D1578
Note on G9: Author: See E150
Note on J9: Author: See nameplate picture
Note on L9: Author: See nameplate picture
Note on N9: Author: See nameplate picture
Note on O9: Author: See nameplate picture
Note on S9: Author: Tap 3
Note on T9: Author: See sheet 2
Note on V9: Author: GSU Nameplate
Note on W9: Author: 50 Relay setting set at 13A on 230kV 1200:5 CT = 3120A Primary =40872A Secondary. 51 function is set to 4.5 Amps on 230kV 1200:5 = 1080A Primary = 14148A Secondary. 21 function has been evaluated to PRC-025.
Note on Y9: Author: GSU Nameplate
Note on AC9: Author: Info from Generator Data sheet, corrected for altitude.
Note on AD9: Author: See K14-76T-E5091
Note on C10: Author: See BS 2 Gen namplate
Note on D10: Author: See BS 2 Gen namplate
Note on E10: Author: See BS 2 Gen namplate
Note on F10: Author: See 207D1578
Note on G10: Author: See E150
Note on J10: Author: See nameplate picture
Note on L10: Author: See nameplate picture
Note on N10: Author: See nameplate picture
Note on O10: Author: See nameplate picture
Note on S10: Author: Tap 3
Note on T10: Author: See sheet 2
Note on V10: Author: GSU Nameplate
Note on W10: Author: 50 Relay setting set at 13A on 230kV 1200:5 CT = 3120A Primary =40872A Secondary. 51 function is set to 4.5 Amps on 230kV 1200:5 = 1080A Primary = 14148A Secondary. 21 function has been evaluated to PRC-025.
Note on Y10: Author: GSU Nameplate
Note on AC10: Author: Info from Generator Data sheet, corrected for altitude.
Note on AD10: Author: See K14-76T-E5091
Note on C11: Author: See BS 2 Gen namplate
Note on D11: Author: See BS 2 Gen namplate
Note on E11: Author: See BS 2 Gen namplate
Note on F11: Author: See 207D1578
Note on G11: Author: See E150
Note on J11: Author: See nameplate picture
Note on L11: Author: See nameplate picture
Note on N11: Author: See nameplate picture
Note on O11: Author: See nameplate picture
Note on S11: Author: Tap 3
Note on T11: Author: See sheet 2
Note on V11: Author: GSU Nameplate
Note on W11: Author: 50 Relay setting set at 13A on 230kV 1200:5 CT = 3120A Primary =40872A Secondary. 51 function is set to 4.5 Amps on 230kV 1200:5 = 1080A Primary = 14148A Secondary. 21 function has been evaluated to PRC-025.
Note on Y11: Author: GSU Nameplate
Note on AC11: Author: Info from Generator Data sheet, corrected for altitude.
Note on AD11: Author: See K14-76T-E5091
Note on B12: Author: Combined rating for shared conductors to Spruce Sub
Note on C12: Author: Combined rating of both ratings (summer)
Note on E12: Author: Combined rating of both generators (summer)
Note on J12: Author: Combined rating of both GSUs
Note on T12: Author: See sheet 2 Metering Element
Note on B13: Author: Combined rating for shared conductors to Spruce Sub
Note on C13: Author: Combined rating of both ratings (winter)
Note on E13: Author: Combined rating of both generators (winter)
Note on J13: Author: Combined rating of both GSUs
Note on T13: Author: See sheet 2 Metering Element
Note on C14: Author: 10930 GE-1A, Generator Electrical and Physical Data sheet, and nameplate picture
Note on D14: Author: 1-line, 10930 GE-1A and nameplate picture
Note on E14: Author: See name plate picture and Generator Electrical and Physical Data sheet HNAEM 4.02.1103 FR R10
Note on F14: Author: 1-line, 10930 GE-1A SH2
Note on G14: Author: 10930 GE-1A sh1
Note on H14: Author: Reversing switch, see GMZ60115R4 and GMZ60749R1 only disconnects b and c phase see 10930 ESA-7F SH5
Note on J14: Author: 1-line, 10930 GE-1A and nameplate picture
Note on K14: Author: Tap 3
Note on L14: Author: 1-line, 10930 GE-1A and nameplate picture
Note on N14: Author: See 10930 GE-1F
Note on S14: Author: Tap 1
Note on T14: Author: Value from Subs Eng FAC-008-3 Spreadsheet. Limiting Element: Secondary Element
Note on V14: Author: Matches Nameplate value of 5312*sqrt(3) to reflect effect on generator current
Note on W14: Brady Nunn: 50 Function not used 51 Function not used 21 Function evaluated to PRC-025
Note on Y14: Author: Nameplate
Note on AC14: Author: Info from Generator Data sheet, corrected for altitude.
Note on AD14: Author: See K14-76T-E5091
Note on C15: Author: 1-line, 10930 GE-1A and nameplate picture
Note on D15: Author: 1-line, 10930 GE-1A and nameplate picture
Note on E15: Author: See name plate picture and Generator Electrical and Physical Data sheet HNAEM 4.02.1103 FR R10
Note on F15: Author: 3-line, 10930 GE-1F sh2
Note on G15: Author: See 712E0067
Note on H15: Author: Reversing switch, see GMZ60115R4 and GMZ60749R1 only disconnects b and c phase see 10930
Note on J15: Author: 1-line, 10930 GE-1A and nameplate picture
Note on K15: Author: Tap 3
Note on L15: Author: 1-line, 10930 GE-1A and nameplate picture
Note on N15: Author: See 10930 GE-1F SH2
Note on S15: Author: Tap 1
Note on T15: Author: Value from Subs Eng FAC-008-3 Spreadsheet. Limiting Element: Secondary Element
Note on V15: Author: Matches Nameplate value of 5312*sqrt(3) to reflect effect on generator current
Note on W15: Author: 50 Function not available 51 Function Not Available 21 Function not evaluated to PRC-025 67 Function not evaluated to PRC-025
Note on Y15: Author: Nameplate
Note on AC15: Author: Info from Generator Data sheet, corrected for altitude.
Note on AD15: Author: See K14-76T-E5091
Note on C16: Author: See PRC-019 curve for limits and "CHR2 Capability Curve2" for MVAR and MW maximums
Note on D16: Author: 1-line, G130723 and nameplate picture
Note on E16: Author: From Summer capability corrected for altitude. 104F corrected for altitude. 7546' (.875)
Note on F16: Author: 1-line, G130723
Note on G16: Author: See summary of Equipment document CH2 isophase
Note on J16: Author: See name plate picture
Note on K16: Author: Tap D sqrt(3)*64740V
Note on L16: Author: See name plate picture
Note on N16: Author: See name plate picture note, rating 4000A with TR=2
Note on S16: Author: Tap B
Note on T16: Author: Value from Subs Eng FAC-008-3 Spreadsheet. Limiting Element: 715.5 Al Jumper
Note on V16: Author: Nameplate rating at 3178, multiply by sqrt(3) for generator amps due to 3 separate transformers.
Note on W16: Author: 50 Relay setting set above 51 function 51 function is set to 4.32 Amps on 115kV 1200:5 = 1037A Primary = 8265A Secondary. 21 function has been evaluated to PRC-025.
Note on Y16: Author: From nameplate.
Note on AC16: Author: Info from Generator Data sheet, corrected for altitude.
Note on AD16: Author: See K14-76T-E5091
Note on C17: Author: 1-line, L-21500 E2-1 and nameplate picture
Note on D17: Author: 1-line, L-21500 E2-1 and nameplate picture
Note on E17: Brady Nunn: Nameplate
Note on F17: Author: 1-line, L-21500 E2-1
Note on G17: Author: See summary of Equipment document
Note on J17: Author: See name plate picture, at 45C rise.
Note on L17: Author: See name plate picture
Note on O17: Author: 1-line, L-21500 E2-1 and nameplate picture
Note on S17: Author: Tap 5
Note on T17: Value from switch nameplate Limiting Element: Switches and Secondary Element Transmission removed methodology to split current between switches.
Note on V17: Author: From Nameplate
Note on W17: Brady Nunn: 50 Function not available 51 Function Not Available 21 Function evaluated to PRC-025 67 Function evaluated to PRC-025
Note on Y17: Author: Nameplate
Note on AC17: Author: Info from Generator Data sheet, corrected for altitude.
Note on AD17: Author: See K14-76T-E5091
Note on C18: Author: 1-Line Dwg E11007-ESHVE107001 and nameplate picture.
Note on D18: Author: 1-Line Dwg E11007-ESHVE107001 and nameplate picture.
Note on E18: Author: See nameplate picture.
Note on F18: Author: 1-Line Dwg E11005-ESHVE105001.
Note on G18: Author: 1-Line Dwg E11007-ESHVE107001.
Note on H18: Author: 1-Line Dwg E11007-ESHVE107001.
Note on J18: Author: 1-Line Dwg E11007-ESHVE107001 and nameplate picture.
Note on L18: Author: 1-Line Dwg E11007-ESHVE107001 and nameplate picture.
Note on N18: Author: 1-Line Dwg E11005-ESHVE105002 and nameplate picture.
Note on O18: Author: 1-Line Dwg E11005-ESHVE105002 and nameplate picture.
Note on Q18: Author: 1-Line Dwg E11005-ESHVE105001.
Note on R18: Author: 1-Line Dwg E11005-ESHVE105001.
Note on S18: Author: Tap 3
Note on T18: Author: See sheet 2
Note on V18: Author: agrees with nameplate
Note on W18: Brady Nunn: 50 Relay setting set above 51 setting 51 function is set to 6.67 Amps on 115kV 1600:5 = 2134 Primary = 13978A Secondary. 21 function has been evaluated to PRC-025.
Note on Y18: Author: Nameplate
Note on C19: Author: 1-Line Dwg E11007-ESHVE107001 and nameplate picture.
Note on D19: Author: 1-Line Dwg E11007-ESHVE107001 and nameplate picture.
Note on E19: Author: See nameplate picture.
Note on F19: Author: 1-Line Dwg E11005-ESHVE105001.
Note on G19: Author: 1-Line Dwg E11007-ESHVE107001.
Note on H19: Author: 1-Line Dwg E11007-ESHVE107001.
Note on J19: Author: 1-Line Dwg E11007-ESHVE107001 and nameplate picture.
Note on L19: Author: 1-Line Dwg E11007-ESHVE107001 and nameplate picture.
Note on N19: Author: 1-Line Dwg E11005-ESHVE105002 and nameplate picture.
Note on O19: Author: 1-Line Dwg E11005-ESHVE105002 and nameplate picture.
Note on Q19: Author: 1-Line Dwg E11005-ESHVE105001.
Note on R19: Author: 1-Line Dwg E11005-ESHVE105001.
Note on S19: Author: Tap 3
Note on T19: Author: See sheet 2
Note on W19: Brady Nunn: 50 Relay setting set above 51 setting 51 function is set to 6.67 Amps on 115kV 1600:5 = 2134 Primary = 13978A Secondary. 21 function has been evaluated to PRC-025.
Note on Y19: Author: Nameplate
Note on C20: Author: 1-Line Dwg E11007-ESHVE107001 and nameplate picture.
Note on D20: Author: 1-Line Dwg E11007-ESHVE107001 and nameplate picture.
Note on E20: Author: See nameplate picture.
Note on F20: Author: 1-Line Dwg E11006-ESHVE106001.
Note on G20: Author: 1-Line Dwg E11007-ESHVE107001.
Note on H20: Author: 1-Line Dwg E11007-ESHVE107001.
Note on J20: Author: 1-Line Dwg E11007-ESHVE107001 and nameplate picture.
Note on L20: Author: 1-Line Dwg E11007-ESHVE107001 and nameplate picture.
Note on N20: Author: 1-Line Dwg E11006-ESHVE106002 and nameplate picture.
Note on O20: Author: 1-Line Dwg E11006-ESHVE106002 and nameplate picture.
Note on Q20: Author: 1-Line Dwg E1106-ESHVE106001.
Note on R20: Author: 1-Line Dwg E1106-ESHVE106001.
Note on S20: Author: Tap 3
Note on T20: Author: See sheet 2
Note on V20: Author: agrees with nameplate
Note on W20: Brady Nunn: 50 Relay setting set above 51 setting 51 function is set to 6.67 Amps on 115kV 1600:5 = 2134 Primary = 13978A Secondary. 21 function has been evaluated to PRC-025.
Note on Y20: Author: Nameplate
Note on C21: Author: 1-Line Dwg E11007-ESHVE107001 and nameplate picture.
Note on D21: Author: 1-Line Dwg E11007-ESHVE107001 and nameplate picture.
Note on E21: Author: See nameplate picture.
Note on F21: Author: 1-Line Dwg E11006-ESHVE106001.
Note on G21: Author: 1-Line Dwg E11007-ESHVE107001.
Note on H21: Author: 1-Line Dwg E11007-ESHVE107001.
Note on J21: Author: 1-Line Dwg E11007-ESHVE107001 and nameplate picture.
Note on L21: Author: 1-Line Dwg E11007-ESHVE107001 and nameplate picture.
Note on N21: Author: 1-Line Dwg E11006-ESHVE106002 and nameplate picture.
Note on O21: Author: 1-Line Dwg E11006-ESHVE106002 and nameplate picture.
Note on Q21: Author: 1-Line Dwg E1106-ESHVE106001.
Note on R21: Author: 1-Line Dwg E1106-ESHVE106001.
Note on S21: Author: Tap 3
Note on T21: Author: See sheet 2
Note on W21: Brady Nunn: 50 Relay setting set above 51 setting 51 function is set to 6.67 Amps on 115kV 1600:5 = 2134 Primary = 13978A Secondary. 21 function has been evaluated to PRC-025.
Note on Y21: Author: Nameplate
Note on C22: Author: 1-Line Dwg E11007-ESHVE107001 and nameplate picture.
Note on D22: Author: 1-Line Dwg E11007-ESHVE107001 and nameplate picture.
Note on E22: Author: See nameplate picture.
Note on F22: Author: 1-Line Dwg e11007-eshve107002.
Note on G22: Author: 1-Line Dwg E11007-ESHVE107001.
Note on J22: Author: 1-Line Dwg E11007-ESHVE107001 and nameplate picture.
Note on L22: Author: 1-Line Dwg E11007-ESHVE107001 and nameplate picture.
Note on N22: Brady Nunn: 1-Line Dwg E11007-ESHVE107003 and nameplate picture. 10000 A CTs with a TRF=1.5 10000*1.5= 15000A
Note on O22: Brady Nunn: 1-Line Dwg E11007-ESHVE107003 and nameplate picture. 2000A CTs on all phases and 1600A CT on H2. All have 1.5 TRF. 1600A*1.5 = 2400A
Note on S22: Author: Tap 3
Note on T22: Author: See sheet 2
Note on V22: Author: See Nameplate
Note on W22: Author: 50 Relay setting set at 47.07A on 115kV 2000:5 CT = 18828A Primary = 123374A Secondary. 51 function is set to 6.76 Amps on 115kV 2000:5 = 2704A Primary = 17718A Secondary. 21 function has been evaluated to PRC-025.
Note on Y22: Author: Nameplate
Note on C23: Author: 1-Line Dwg E11007-ESHVE107001 and nameplate picture.
Note on D23: Author: 1-Line Dwg E11007-ESHVE107001 and nameplate picture.
Note on E23: Author: See nameplate picture.
Note on F23: Author: 1-Line Dwg e11007-eshve107002.
Note on G23: Author: 1-Line Dwg E11007-ESHVE107001.
Note on J23: Author: 1-Line Dwg E11007-ESHVE107001 and nameplate picture.
Note on L23: Author: 1-Line Dwg E11007-ESHVE107001 and nameplate picture.
Note on N23: Brady Nunn: 1-Line Dwg E11007-ESHVE107003 and nameplate picture. 10000 A CTs with a TRF=1.5 10000*1.5= 15000A
Note on O23: Brady Nunn: 1-Line Dwg E11007-ESHVE107003 and nameplate picture. 2000A CTs on all phases and 1600A CT on H2. All have 1.5 TRF. 1600A*1.5 = 2400A
Note on S23: Author: Tap 3
Note on T23: Author: See sheet 2
Note on V23: Author: See Nameplate
Note on W23: Author: 50 Relay setting set at 47.07A on 115kV 2000:5 CT = 18828A Primary = 123374A Secondary. 51 function is set to 6.76 Amps on 115kV 2000:5 = 2704A Primary = 17718A Secondary. 21 function has been evaluated to PRC-025.
Note on Y23: Author: Nameplate
Note on C24: Author: Mike H: See nameplate picture and L-22329 E2-1
Note on D24: Author: Mike H: See nameplate picture and L-22329 E2-1
Note on E24: Author: Mike H: See nameplate picture and L-22329 E2-1
Note on F24: Author: Mike H: See L-22329 E2-1
Note on G24: Author: Mike H: See L-22329 E2-1
Note on J24: Author: Mike H: See nameplate picture and L-22329 E2-1
Note on L24: Author: Mike H: See nameplate picture and L-22329 E2-1
Note on O24: Author: Mike H: See nameplate picture and L-22329 E2-1
Note on S24: Author: Tap 3
Note on T24: Author: Value from Subs Eng FAC-008-3 Spreadsheet. Limiting element: Relaying SLA
Note on V24: Author: Matches Nameplate
Note on W24: Brady Nunn: 50 function not set 51 function pickup at 2219A on GSU high side, 22190A on GSU low side. 21 function has NOT been evaluated to PRC-025.
Note on Y24: Author: From Nameplate
Note on AC24: Author: Info from Generator Data sheet, corrected for altitude.
Note on AD24: Author: See K14-76T-E5091
Note on C25: Author: 1-line, E0178803-ESMVE13002 Sh1.
Note on D25: Author: 1-line, E0178803-ESMVE13002 Sh1.
Note on E25: Author: 1-line, E0178803-ESMVE13002 Sh1.
Note on F25: Author: 1-line, E0178803-ESMVE13002 Sh1.
Note on G25: Author: Equipment data sheet, page 21 of 119573-S-S-40600 SIL R01
Note on J25: Author: 1-line, E0178803-ESMVE13002 Sh1.
Note on L25: Author: 1-line, E0178803-ESMVE13002 Sh1.
Note on N25: Author: 1-line, E0178803-ESMVE13002 Sh1. 16000A per phase connected delta. Therefore multiply by square root of 3 to get equivalent value of phase current.
Note on O25: Author: E0178803-ESMVE13002 Sh1.
Note on S25: Author: Tap 2
Note on T25: Author: See sheet 2
Note on V25: Author: Matches current rating. Tap 2 HS 1645.7 LS 12444.4 Multiply by sqrt(3) for generator impact at 21554.33307 See Hyundai manufacturer report page 24
Note on W25: Brady Nunn: 50 function set @ 22435A GSU high side, 293899 51 function is set to 8.22 Amps on 345kV 2000:5 = 3288A GSU HS = 43072.8A Secondary. 21 function has been evaluated to PRC-025.
Note on Y25: Author: Based on Manufacturer test report
Note on AC25: Author: Info from Generator Data sheet, corrected for altitude.
Note on AD25: Author: See K14-76T-E5091
Note on C26: Author: 1-line, E0178803-ESMVE13002 Sh1.
Note on D26: Author: 1-line, E0178803-ESMVE13002 Sh1.
Note on E26: Author: 1-line, E0178803-ESMVE13002 Sh1.
Note on F26: Author: 1-line, E0178803-ESMVE13002 Sh1.
Note on G26: Author: Equipment data sheet, page 21 of 119573-S-S-40600 SIL R01
Note on J26: Author: 1-line, E0178803-ESMVE13002 Sh1.
Note on L26: Author: 1-line, E0178803-ESMVE13002 Sh1.
Note on N26: Author: 1-line, E0178803-ESMVE13002 Sh1. 16000A per phase connected delta. Therefore multiply by square root of 3 to get equivalent value of phase current.
Note on O26: Author: E0178803-ESMVE13002 Sh1.
Note on S26: Author: Tap 2
Note on T26: Author: See sheet 2
Note on V26: Author: Matches current rating. Tap 2 HS 1645.7 LS 12444.4 Multiply by sqrt(3) for generator impact at 21554.33307 See Hyundai manufacturer report page 24
Note on W26: Brady Nunn: 50 function set @ 22435A GSU high side, 293899 51 function is set to 8.22 Amps on 345kV 2000:5 = 3288A GSU HS = 43072.8A Secondary. 21 function has been evaluated to PRC-025.
Note on Y26: Author: Based on Manufacturer test report
Note on AC26: Author: Info from Generator Data sheet, corrected for altitude.
Note on AD26: Author: See K14-76T-E5091
Note on C27: Author: See nameplate picture or 1APK-E1001
Note on D27: Author: See nameplate picture or 1APK-E1001
Note on E27: Author: See nameplate picture
Note on F27: Author: See 1APK-E1001
Note on G27: Author: See FP 90/92-N-050-0001
Note on J27: Author: See nameplate picture
Note on L27: Author: See nameplate picture
Note on O27: Author: Hot Spot CT
Note on S27: Author: Tap 3
Note on T27: Author: Value from Subs Eng FAC-008-3 Spreadsheet. Limiting Element: Metering Unit CTs
Note on V27: Author: Calculation since nameplate is in 403000kva or the 55C hot spot capability
Note on W27: Brady Nunn: 50 function set at 32.878A secondary, CTR = 400. GSU HS Pickup = 13151.2A. GSU LS pickup = 144005.6A 51 function set at 4.93A secondary, CTR=400. GSU HS pickup = 1972A. GSU LS pickup = 21593.4A 21 function has been evaluated to PRC-025.
Note on Y27: Author: from nameplate
Note on AC27: Author: Info from Generator Data sheet, corrected for altitude.
Note on AD27: Author: See K14-76T-E5091
Note on C28: Author: See nameplate picture or 1APK-E1001
Note on D28: Author: See nameplate picture or 1APK-E1001
Note on E28: Author: See nameplate picture
Note on F28: Author: See 1APK-E1001
Note on G28: Author: See FP 90/92-N-050-0001
Note on J28: Author: See nameplate picture or 1APK-E1001
Note on L28: Author: See nameplate picture
Note on O28: Author: Hot Spot CT
Note on S28: Author: Tap 3
Note on T28: Author: Value from Subs Eng FAC-008-3 Spreadsheet. Limiting Element: Metering Unit CTs
Note on V28: Author: Calculation since nameplate is in 403000kva or the 55C hot spot capability
Note on W28: Brady Nunn: 50 function set at 32.878A secondary, CTR = 400. GSU HS Pickup = 13151.2A. GSU LS pickup = 144005.6A 51 function set at 4.93A secondary, CTR=400. GSU HS pickup = 1972A. GSU LS pickup = 21593.4A 21 function has been evaluated to PRC-025.
Note on Y28: Author: From Nameplate
Note on AC28: Author: Info from Generator Data sheet, corrected for altitude.
Note on AD28: Author: See K14-76T-E5091
Note on C29: Author: See nameplate picture
Note on D29: Author: See nameplate picture
Note on E29: Author: See nameplate picture
Note on F29: Author: See 188D8641
Note on G29: Author: See 167D7871 Sh1
Note on H29: Author: Part of generator bkr. See nameplate photo
Note on J29: Author: See nameplate picture
Note on L29: Author: See nameplate picture
Note on N29: Author: CT to WTI, ratio 7600/5 with a continuous current rating factor = 2.0. See nameplate photo. 7600*2=15200
Note on O29: Brady Nunn: CT4 rated at 625/5A, with a continous current factor = 2.0. See nameplate photo. 625*2 = 1250
Note on Q29: Author: See Bkr 252G nameplate picture
Note on R29: Author: See 188D8641 Sh2
Note on S29: Author: Tap 2
Note on T29: Author: Value from Subs Eng FAC-008-3 Spreadsheet. Limiting Element: Metering Unit CTs
Note on V29: Author: Matches Nameplate Value
Note on W29: Brady Nunn: 50 function pickup at 23.612A secondary, CTR=240A. HS GSU pickup = 5666.9A. GSU LS pickup = 76106.5A 51 function pickup at 4.2A secondary, CTR=240A. HS GSU pickup = 1008A. GSU LS pickup = 13537 A. 21 function has been evaluated to PRC-025.
Note on Y29: Author: Nameplate
Note on AC29: Author: Info from Generator Data sheet, corrected for altitude.
Note on AD29: Author: See K14-76T-E5091
Note on C30: Author: See nameplate picture
Note on D30: Author: See nameplate picture
Note on E30: Author: See nameplate picture
Note on F30: Author: See 188D8641
Note on G30: Author: See 167D7871 Sh1
Note on H30: Author: Part of generator bkr See nameplate photo
Note on J30: Author: See nameplate picture
Note on L30: Author: See nameplate picture
Note on N30: Author: CT to WTI, ratio 7600/5 with a continuous current rating factor = 2.0. See nameplate photo. 7600*2=15200
Note on O30: Brady Nunn: CT4 rated at 625/5A, with a continous current factor = 2.0. See nameplate photo. 625*2 = 1250
Note on Q30: Author: See Bkr 252G nameplate picture
Note on R30: Author: See 188D8641 Sh2
Note on S30: Author: Tap 2
Note on T30: Author: Value from Subs Eng FAC-008-3 Spreadsheet. Limiting Element: Metering Unit CTs
Note on V30: Author: Matches Nameplate Value
Note on W30: Brady Nunn: 50 function pickup at 23.612A secondary, CTR=240A. HS GSU pickup = 5666.9A. GSU LS pickup = 76106.5A 51 function pickup at 4.2A secondary, CTR=240A. HS GSU pickup = 1008A. GSU LS pickup = 13537 A. 21 function has been evaluated to PRC-025.
Note on Y30: Author: Nameplate
Note on AC30: Author: Info from Generator Data sheet, corrected for altitude.
Note on AD30: Author: See K14-76T-E5091
Note on C31: Author: See nameplate picture
Note on D31: Author: See nameplate picture
Note on E31: Author: See nameplate picture
Note on F31: Author: See 194D5743 Sh 2
Note on G31: Author: See 192D1174 Sh 1
Note on H31: Author: Part of generator bkr See nameplate photo
Note on J31: Author: See nameplate picture
Note on L31: Author: See nameplate picture
Note on O31: Author: See nameplate picture KBS - Not Used
Note on Q31: Author: See nameplate picture
Note on R31: Author: See 194D5743 Sh 2
Note on S31: Author: Tap 2
Note on T31: Author: Value from Subs Eng FAC-008-3 Spreadsheet. Limiting Element: Metering Unit CTs
Note on V31: Author: See namplate
Note on W31: Brady Nunn: 50 function pickup at 22.816A secondary, CTR=240A. HS GSU pickup = 5475.8A. GSU LS pickup = 73540.5A 51 function pickup at 4.2A secondary, CTR=240A. HS GSU pickup = 1008A. GSU LS pickup = 13537 A. 21 function has been evaluated to PRC-025.
Note on Y31: Author: See Nameplate
Note on AC31: Author: Info from Generator Data sheet, corrected for altitude.
Note on AD31: Author: See K14-76T-E5091
Note on C32: Author: See nameplate picture
Note on D32: Author: See nameplate picture
Note on E32: Author: See nameplate picture
Note on F32: Author: See 194D5743 Sh 2
Note on G32: Author: See 192D1174 Sh 1
Note on H32: Author: Part of generator bkr See nameplate photo
Note on J32: Author: See nameplate picture
Note on L32: Author: See nameplate picture
Note on O32: Author: See nameplate picture KBS - Not Used
Note on Q32: Author: See nameplate picture
Note on R32: Author: See 194D5743 Sh 2
Note on S32: Author: Tap 2
Note on T32: Author: Value from Subs Eng FAC-008-3 Spreadsheet. Limiting Element: Metering Unit CTs
Note on V32: Author: See Nameplate
Note on W32: Brady Nunn: 50 function pickup at 22.816A secondary, CTR=240A. HS GSU pickup = 5475.8A. GSU LS pickup = 73540.5A 51 function pickup at 4.2A secondary, CTR=240A. HS GSU pickup = 1008A. GSU LS pickup = 13537 A. 21 function has been evaluated to PRC-025.
Note on Y32: Author: See Nameplate
Note on AC32: Author: Info from Generator Data sheet, corrected for altitude.
Note on AD32: Author: See K14-76T-E5091
Note on C33: Author: See nameplate picture
Note on D33: Author: See nameplate picture
Note on E33: Author: See nameplate picture
Note on F33: Author: See E158 Sh 2
Note on G33: Author: See 192D2849 Sh1
Note on H33: Author: Part of generator bkr See nameplate photo
Note on J33: Author: See nameplate picture
Note on L33: Author: See nameplate picture
Note on O33: Author: See nameplate picture KBS - HOT SPOT CT
Note on Q33: Author: See Bkr 452G nameplate picture
Note on R33: Author: See Bkr 452G nameplate picture
Note on S33: Author: Tap 2
Note on T33: Author: Value from Subs Eng FAC-008-3 Spreadsheet. Limiting Element: Metering Unit CTs
Note on V33: Author: Matches Nameplate data
Note on W33: Brady Nunn: 50 function pickup at 22.816A secondary, CTR=240A. HS GSU pickup = 5475.8A. GSU LS pickup = 73540.5A 51 function pickup at 4.2A secondary, CTR=240A. HS GSU pickup = 1008A. GSU LS pickup = 13537 A. 21 function has been evaluated to PRC-025.
Note on Y33: Author: Nameplate
Note on AC33: Author: Info from Generator Data sheet, corrected for altitude.
Note on AD33: Author: See K14-76T-E5091
Note on C34: Author: See nameplate picture
Note on D34: Author: See nameplate picture
Note on E34: Author: See nameplate picture
Note on F34: Author: See E158 Sh 2
Note on G34: Author: See 192D2849 Sh1
Note on H34: Author: Part of generator bkr See nameplate photo
Note on J34: Author: See nameplate picture
Note on L34: Author: See nameplate picture
Note on O34: Author: See nameplate picture KBS - HOT SPOT CT
Note on Q34: Author: See Bkr 452G nameplate picture
Note on R34: Author: See Bkr 452G nameplate picture
Note on S34: Author: Tap 2
Note on T34: Author: Value from Subs Eng FAC-008-3 Spreadsheet. Limiting Element: Metering Unit CTs
Note on V34: Author: Matches Nameplate data
Note on W34: Brady Nunn: 50 function pickup at 22.816A secondary, CTR=240A. HS GSU pickup = 5475.8A. GSU LS pickup = 73540.5A 51 function pickup at 4.2A secondary, CTR=240A. HS GSU pickup = 1008A. GSU LS pickup = 13537 A. 21 function has been evaluated to PRC-025.
Note on Y34: Author: Nameplate
Note on AC34: Author: Info from Generator Data sheet, corrected for altitude.
Note on AD34: Author: See K14-76T-E5091
Note on C35: Author: See nameplate picture
Note on D35: Author: See nameplate picture
Note on E35: Author: See nameplate picture
Note on F35: Author: See 5GTA-E1002 Sh1
Note on G35: Author: See 5GTA-E1002 Sh1
Note on H35: Author: Part of generator bkr
Note on N35: Author: See nameplate picture. CT to WTI.
Note on S35: Brady Nunn: Tap 1
Note on T35: Author: See sheet 2
Note on V35: Author: matches nameplate value
Note on W35: Author: 51P set at 883 A HS 883 * 13.42 = 11850 21 function evaluated to PRC-025
Note on Y35: Author:
Note on C36: Author: See nameplate picture
Note on D36: Author: See nameplate picture
Note on E36: Author: See nameplate picture
Note on F36: Author: See 5GTA-E1002 Sh1
Note on G36: Author: See 5GTA-E1002 Sh1
Note on H36: Author: Part of generator bkr
Note on J36: Author: See nameplate picture
Note on L36: Author: See nameplate picture
Note on N36: Author: See nameplate picture. CT to WTI.
Note on O36: Author: See nameplate picture and 5GTA-E1002 Sh2
Note on Q36: Author: See Bkr 552G nameplate picture
Note on R36: Author: See 5GTA-E1002 Sh1
Note on S36: Brady Nunn: Tap 1
Note on T36: Author: See sheet 2
Note on V36: Author: Matches Nameplate value
Note on W36: Brady Nunn: 51P set at 883 A HS 883 * 13.42 = 11850 21 function evaluated to PRC-025
Note on Y36: Author: Nameplate
Note on AC36: Author: Info from Generator Data sheet, corrected for altitude.
Note on AD36: Author: See K14-76T-E5091
Note on C37: Author: See nameplate picture
Note on D37: Author: See nameplate picture
Note on E37: Author: See nameplate picture
Note on F37: Author: See 6GTA-E1002 Sh1
Note on G37: Author: See 6GTA-E1002 Sh1
Note on H37: Author: Part of generator bkr
Note on J37: Author: See nameplate picture
Note on L37: Author: See nameplate picture
Note on N37: Author: See nameplate picture. 8000/5 CTs and 2000/5 CTs with a TRF=4.
Note on O37: Author: See nameplate picture KBS Updated Value
Note on Q37: Author: See Bkr 652G nameplate picture
Note on R37: Author: See 6GTA-E1002 Sh1
Note on S37: Author: Tap 2
Note on T37: Author: See sheet 2
Note on V37: Author: See Nameplate
Note on W37: Brady Nunn: 51P set at 883 A HS 883 * 13.43 = 11850 21 function evaluated to PRC-025
Note on Y37: Author: Nameplate
Note on AC37: Author: Info from Generator Data sheet, corrected for altitude.
Note on AD37: Author: See K14-76T-E5091
Note on C38: Author: See nameplate picture
Note on D38: Author: See nameplate picture
Note on E38: Author: See nameplate picture
Note on F38: Author: See 6GTA-E1002 Sh1
Note on G38: Author: See 6GTA-E1002 Sh1
Note on H38: Author: Part of generator bkr
Note on J38: Author: See nameplate picture
Note on L38: Author: See nameplate picture
Note on N38: Author: See nameplate picture. 8000/5 CTs and 2000/5 CTs with a TRF=4.
Note on O38: Author: See nameplate picture KBS Updated Value
Note on Q38: Author: See Bkr 652G nameplate picture
Note on R38: Author: See 6GTA-E1002 Sh1
Note on S38: Author: Tap 2
Note on T38: Author: See sheet 2
Note on V38: Author: See Nameplate
Note on W38: Brady Nunn: 51P set at 883 A HS 883 * 13.43 = 11850 21 function evaluated to PRC-025
Note on Y38: Author: Nameplate
Note on AC38: Author: Info from Generator Data sheet, corrected for altitude.
Note on AD38: Author: See K14-76T-E5091
Note on C39: Author: From Generator Data sheet generator output as a function of inlet air temperature corrected for altitude. 4993' (.94 multiplier). Base capability curve at 104F used
Note on D39: Author: Info from Generator Data sheet, corrected for altitude.
Note on E39: Author: From Summer capability corrected for altitude. 4993' (.94 multiplier)
Note on F39: Brady Nunn: 0130-008.001S01
Note on G39: Author: Drawing 130-13.5 sh2 Unit Bus bars are 5" AL with 1033.5 Kcmil ACSR inside if segments exceed 20'. Since some segments are smaller than 20' (between disconnect and right angle to GSU) the tubular conductor will be the most limiting element. Value found on 2014 XEL-EVD-Faciltiy Rating Supplement-Table-Tubular and Square Conductor.
Note on H39: Author: Drawing 130-13.5 sh2 Unit Bus bars are 5" AL with 1033.5 Kcmil ACSR inside if segments exceed 20'. Since some segments are smaller than 20' (between disconnect and right angle to GSU) the tubular condcustor will be the most limiting element. Value found on 2014 XEL-EVD-Faciltiy Rating Supplement-Table-Tubular and Square Conductor.
Note on J39: Author: See name plate picture
Note on L39: Author: See name plate picture
Note on O39: Author: Rated by transmission
Note on Q39: Author: 1-line, 813E131 Sh1.
Note on R39: Author: 1-line, 813E131 Sh1. 0130-008.001S01
Note on S39: Author: Tap B
Note on T39: Author: Value from Subs Eng FAC-008-3 Spreadsheet. Limiting Element: Conductor
Note on V39: Author: Calculation used as Nameplate is at 110000kva
Note on W39: Brady Nunn: 50 function pickup at 39.1A secondary, CTR= 200. HS pickup = 7820A. LS pickup = 70067.2A 51 function is set to 5.84 Amps on 115kV 1000:5 = 1168A Primary = 10465.3A Secondary. 21 function (on generator) has been evaluated to PRC-025.
Note on AC39: Author: Info from Generator Data sheet, corrected for altitude.
Note on AD39: Author: See K14-76T-E5091
Note on C40: Author: From Generator Data sheet generator output as a function of inlet air temperature corrected for altitude. 4993' (.94 multiplier). Base capability curve at 0F used
Note on D40: Author: Info from Generator Data sheet, corrected for altitude.
Note on E40: Author: From Winter capability corrected for altitude. 4993' (.94 multiplier)
Note on F40: Brady Nunn: 0130-008.001S01
Note on G40: Author: Drawing 130-13.5 sh2 Unit Bus bars are 5" AL with 1033.5 Kcmil ACSR inside if segments exceed 20'. Since some segments are smaller than 20' (between disconnect and right angle to GSU) the tubular conductor will be the most limiting element. Value found on 2014 XEL-EVD-Faciltiy Rating Supplement-Table-Tubular and Square Conductor.
Note on H40: Author: Drawing 130-13.5 sh2 Unit Bus bars are 5" AL with 1033.5 Kcmil ACSR inside if segments exceed 20'. Since some segments are smaller than 20' (between disconnect and right angle to GSU) the tubular condcustor will be the most limiting element. Value found on 2014 XEL-EVD-Faciltiy Rating Supplement-Table-Tubular and Square Conductor.
Note on J40: Author: See name plate picture
Note on L40: Author: See name plate picture
Note on Q40: Author: 1-line, 813E131 Sh1.
Note on R40: Author: 1-line, 813E131 Sh1. 0130-008.001S01
Note on S40: Author: Tap B
Note on T40: Author: Value from Subs Eng FAC-008-3 Spreadsheet. Limiting Element: Secondary Limit
Note on V40: Author: Calculation used as Nameplate is at 110000kva
Note on W40: Brady Nunn: 50 function pickup at 39.1A secondary, CTR= 200. HS pickup = 7820A. LS pickup = 70067.2A 51 function is set to 5.84 Amps on 115kV 1000:5 = 1168A Primary = 10465.3A Secondary. 21 function (on generator) has been evaluated to PRC-025.
Note on AC40: Author: Info from Generator Data sheet, corrected for altitude.
Note on AD40: Author: See K14-76T-E5091
Note on C41: Author: From Generator Data sheet generator output as a function of inlet air temperature corrected for altitude. 4993' (.94 multiplier). Base capability curve at 104F used
Note on D41: Author: Info from Generator Data sheet, corrected for altitude.
Note on E41: Author: From Summer capability corrected for altitude. 4993' (.94 multiplier)
Note on F41: Brady Nunn: 0130-008.001S01
Note on G41: Author: Drawing 130-13.5 sh2 Unit Bus bars are 5" AL with 1033.5 Kcmil ACSR inside if segments exceed 20'. Since some segments are smaller than 20' (between disconnect and right angle to GSU) the tubular conductor will be the most limiting element. Value found on 2014 XEL-EVD-Faciltiy Rating Supplement-Table-Tubular and Square Conductor.
Note on H41: Author: Drawing 130-13.5 sh2 Unit Bus bars are 5" AL with 1033.5 Kcmil ACSR inside if segments exceed 20'. Since some segments are smaller than 20' (between disconnect and right angle to GSU) the tubular condcustor will be the most limiting element. Value found on 2014 XEL-EVD-Faciltiy Rating Supplement-Table-Tubular and Square Conductor.
Note on J41: Author: See name plate picture
Note on L41: Author: See name plate picture
Note on Q41: Author: 1-line, 813E131 Sh1.
Note on R41: Author: 1-line, 813E131 Sh1. 0130-008.001S01
Note on S41: Author: Tap B
Note on T41: Author: Value from Subs Eng FAC-008-3 Spreadsheet. Limiting Element: Conductor
Note on V41: Author: Calculation used as Nameplate is at 110000kva
Note on W41: Brady Nunn: 50 function pickup at 39.1A secondary, CTR= 200. HS pickup = 7820A. LS pickup = 70067.2A 51 function is set to 5.84 Amps on 115kV 1000:5 = 1168A Primary = 10465.3A Secondary. 21 function (on generator) has been evaluated to PRC-025.
Note on AC41: Author: Info from Generator Data sheet, corrected for altitude.
Note on AD41: Author: See K14-76T-E5091
Note on C42: Author: From Generator Data sheet generator output as a function of inlet air temperature corrected for altitude. 4993' (.94 multiplier). Base capability curve at 0F used
Note on D42: Author: Info from Generator Data sheet, corrected for altitude.
Note on E42: Author: From Summer capability corrected for altitude. 4993' (.94 multiplier)
Note on F42: Brady Nunn: 0130-008.001S01
Note on G42: Author: Drawing 130-13.5 sh2 Unit Bus bars are 5" AL with 1033.5 Kcmil ACSR inside if segments exceed 20'. Since some segments are smaller than 20' (between disconnect and right angle to GSU) the tubular conductor will be the most limiting element. Value found on 2014 XEL-EVD-Faciltiy Rating Supplement-Table-Tubular and Square Conductor.
Note on H42: Author: Drawing 130-13.5 sh2 Unit Bus bars are 5" AL with 1033.5 Kcmil ACSR inside if segments exceed 20'. Since some segments are smaller than 20' (between disconnect and right angle to GSU) the tubular condcustor will be the most limiting element. Value found on 2014 XEL-EVD-Faciltiy Rating Supplement-Table-Tubular and Square Conductor.
Note on J42: Author: See name plate picture
Note on L42: Author: See name plate picture
Note on Q42: Author: 1-line, 813E131 Sh1.
Note on R42: Author: 1-line, 813E131 Sh1. 0130-008.001S01
Note on S42: Author: Tap B
Note on T42: Author: Value from Subs Eng FAC-008-3 Spreadsheet. Limiting Element: Secondary Limit
Note on V42: Author: Calculation used as Nameplate is at 110000kva
Note on W42: Brady Nunn: 50 function pickup at 39.1A secondary, CTR= 200. HS pickup = 7820A. LS pickup = 70067.2A 51 function is set to 5.84 Amps on 115kV 1000:5 = 1168A Primary = 10465.3A Secondary. 21 function (on generator) has been evaluated to PRC-025.
Note on AC42: Author: Info from Generator Data sheet, corrected for altitude.
Note on AD42: Author: See K14-76T-E5091
Note on B43: Author: Combined rating of both units for shared GSU transformer
Note on C43: Author: Combined summer nameplate values
Note on D43: Author: Info from Generator Data sheet, corrected for altitude.
Note on E43: Author: Combined summer nameplate values
Note on F43: Brady Nunn: 0130-008.001S01 No CTs on common bus
Note on G43: Author: Drawing 130-13.5 sh2 Unit Bus bars are 6" and 12 500Kcmil conductors to connect. the tubular conductor will be the most limiting element. Value found on 2014 XEL-EVD-Faciltiy Rating Supplement-Table-Tubular and Square Conductor.
Note on J43: Author: See name plate picture
Note on L43: Author: See name plate picture
Note on Q43: Author: 1-line, 813E131 Sh1.
Note on R43: Author: 1-line, 813E131 Sh1. 0130-008.001S01
Note on S43: Author: Tap B
Note on T43: Author: Value from Subs Eng FAC-008-3 Spreadsheet. Limiting Element: Conductor
Note on V43: Author: Calculation used as Nameplate is at 110000kva
Note on W43: Brady Nunn: 50 function pickup at 39.1A secondary, CTR= 200. HS pickup = 7820A. LS pickup = 70067.2A 51 function is set to 5.84 Amps on 115kV 1000:5 = 1168A Primary = 10465.3A Secondary. 21 function (on generator) has been evaluated to PRC-025.
Note on Y43: Author: Calculated from FOA rating
Note on AC43: Author: Info from Generator Data sheet, corrected for altitude.
Note on AD43: Author: See K14-76T-E5091
Note on B44: Author: Combined rating of both units for shared GSU transformer
Note on C44: Author: Combined winter nameplate values
Note on D44: Author: Info from Generator Data sheet, corrected for altitude.
Note on E44: Author: Combined winter nameplate values
Note on F44: Brady Nunn: 0130-008.001S01 No CTs on common bus
Note on G44: Author: Drawing 130-13.5 sh2 Unit Bus bars are 6" and 12 500Kcmil conductors to connect. the tubular conductor will be the most limiting element. Value found on 2014 XEL-EVD-Faciltiy Rating Supplement-Table-Tubular and Square Conductor.
Note on J44: Author: See name plate picture
Note on L44: Author: See name plate picture
Note on Q44: Author: 1-line, 813E131 Sh1.
Note on R44: Author: 1-line, 813E131 Sh1. 0130-008.001S01
Note on S44: Author: Tap B
Note on T44: Author: Value from Subs Eng FAC-008-3 Spreadsheet. Limiting Element: Secondary Limit
Note on V44: Author: Calculation used as Nameplate is at 110000kva
Note on W44: Brady Nunn: 50 function pickup at 39.1A secondary, CTR= 200. HS pickup = 7820A. LS pickup = 70067.2A 51 function is set to 5.84 Amps on 115kV 1000:5 = 1168A Primary = 10465.3A Secondary. 21 function (on generator) has been evaluated to PRC-025.
Note on Y44: Author: Calculated from FOA rating
Note on AC44: Author: Info from Generator Data sheet, corrected for altitude.
Note on AD44: Author: See K14-76T-E5091
Note on C45: Author: See nameplate picture, capability curve, and uprating explanation
Note on D45: Author: See nameplate picture and 0010-065-07-0007 Sh1
Note on E45: Author: See nameplate picture and 0010-065-07-0007 Sh1
Note on F45: Author: See 0010-065-07-0007 Sh1
Note on G45: Author: See u1 isorate
Note on J45: Author: See nameplate picture
Note on L45: Author: See nameplate picture
Note on O45: Author: See nameplate picture and 0010-065-07-0007 Sh1
Note on S45: Author: Tap D
Note on T45: Author: See sheet 2
Note on V45: Author: matches Nameplate
Note on W45: Brady Nunn: 51 set at 4.36 A secondary. CTR=240. 240*4.36 = 1046.4 A HS 1046.4*13.11 = 13718 A LS 21 Function evaluated to PRC-025
Note on AC45: Author: Info from Generator Data sheet, corrected for altitude.
Note on AD45: Author: See K14-76T-E5091
Note on C46: Author: See nameplate picture and A-723 Sh E-102
Note on D46: Author: See nameplate picture and A-723 Sh E-102
Note on E46: Author: See nameplate picture and A-723 Sh E-102
Note on F46: Author: See A-723 Sh E-102
Note on G46: Author: See u2isorate
Note on J46: Author: See nameplate picture and A-723 Sh E-102
Note on L46: Author: See nameplate picture and A-723 Sh E-102
Note on O46: Author: See A-723 Sh E-102 and GSU nameplate. Hotspot CT rated at 1000A
Note on S46: Author: Tap 2
Note on T46: Author: See sheet 2
Note on V46: Author: see nameplate
Note on W46: Brady Nunn: 51 function is set to 6.43 Amps on 230kV 1200:5 = 1543.2A Primary = 16543 Secondary. 21 function has been evaluated to PRC-025.
Note on AC46: Author: Info from Generator Data sheet, corrected for altitude.
Note on AD46: Author: See K14-76T-E5091
Note on C47: Author: See generator curves
Note on D47: Author: See Generator curves
Note on E47: Author: See Generator curves
Note on F47: Author: Reference one-line D991030-500E101 SH.1.pdf and H3181-393-X-1101 SH1
Note on G47: Author: Reference DWG 192D2633 SH1 and one-line
Note on J47: Author: See Transformer nameplate
Note on K47: Author: Reference transformer nameplate and tap position photo
Note on L47: Author: Nameplate data, Actual voltage at generator kV
Note on N47: Author: Reference DWG D991030-500E102 SH1
Note on O47: Author: Reference DWG D991030-500E102 SH1
Note on T47: Author: See Sheet 2
Note on W47: Zenon Kampman: SEL 587 50P14P Pickup 4 A secondary, 6400A primary
Note on Y47: Author: Nameplate
Note on C48: Author: See generator curves
Note on D48: Author: See Generator curves
Note on E48: Author: See Generator curves
Note on F48: Author: Reference one-line D991030-500E101 SH.1.pdf and H3181-393-X-1101 SH1
Note on G48: Author: Reference DWG 192D2633 SH1 and one-line
Note on J48: Author: See Transformer nameplate
Note on K48: Author: Reference transformer nameplate and tap position photo
Note on L48: Author: Nameplate data, Actual voltage at generator kV
Note on N48: Author: Reference DWG D991030-500E102 SH1
Note on O48: Author: Reference DWG D991030-500E102 SH1
Note on T48: Author: See Sheet 2
Note on W48: Author: SEL 587 50P14P Pickup 4 A secondary, 6400A primary
Note on Y48: Author: Nameplate
Note on C49: Author: See generator curves
Note on D49: Author: See Generator curves
Note on E49: Author: See Generator curves
Note on F49: Author: Reference one-line D991030-500E101 SH.1.pdf H3181-393-X-1201 SH1
Note on G49: Author: Reference DWG 192D2633 SH1 and one-line
Note on J49: Author: See Transformer nameplate
Note on K49: Author: Reference transformer nameplate and tap position photo
Note on L49: Author: Nameplate data, Actual voltage at generator kV
Note on N49: Author: Reference DWG D991030-500E102 SH1
Note on O49: Author: Reference DWG D991030-500E102 SH1
Note on T49: Author: See Sheet 2
Note on W49: Author: SEL 587 50P14P Pickup 4 A secondary, 6400A primary
Note on Y49: Author: Nameplate
Note on C50: Author: See generator curves
Note on D50: Author: See Generator curves
Note on E50: Author: See Generator curves
Note on F50: Author: Reference one-line D991030-500E101 SH.1.pdf H3181-393-X-1201 SH1
Note on G50: Author: Reference DWG 192D2633 SH1 and one-line
Note on J50: Author: See Transformer nameplate
Note on K50: Author: Reference transformer nameplate and tap position photo
Note on L50: Author: Nameplate data, Actual voltage at generator kV
Note on N50: Author: Reference DWG D991030-500E102 SH1
Note on O50: Author: Reference DWG D991030-500E102 SH1
Note on T50: Author: See Sheet 2
Note on W50: Zenon Kampman: SEL 587 50P14P Pickup 4 A secondary, 6400A primary
Note on Y50: Author: Nameplate
Note on C51: Author: See generator curves - Combined MVA of both units
Note on D51: Author: See Generator curves
Note on E51: Author: See Generator curves
Note on J51: Author: See Transformer nameplate
Note on K51: Author: Reference transformer nameplate and tap position photo
Note on L51: Author: Nameplate data, Actual voltage at generator kV
Note on N51: Author: Reference DWG D991030-500E102 SH1
Note on O51: Author: Reference DWG D991030-500E102 SH1
Note on T51: Author: See Sheet 2
Note on C52: Author: See generator curves- Combined MVA of both generators
Note on D52: Author: See Generator curves
Note on E52: Author: See Generator curves
Note on J52: Author: See Transformer nameplate
Note on K52: Author: Reference transformer nameplate and tap position photo
Note on L52: Author: Nameplate data, Actual voltage at generator kV
Note on N52: Author: Reference DWG D991030-500E102 SH1
Note on O52: Author: Reference DWG D991030-500E102 SH1
Note on C53: Author: See Name plate piture or L-22666 E2-1
Note on D53: Author: See Name plate piture or L-22666 E2-1
Note on E53: Author: See Name plate piture or L-22666 E2-1
Note on F53: Author: See L-22666 E2-1
Note on G53: Author: See L-22666 E2-1 Rev21 and 79DCN013. Generator Isophase rated at 18000 A. GSU sections each rated at 11000A. 2 sections in parallel, combined rating of 22000A.
Note on J53: Author: See L-22666 E2-1. Two GSU transformers in parallel. Combined rating of 728 MVA
Note on L53: Author: See L-22666 E2-1
Note on O53: Rated by Transmission
Note on Q53: Author: Generator Breakers are part of transmission FAC-008
Note on R53: Author: Generator Breakers are part of transmission FAC-008
Note on S53: Author: Tap E
Note on T53: Author: Value from Subs Eng FAC-008-3 Spreadsheet. Limiting Element: Conductor
Note on W53: Brady Nunn: 50 function not set 51 function picjup at 7.74A secondary, CTR=400. GSU HS pickup = 3096A. GSU LS pickup = 33901A 21 function has been evaluated to PRC-025.
Note on Y53: Author: Calculated from 65C rise. Both transformer banks are combined at the yard.
Note on AC53: Author: Info from Generator Data sheet, corrected for altitude.
Note on AD53: Author: See K14-76T-E5091
Note on C54: Author: See Instruction Book Photo
Note on D54: Author: See Instruction Book Photo
Note on E54: Author: See Instruction Book Photo, AMP rating given
Note on F54: Author: See 9727D20 sh1
Note on G54: Author: See U-126674-M
Note on H54: Author: Part of Gen Bkr. Reference D010208-EMAE100 and Gen Bkr Photo, rating of assembly is used since component ratings are not differentiated by manufacturer
Note on J54: Author: See nameplate picture
Note on L54: Author: See nameplate picture
Note on N54: Author: See nameplate picture
Note on O54: Author: See nameplate picture
Note on Q54: Author: See 1HC0015420
Note on R54: Author: See 9727D20 sh2
Note on S54: Author: Tap 2
Note on T54: Author: Value from Subs Eng FAC-008-3 Spreadsheet. Limiting Element: 1272 ACSR Conductor
Note on V54: Author: Delta Current rating per nameplate
Note on W54: Brady Nunn: 50 function pickup at 21.24A secondary, CTR= 240. HS pickup = 5097.6A. LS pickup = 80796.96A 51 function is set to 4.2 A secondary, CTR=240. HS pickup = 1008A. LS pickup = 15977A 21 function (on generator) has been evaluated to PRC-025.
Note on Y54: Author: Nameplate
Note on AC54: Author: Info from Generator Data sheet, corrected for altitude.
Note on AD54: Author: See K14-76T-E5091
Note on C55: Author: See Instruction Book Photo
Note on D55: Author: See Instruction Book Photo
Note on E55: Author: See Instruction Book Photo, AMP rating given
Note on F55: Author: See 9727D20 sh1
Note on G55: Author: See U-126674-M
Note on H55: Author: Part of Gen Bkr. Reference D010208-EMAE100 and Gen Bkr Photo, rating of assembly is used since component ratings are not differentiated by manufacturer
Note on J55: Author: See nameplate picture
Note on L55: Author: See nameplate picture
Note on N55: Author: See nameplate picture
Note on O55: Author: See nameplate picture
Note on Q55: Author: See 1HC0015420
Note on R55: Author: See 9727D20 sh2
Note on S55: Author: Tap 2
Note on T55: Author: Value from Subs Eng FAC-008-3 Spreadsheet. Limiting Element: 1272 ACSR Conductor
Note on V55: Author: Delta Current rating per nameplate
Note on W55: Brady Nunn: 50 function pickup at 21.24A secondary, CTR= 240. HS pickup = 5097.6A. LS pickup = 80796.96A 51 function is set to 4.2 A secondary, CTR=240. HS pickup = 1008A. LS pickup = 15977A 21 function (on generator) has been evaluated to PRC-025.
Note on Y55: Author: Nameplate
Note on AC55: Author: Info from Generator Data sheet, corrected for altitude.
Note on AD55: Author: See K14-76T-E5091
Note on C56: Author: See Instruction Book Photo
Note on D56: Author: See Instruction Book Photo
Note on E56: Author: See Instruction Book Photo, AMP rating given
Note on F56: Author: See 9727D20 sh1
Note on G56: Author: See U-126674-M
Note on H56: Author: Part of Gen Bkr. Reference D010208-EMAE100 and Gen Bkr Photo, rating of assembly is used since component ratings are not differentiated by manufacturer
Note on J56: Author: See nameplate picture
Note on L56: Author: See nameplate picture
Note on N56: Author: See nameplate picture
Note on O56: Author: See nameplate picture
Note on Q56: Author: See 1HC0015420
Note on R56: Author: See 9727D20 sh2
Note on S56: Author: Tap 2
Note on T56: Author: Value from Subs Eng FAC-008-3 Spreadsheet. Limiting Element: 1272 ACSR Conductor
Note on V56: Author: Delta Current rating per nameplate
Note on W56: Brady Nunn: 50 function pickup at 21.24A secondary, CTR= 240. HS pickup = 5097.6A. LS pickup = 80796.96A 51 function is set to 4.2 A secondary, CTR=240. HS pickup = 1008A. LS pickup = 15977A 21 function (on generator) has been evaluated to PRC-025.
Note on Y56: Author: Nameplate
Note on AC56: Author: Info from Generator Data sheet, corrected for altitude.
Note on AD56: Author: See K14-76T-E5091
Note on C57: Author: See Instruction Book Photo
Note on D57: Author: See Instruction Book Photo
Note on E57: Author: See Instruction Book Photo, AMP rating given
Note on F57: Author: See 9727D20 sh1
Note on G57: Author: See U-126674-M
Note on H57: Author: Part of Gen Bkr. Reference D010208-EMAE100 and Gen Bkr Photo, rating of assembly is used since component ratings are not differentiated by manufacturer
Note on J57: Author: See nameplate picture
Note on L57: Author: See nameplate picture
Note on N57: Author: See nameplate picture
Note on O57: Author: See nameplate picture
Note on Q57: Author: See 1HC0015420
Note on R57: Author: See 9727D20 sh2
Note on S57: Author: Tap 2
Note on T57: Author: Value from Subs Eng FAC-008-3 Spreadsheet. Limiting Element: 1272 ACSR Conductor
Note on V57: Author: Delta Current rating per nameplate
Note on W57: Brady Nunn: 50 function pickup at 21.24A secondary, CTR= 240. HS pickup = 5097.6A. LS pickup = 80796.96A 51 function is set to 4.2 A secondary, CTR=240. HS pickup = 1008A. LS pickup = 15977A 21 function (on generator) has been evaluated to PRC-025.
Note on Y57: Author: Nameplate
Note on AC57: Author: Info from Generator Data sheet, corrected for altitude.
Note on AD57: Author: See K14-76T-E5091
Note on C58: Author: See nameplate picture
Note on D58: Author: See nameplate picture
Note on E58: Author: See nameplate picture
Note on F58: Author: See 1778D02
Note on G58: Author: See U-126675-M
Note on H58: Author: Generator disconnect is part of transmission FAC-008
Note on J58: Author: See nameplate picture
Note on L58: Author: See nameplate picture
Note on N58: Author: See nameplate picture
Note on O58: Author: See nameplate picture. Single CT on H2 rated at 1125A
Note on Q58: Author: Generator Breakers are part of transmission FAC-008
Note on R58: Author: Generator Breakers are part of transmission FAC-008
Note on S58: Author: Tap 1
Note on T58: Author: Value from Subs Eng FAC-008-3 Spreadsheet. Limiting Element: 1272 ACSR Conductor
Note on V58: Author: Delta Current rating per nameplate
Note on W58: Brady Nunn: 50 function pickup at 33.12A secondary, CTR= 240. HS pickup = 7948.8A. LS pickup = 84177.792A 51 function is set to 8.03 A secondary, CTR=240. HS pickup = 1927.2A. LS pickup = 20409A 21 function (on generator) has been evaluated to PRC-025.
Note on Y58: Author: Nameplate
Note on AC58: Author: Info from Generator Data sheet, corrected for altitude.
Note on AD58: Author: See K14-76T-E5091
Note on C59: Author: See nameplate picture
Note on D59: Author: See nameplate picture
Note on E59: Author: See nameplate picture
Note on F59: Author: See 1778D02
Note on G59: Author: See U-126675-M
Note on H59: Author: Generator disconnect is part of transmission FAC-008
Note on J59: Author: See nameplate picture
Note on L59: Author: See nameplate picture
Note on N59: Author: See nameplate picture
Note on O59: Author: See nameplate picture. Single CT on H2 rated at 1125A
Note on Q59: Author: Generator Breakers are part of transmission FAC-008
Note on R59: Author: Generator Breakers are part of transmission FAC-008
Note on S59: Author: Tap 1
Note on T59: Author: Value from Subs Eng FAC-008-3 Spreadsheet. Limiting Element: 1272 ACSR Conductor
Note on V59: Author: Delta Current rating per nameplate
Note on W59: Author: No setting changes have been made since the acquisition of this plant
Note on Y59: Author: Nameplate
Note on AC59: Author: Info from Generator Data sheet, corrected for altitude.
Note on AD59: Author: See K14-76T-E5091
Note on C60: Author: From Generator Data sheet generator output as a function of inlet air temperature corrected for altitude. 5430' (.915 multiplier). Base capability curve at 104F used
Note on D60: Author: From Generator Data sheet.
Note on E60: Author: From Summer capability corrected for altitude. 5430' (.915 multiplier)
Note on F60: Author: See 813E895
Note on G60: Author: See 952614
Note on H60: Author: See name plate picture for DS 1512
Note on J60: Author: See nameplate picture
Note on L60: Author: See nameplate picture
Note on N60: Author: See nameplate picture
Note on O60: Author: See nameplate picture - KBS - Not Used
Note on Q60: Author: See 813E895
Note on R60: Author: See 813E895
Note on S60: Author: Tap C
Note on T60: Author: Value from Subs Eng FAC-008-3 Spreadsheet. Limiting element: Breaker CTs
Note on V60: Author: Nameplate is at 60MVA so a calculation is used.
Note on W60: Brady Nunn: 50 function pickup at 27.4A secondary, CTR= 160. HS pickup = 4384A. LS pickup = 38184.6A 51 function is set to 4.3 A secondary, CTR=160. HS pickup = 688A. LS pickup = 5992.5A 21 function (on generator) has been evaluated to PRC-025.
Note on Y60: Author: Nameplate shows capability at 55F rating, this is calculated using KVA for 65F rating at 62700KVA
Note on AC60: Author: Info from Generator Data sheet, corrected for altitude.
Note on AD60: Author: See K14-76T-E5091
Note on C61: Author: From Generator Data sheet generator output as a function of inlet air temperature corrected for altitude. 5430' (.915 multiplier) Base capability curve at 0F used
Note on D61: Author: From Generator Data sheet.
Note on E61: Author: From Winter capability corrected for altitude. 5430' (.915 multiplier)
Note on F61: Author: See 813E895
Note on G61: Author: See 952614
Note on H61: Author: See name plate picture for DS 1512
Note on J61: Author: See nameplate picture
Note on L61: Author: See nameplate picture
Note on N61: Author: See nameplate picture
Note on O61: Author: See nameplate picture KBS - Not Used
Note on Q61: Author: See 813E895
Note on R61: Author: See 813E895
Note on S61: Author: Tap C
Note on T61: Author: Value from Subs Eng FAC-008-3 Spreadsheet. Limiting Element: Breaker CTs
Note on V61: Author: Nameplate is at 60MVA so a calculation is used.
Note on W61: Brady Nunn: 50 function pickup at 27.4A secondary, CTR= 160. HS pickup = 4384A. LS pickup = 38184.6A 51 function is set to 4.3 A secondary, CTR=160. HS pickup = 688A. LS pickup = 5992.5A 21 function (on generator) has been evaluated to PRC-025.
Note on Y61: Author: Nameplate shows capability at OA rating, this is calculated using KVA for FOA rating at 62700KVA
Note on AC61: Author: Info from Generator Data sheet, corrected for altitude.
Note on AD61: Author: See K14-76T-E5091
Note on C62: Author: Variation of generator output with air inlet temp at 104F (40C) accounted for PF (0.8 curve) Altitude adjustment 5430' (.915 multiplier)
Note on F62: Author: D001449-100E100 SH1
Note on G62: Author: Drawing D001449-500E001 8 MV-105 750 KCMIL conductors in underground electrical ducts. 375A *8 = 3000A per 2008 NEC table 310.77. Reference Valmont Facility Rating Assessment 5" AL Pipe: 3850 A - Reference XEL-EVD-Facility Rating Supplement-Table-Tubular and Square Conductor.xls 3x750 KCMIL open air conductors. Reference XEL-EVD-Facility Rating Supllement - Table - Bare Overhead Condctor.xls. Spacing Unknown, assume de-rated (more limiting). 2717A. Gen Bus Section Most limiting: 2717A
Note on J62: Author: Nameplate photo. 3 winding transformer, generator rating corresponds to LS winding connected to generator
Note on N62: Author: Reference Nameplate Photo
Note on Q62: Author: M991081-510E003 S01 and D001449-100E100 SH1
Note on R62: Author: M991081-510E003 S01 and D001449-100E100 SH1
Note on T62: Author: see sheet 2
Note on V62: Author: Reflects nameplate value on GSU
Note on W62: Author: GSU SEL-387. 51 set at 5.25 A secondary. CTR=120. 5.25*120=630A Primary on high side of GSU. Low side calc performed in cell. 51LT relay: 51 set at 160%, 160%*600 = 960A primary on high side of GSU. Less limiting than SEL-387
Note on C63: Author: Variation of generator output with air inlet temp at 0F (-17.778C) accounted for PF Altitude adjustment 5430' (.915 multiplier)
Note on F63: Author: D001449-100E100 SH1
Note on G63: Author: Drawing D001449-500E001 8 MV-105 750 KCMIL conductors in underground electrical ducts. 375A *8 = 3000A per 2008 NEC table 310.77. Reference Valmont Facility Rating Assessment 5" AL Pipe: 3850 A - Reference XEL-EVD-Facility Rating Supplement-Table-Tubular and Square Conductor.xls 3x750 KCMIL open air conductors. Reference XEL-EVD-Facility Rating Supllement - Table - Bare Overhead Condctor.xls. Spacing Unknown, assume de-rated (more limiting). 3237A. Gen Bus Section Most limiting: 3237A
Note on V63: Author: Reflects nameplate value on GSU
Note on C64: Author: Variation of generator output with air inlet temp at 104F (40C) accounted for PF (0.8 curve) Altitude adjustment 5430' (.915 multiplier)
Note on F64: Author: D001449-100E100 SH1
Note on G64: Author: Drawing D001449-500E001 8 MV-105 750 KCMIL conductors in underground electrical ducts. 375A *8 = 3000A per 2008 NEC table 310.77. Reference Valmont Facility Rating Assessment 5" AL Pipe: 3850 A - Reference XEL-EVD-Facility Rating Supplement-Table-Tubular and Square Conductor.xls 3x750 KCMIL open air conductors. Reference XEL-EVD-Facility Rating Supllement - Table - Bare Overhead Condctor.xls. Spacing Unknown, assume de-rated (more limiting). 3237A. Gen Bus Section Most limiting: 3237A
Note on V64: Author: Reflects nameplate value on GSU
Note on C65: Author: Variation of generator output with air inlet temp at 0F (-17.778C) accounted for PF Altitude adjustment 5430' (.915 multiplier)
Note on F65: Author: D001449-100E100 SH1
Note on G65: Author: Drawing D001449-500E001 8 MV-105 750 KCMIL conductors in underground electrical ducts. 375A *8 = 3000A per 2008 NEC table 310.77. Reference Valmont Facility Rating Assessment 5" AL Pipe: 3850 A - Reference XEL-EVD-Facility Rating Supplement-Table-Tubular and Square Conductor.xls 3x750 KCMIL open air conductors. Reference XEL-EVD-Facility Rating Supllement - Table - Bare Overhead Condctor.xls. Spacing Unknown, assume de-rated (more limiting). 3237A. Gen Bus Section Most limiting: 3237A
Note on J65: Author: Nameplate photo. 3 winding transformer, generator rating corresponds to LS winding connected to generator
Note on N65: Author: Reference Nameplate Photo
Note on Q65: Author: M991081-510E003 S01 and D001449-100E100 SH1
Note on R65: Author: M991081-510E003 S01 and D001449-100E100 SH1
Note on T65: Author: see sheet 2
Note on V65: Author: Reflects nameplate value on GSU
Note on W65: Author: GSU SEL-387. 51 set at 5.25 A secondary. CTR=120. 5.25*120=630A Primary on high side of GSU. Low side calc performed in cell. 51LT relay: 51 set at 160%, 160%*600 = 960A primary on high side of GSU. Less limiting than SEL-387
Note on Y66: Author: Nameplate
Note on G67: Author: No Common Bus. Transformer is a 3 winding transformer.
Note on H67: Author: No Common Bus. Transformer is a 3 winding transformer.
Note on J67: Author: Nameplate Photo. HS winding rating
Note on T67: Author: see sheet 2
Note on W67: Author: GSU SEL-387. 51 set at 5.25 A secondary. CTR=120. 5.25*120=630A Primary on high side of GSU. Low side calc performed in cell. 51LT relay: 51 set at 160%, 160%*600 = 960A primary on high side of GSU. Less limiting than SEL-387
Note on Y67: Author: From Nameplate at 115kV

## E.S. Wind Farms
PSCo Region Energy Supply Facility Equipment Ratings - Wind Farms
Plant/Site | Unit | Unit Type | Combined MVA | Transformer HS kV | Transformer LS kV | Most Limiting Equipment |  |  | Next Most Limiting Equipment
[6 empty] | HS of Xfmr Limiting Current | LS of Xfmr Limiting Current | Limiting Electrical Equipment | HS of Xfmr Limiting Current | LS of Xfmr Limiting Current | Limiting Electrical Equipment
Rush Creek 1 | 1101A | 34.5 kV Feeder | 27.0821 | 345 | 34.5 | 45.3214 | 453.2136 | Combined Equip MVA | 47.32 | 473.2 | Underground Cable
| 1101B | 34.5 kV Feeder | 20.8324 | 345 | 34.5 | 34.8626 | 348.6259 | Combined Equip MVA | 36.15 | 361.5 | Underground Cable
| 1101 | 34.5 kV Collector | 47.9145 | 345 | 34.5 | 80.1839 | 801.8395 | Combined Equip MVA | 120 | 1200 | Reactor
| 1102A | 34.5 kV Feeder | 27.3791 | 345 | 34.5 | 45.8184 | 458.1839 | Combined Equip MVA | 46.84 | 468.4 | Underground Cable
| 1102B | 34.5 kV Feeder | 27.3791 | 345 | 34.5 | 45.8184 | 458.1839 | Combined Equip MVA | 46.84 | 468.4 | Underground Cable
| 1102 | 34.5 kV Collector | 54.7582 | 345 | 34.5 | 91.6368 | 916.3678 | Combined Equip MVA | 120 | 1200 | Reactor*
| 1103A | 34.5 kV Feeder | 27.3791 | 345 | 34.5 | 45.8184 | 458.1839 | Combined Equip MVA | 46.84 | 468.4 | Underground Cable
| 1103B | 34.5 kV Feeder | 27.3791 | 345 | 34.5 | 45.8184 | 458.1839 | Combined Equip MVA | 46.84 | 468.4 | Underground Cable
| 1103 | 34.5 kV Collector | 54.7582 | 345 | 34.5 | 91.6368 | 916.3678 | Combined Equip MVA | 120 | 1200 | Reactor*
| 1104A | 34.5 kV Feeder | 27.3791 | 345 | 34.5 | 45.8184 | 458.1839 | Combined Equip MVA | 46.84 | 468.4 | Underground Cable
| 1104B | 34.5 kV Feeder | 27.3791 | 345 | 34.5 | 45.8184 | 458.1839 | Combined Equip MVA | 46.84 | 468.4 | Underground Cable
| 1104 | 34.5 kV Collector | 54.7582 | 345 | 34.5 | 91.6368 | 916.3678 | Combined Equip MVA | 120 | 1200 | Reactor*
| C1153 | Cap Bank Feeder | 21.7 | 345 | 34.5 | 36.3145 | 363.145 | Combined Equip MVA | 60 | 600 | Switcher
| C1154 | Cap Bank Feeder | 21.7 | 345 | 34.5 | 36.3145 | 363.145 | Combined Equip MVA | 60 | 600 | Switcher
| C1155 | Cap Bank Feeder | 21.7 | 345 | 34.5 | 36.3145 | 363.145 | Combined Equip MVA | 60 | 600 | Switcher
| 1150C | Capacitor Switch Feeder | 65.1 | 345 | 34.5 | 108.9435 | 1089.4349 | Combined Equip MVA | 147.1 | 1471 | Relay Trip Setpoint
| R1151 | Reactor Feeder | 23 | 345 | 34.5 | 38.49 | 384.9002 | Combined Equip MVA | 60 | 600 | Switcher
| R1152 | Reactor Feeder | 23 | 345 | 34.5 | 38.49 | 384.9002 | Combined Equip MVA | 60 | 600 | Switcher
| 1150R | Reactor Switch Feeder | 46 | 345 | 34.5 | 76.98 | 769.8004 | Combined Equip MVA | 77 | 770 | Underground Cable
| 1150 | 34.5 kV Capacitor/Reactor Collector | 65.1 | 345 | 34.5 | 108.9435 | 1089.4349 | Combined Equip MVA | 147.1 | 1471 | Relay Trip Setpoint
| 1201A | 34.5 kV Feeder | 27.3551 | 345 | 34.5 | 45.7782 | 457.7817 | Combined Equip MVA | 47.32 | 473.2 | Underground Cable
| 1201B | 34.5 kV Feeder | 27.3076 | 345 | 34.5 | 45.6987 | 456.9872 | Combined Equip MVA | 47.32 | 473.2 | Underground Cable
| 1201 | 34.5 kV Collector | 54.6627 | 345 | 34.5 | 91.4769 | 914.7689 | Combined Equip MVA | 120 | 1200 | Reactor*
| 1202A | 34.5 kV Feeder | 27.3791 | 345 | 34.5 | 45.8184 | 458.1839 | Combined Equip MVA | 47.32 | 473.2 | Underground Cable
| 1202B | 34.5 kV Feeder | 23.167 | 345 | 34.5 | 38.7694 | 387.6941 | Combined Equip MVA | 40.36 | 403.6 | Underground Cable
| 1202 | 34.5 kV Collector | 50.5461 | 345 | 34.5 | 84.5878 | 845.878 | Combined Equip MVA | 120 | 1200 | Reactor*
| 1203 Feeder | 34.5 kV Feeder | 27.3791 | 345 | 34.5 | 45.8184 | 458.1839 | Combined Equip MVA | 47.32 | 473.2 | Underground Cable
| 1203 Breaker | 34.5 kV Collector | 27.3791 | 345 | 34.5 | 45.8184 | 458.1839 | Combined Equip MVA | 120 | 1200 | Reactor*
| 1204A | 34.5 kV Feeder | 27.3791 | 345 | 34.5 | 45.8184 | 458.1839 | Combined Equip MVA | 47.32 | 473.2 | Underground Cable
| 1204B | 34.5 kV Feeder | 27.3076 | 345 | 34.5 | 45.6987 | 456.9872 | Combined Equip MVA | 47.32 | 473.2 | Underground Cable
| 1204 | 34.5 kV Collector | 54.6867 | 345 | 34.5 | 91.5171 | 915.1711 | Combined Equip MVA | 120 | 1200 | Reactor
| C1253 | Cap Bank Feeder | 21.7 | 345 | 34.5 | 36.3145 | 363.145 | Combined Equip MVA | 60 | 600 | Switcher
| C1254 | Cap Bank Feeder | 21.7 | 345 | 34.5 | 36.3145 | 363.145 | Combined Equip MVA | 60 | 600 | Switcher
| C1255 | Cap Bank Feeder | 21.7 | 345 | 34.5 | 36.3145 | 363.145 | Combined Equip MVA | 60 | 600 | Switcher
| 1250C | Capacitor Switch Feeder | 65.1 | 345 | 34.5 | 108.9435 | 1089.4349 | Combined Equip MVA | 147.1 | 1471 | Relay Trip Setpoint
| R1251 | Reactor Feeder | 23 | 345 | 34.5 | 38.49 | 384.9002 | Combined Equip MVA | 38.5 | 385 | Underground Cable
| 1250R | Reactor Switch Feeder | 23 | 345 | 34.5 | 38.49 | 384.9002 | Combined Equip MVA | 38.5 | 385 | Underground Cable
| 1250 | 34.5 kV Capacitor/Reactor Collector | 65.1 | 345 | 34.5 | 108.9435 | 1089.4349 | Combined Equip MVA | 147.1 | 1471 | Relay Trip Setpoint
| 1001M | Collector Tie Switch | 238.0322 | 345 | 34.5 | 398.3419 | 3983.4195 | Combined Equip MVA | 415.035 | 4150.3498 | Main Power Transformer
| XFMR T1 - Normal | Main Power Transformer-Normal | 238.0322 | 345 | 34.5 | 398.3419 | 3983.4195 | Combined Equip MVA | 415.035 | 4150.3498 | Main Power Transformer
| XFMR T2 - Normal | Main Power Transformer-Normal | 215.8313 | 345 | 34.5 | 361.1891 | 3611.8909 | Combined Equip MVA | 415.035 | 4150.3498 | Main Power Transformer
| XFMR T1 - Bus Tie | Main Power Transformer-Tie | 362.542 | 345 | 34.5 | 415.035 | 4150.3498 | Main Power Transformer | 450 | 4500 | Metering CT
| XFMR T2 - Bus Tie | Main Power Transformer-Tie | 362.542 | 345 | 34.5 | 415.035 | 4150.3498 | Main Power Transformer | 450 | 4500 | Metering CT
| RCW1 | Combined Rush Creek 1 Rating | 457.2976 | 345 | 34.5 | 765.278 | 7652.7795 | Combined Equip MVA | 830.07 | 8300.6995 | Main Power Transformer
Rush Creek 2 | 2101A | 34.5 kV Feeder | 4.2122 | 345 | 34.5 | 7.049 | 70.4898 | Combined Equip MVA | 23.25 | 232.5 | Underground Cable
| 2101B | 34.5 kV Feeder | 23.167 | 345 | 34.5 | 38.7694 | 387.6941 | Combined Equip MVA | 40.38 | 403.8 | Underground Cable
| 2101A/B | 34.5 kV Feeder | 27.3791 | 345 | 34.5 | 45.8184 | 458.1839 | Combined Equip MVA | 120 | 1200 | Disconnect Switch*
| 2101C | 34.5 kV Feeder | 23.167 | 345 | 34.5 | 38.7694 | 387.6941 | Combined Equip MVA | 40.38 | 403.8 | Underground Cable
| 2101 | 34.5 kV Collector | 50.5461 | 345 | 34.5 | 84.5878 | 845.878 | Combined Equip MVA | 120 | 1200 | Reactor
| 2102A | 34.5 kV Feeder | 23.167 | 345 | 34.5 | 38.7694 | 387.6941 | Combined Equip MVA | 40.38 | 403.8 | Underground Cable
| 2102B | 34.5 kV Feeder | 23.167 | 345 | 34.5 | 38.7694 | 387.6941 | Combined Equip MVA | 40.38 | 403.8 | Underground Cable
| 2102 | 34.5 kV Collector | 46.3339 | 345 | 34.5 | 77.5388 | 775.3881 | Combined Equip MVA | 120 | 1200 | Reactor*
| 2103A | 34.5 kV Feeder | 23.167 | 345 | 34.5 | 38.7694 | 387.6941 | Combined Equip MVA | 40.38 | 403.8 | Underground Cable
| 2103B | 34.5 kV Feeder | 16.8487 | 345 | 34.5 | 28.1959 | 281.9593 | Combined Equip MVA | 30.92 | 309.2 | Underground Cable
| 2103 | 34.5 kV Collector | 40.0156 | 345 | 34.5 | 66.9653 | 669.6534 | Combined Equip MVA | 120 | 1200 | Reactor*
| 2104A | 34.5 kV Feeder | 21.0609 | 345 | 34.5 | 35.2449 | 352.4491 | Combined Equip MVA | 36.45 | 364.5 | Underground Cable
| 2104B | 34.5 kV Feeder | 21.0609 | 345 | 34.5 | 35.2449 | 352.4491 | Combined Equip MVA | 36.45 | 364.5 | Underground Cable
| 2104 | 34.5 kV Collector | 42.1217 | 345 | 34.5 | 70.4898 | 704.8983 | Combined Equip MVA | 120 | 1200 | Reactor*
| 2105A | 34.5 kV Feeder | 23.167 | 345 | 34.5 | 38.7694 | 387.6941 | Combined Equip MVA | 40.38 | 403.8 | Underground Cable
| 2105B | 34.5 kV Feeder | 23.167 | 345 | 34.5 | 38.7694 | 387.6941 | Combined Equip MVA | 40.38 | 403.8 | Underground Cable
| 2105C | 34.5 kV Feeder | 6.3183 | 345 | 34.5 | 10.5735 | 105.7347 | Combined Equip MVA | 23.25 | 232.5 | Underground Cable
| 2105B/C | 34.5 kV Feeder | 29.4852 | 345 | 34.5 | 49.3429 | 493.4288 | Combined Equip MVA | 120 | 1200 | Disconnect Switch*
| 2105 | 34.5 kV Collector | 52.6522 | 345 | 34.5 | 88.1123 | 881.1229 | Combined Equip MVA | 120 | 1200 | Reactor*
| C2153 | Cap Bank Feeder | 17 | 345 | 34.5 | 28.4491 | 284.4914 | Combined Equip MVA | 60 | 600 | Switcher
| C2154 | Cap Bank Feeder | 17 | 345 | 34.5 | 28.4491 | 284.4914 | Combined Equip MVA | 60 | 600 | Switcher
| C2155 | Cap Bank Feeder | 17 | 345 | 34.5 | 28.4491 | 284.4914 | Combined Equip MVA | 60 | 600 | Switcher
| 2150C | Capacitor Switch Feeder | 51 | 345 | 34.5 | 85.3474 | 853.4743 | Combined Equip MVA | 114.3 | 1143 | Underground Cable
| R2151 | Reactor Feeder | 24 | 345 | 34.5 | 40.1635 | 401.635 | Combined Equip MVA | 60 | 600 | Switcher
| R2152 | Reactor Feeder | 24 | 345 | 34.5 | 40.1635 | 401.635 | Combined Equip MVA | 60 | 600 | Switcher
| 2150R | Reactor Switch Feeder | 48 | 345 | 35.5 | 82.6553 | 803.2699 | Combined Equip MVA | 82.9362 | 806 | Underground Cable
| 2150 | 34.5 kV Capacitor/Reactor Collector | 51 | 345 | 34.5 | 85.3474 | 853.4743 | Combined Equip MVA | 123 | 1230 | Relay Trip Setpoint
| XFMR T1 | Main Power Transformer | 252.3429 | 345 | 34.5 | 415.035 | 4150.3498 | Main Power Transformer | 422.2906 | 4222.9062 | Combined Equip MVA
| RCW2 | Combined Rush Creek 2 Rating | 252.3429 | 345 | 34.5 | 415.035 | 4150.3498 | Main Power Transformer | 422.2906 | 4222.9062 | Combined Equip MVA
Cheyenne Ridge East | 2101A | 34.5 kV Feeder | 23.6104 | 345 | 34.5 | 39.5115 | 395.1147 | Combined Equip MVA | 42.29 | 422.9 | Underground Cable
| 2101B | 34.5 kV Feeder | 23.1576 | 345 | 34.5 | 38.7537 | 387.537 | Combined Equip MVA | 42.29 | 422.9 | Underground Cable
| 2101 | 34.5 kV Collector | 46.7679 | 345 | 34.5 | 78.2652 | 782.6517 | Combined Equip MVA | 101.4 | 1014 | Jumper: DS to Main Bus*
| 2102A | 34.5 kV Feeder | 23.6104 | 345 | 34.5 | 39.5115 | 395.1147 | Combined Equip MVA | 42.29 | 422.9 | Underground Cable
| 2102B | 34.5 kV Feeder | 22.9156 | 345 | 34.5 | 38.3488 | 383.4884 | Combined Equip MVA | 42.29 | 422.9 | Underground Cable
| 2102 | 34.5 kV Collector | 46.526 | 345 | 34.5 | 77.8603 | 778.6031 | Combined Equip MVA | 101.4 | 1014 | Jumper: DS to Main Bus*
| 2103A | 34.5 kV Feeder | 9.263 | 345 | 34.5 | 15.5015 | 155.0148 | Combined Equip MVA | 31.66 | 316.6 | Underground Cable
| 2103B | 34.5 kV Feeder | 23.1576 | 345 | 34.5 | 38.7537 | 387.537 | Combined Equip MVA | 42.29 | 422.9 | Underground Cable
| 2103 | 34.5 kV Collector | 32.4206 | 345 | 34.5 | 54.2552 | 542.5518 | Combined Equip MVA | 101.4 | 1014 | Jumper: DS to Main Bus*
| C2152 | Cap Bank Feeder | 12.5 | 345 | 34.5 | 20.9185 | 209.1849 | Combined Equip MVA | 20.9185 | 209.1849 | Jumper: Cap to Switcher
| C2153 | Cap Bank Feeder | 12.5 | 345 | 34.5 | 20.9185 | 209.1849 | Combined Equip MVA | 20.9185 | 209.1849 | Jumper: Cap to Switcher
| C2150 | Capacitor Switch Feeder | 25 | 345 | 34.5 | 41.837 | 418.3698 | Combined Equip MVA | 63.6 | 636 | Relay Amps
| R2151 | Reactor Feeder | 13 | 345 | 34.5 | 21.7552 | 217.5523 | Combined Equip MVA | 60 | 600 | Switcher
| R2150 | Reactor Switch Feeder | 13 | 345 | 34.5 | 21.7552 | 217.5523 | Combined Equip MVA | 63.6 | 636 | Relay Amps
| 2150 | 34.5 kV Capacitor/Reactor Collector | 25 | 345 | 34.5 | 41.837 | 418.3698 | Combined Equip MVA | 63.6 | 636 | Relay Amps
| 2201A | 34.5 kV Feeder | 23.1576 | 345 | 34.5 | 38.7537 | 387.537 | Combined Equip MVA | 42.29 | 422.9 | Underground Cable
| 2201B | 34.5 kV Feeder | 23.1576 | 345 | 34.5 | 38.7537 | 387.537 | Combined Equip MVA | 42.29 | 422.9 | Underground Cable
| 2201 | 34.5 kV Collector | 46.3151 | 345 | 34.5 | 77.5074 | 775.0741 | Combined Equip MVA | 101.4 | 1014 | Jumper: DS to Main Bus*
| 2202B | 34.5 kV Feeder | 23.1576 | 345 | 34.5 | 38.7537 | 387.537 | Combined Equip MVA | 42.29 | 422.9 | Underground Cable
| 2202 | 34.5 kV Collector | 23.1576 | 345 | 34.5 | 38.7537 | 387.537 | Combined Equip MVA | 101.4 | 1014 | Jumper: DS to Main Bus*
| 2203A | 34.5 kV Feeder | 23.1576 | 345 | 34.5 | 38.7537 | 387.537 | Combined Equip MVA | 42.29 | 422.9 | Underground Cable
| 2203B | 34.5 kV Feeder | 23.1576 | 345 | 34.5 | 38.7537 | 387.537 | Combined Equip MVA | 42.29 | 422.9 | Underground Cable
| 2203 | 34.5 kV Collector | 46.3151 | 345 | 34.5 | 77.5074 | 775.0741 | Combined Equip MVA | 101.4 | 1014 | Jumper: DS to Main Bus*
| C2252 | Cap Bank Feeder | 12.5 | 345 | 34.5 | 20.9185 | 209.1849 | Combined Equip MVA | 20.9185 | 209.1849 | Jumper: Cap to Switcher
| C2253 | Cap Bank Feeder | 12.5 | 345 | 34.5 | 20.9185 | 209.1849 | Combined Equip MVA | 20.9185 | 209.1849 | Jumper: Cap to Switcher
| C2250 | Capacitor Switch Feeder | 25 | 345 | 34.5 | 41.837 | 418.3698 | Combined Equip MVA | 63.6 | 636 | Relay Amps
| R2251 | Reactor Feeder | 13 | 345 | 34.5 | 21.7552 | 217.5523 | Combined Equip MVA | 60 | 600 | Switcher
| R2250 | Reactor Switch Feeder | 25 | 345 | 34.5 | 21.7552 | 217.5523 | Combined Equip MVA | 63.6 | 636 | Relay Amps
| 2250 | 34.5 kV Capacitor/Reactor Collector | 25 | 345 | 34.5 | 41.837 | 418.3698 | Combined Equip MVA | 63.6 | 636 | Relay Amps
| 2001 | Collector Tie | 133.1306 | 345 | 34.5 | 222.7912 | 2227.9125 | Combined Equip MVA | 261.0627 | 2610.6273 | Main Power Transformer
| TR1 | Main Power Transformer-Normal | 133.1306 | 345 | 34.5 | 222.7912 | 2227.9125 | Combined Equip MVA | 261.0627 | 2610.6273 | Main Power Transformer
| TR2 | Main Power Transformer-Normal | 125.8544 | 345 | 34.5 | 210.6147 | 2106.1465 | Combined Equip MVA | 261.0627 | 2610.6273 | Main Power Transformer
| TR1 | Main Power Transformer-Tie | 258.985 | 345 | 34.5 | 261.0627 | 2610.6273 | Main Power Transformer | 524 | 5240 | LS XFMR CT
| TR2 | Main Power Transformer-Tie | 258.985 | 345 | 34.5 | 261.0627 | 2610.6273 | Main Power Transformer | 524 | 5240 | LS XFMR CT
| CYRE | Combined Cheyenne Ridge East Rating | 258.985 | 345 | 34.5 | 433.4059 | 4334.059 | Combined Equip MVA | 522.2 | 5222 | Main Power Transformer
Cheyenne Ridge West | 1101A | 34.5 kV Feeder | 18.5261 | 345 | 34.5 | 31.003 | 310.0296 | Combined Equip MVA | 34.86 | 348.6 | Underground Cable
| 1101B | 34.5 kV Feeder | 18.5261 | 345 | 34.5 | 31.003 | 310.0296 | Combined Equip MVA | 34.86 | 348.6 | Underground Cable
| 1101C | 34.5 kV Feeder | 16.2103 | 345 | 34.5 | 27.1276 | 271.2759 | Combined Equip MVA | 34.86 | 348.6 | Underground Cable
| 1101 | 34.5 kV Collector | 53.2624 | 345 | 34.5 | 89.1335 | 891.3352 | Combined Equip MVA | 101.4 | 1014 | Jumper: DS to Main Bus*
| 1102A | 34.5 kV Feeder | 18.5261 | 345 | 34.5 | 31.003 | 310.0296 | Combined Equip MVA | 34.86 | 348.6 | Underground Cable
| 1102B | 34.5 kV Feeder | 18.5261 | 345 | 34.5 | 31.003 | 310.0296 | Combined Equip MVA | 34.86 | 348.6 | Underground Cable
| 1102 | 34.5 kV Collector | 37.0521 | 345 | 34.5 | 62.0059 | 620.0592 | Combined Equip MVA | 101.4 | 1014 | Jumper: DS to Main Bus*
| 1103A | 34.5 kV Feeder | 16.2103 | 345 | 34.5 | 27.1276 | 271.2759 | Combined Equip MVA | 34.86 | 348.6 | Underground Cable
| 1103B | 34.5 kV Feeder | 18.5261 | 345 | 34.5 | 31.003 | 310.0296 | Combined Equip MVA | 34.86 | 348.6 | Underground Cable
| 1103C | 34.5 kV Feeder | 18.5261 | 345 | 34.5 | 31.003 | 310.0296 | Combined Equip MVA | 42.29 | 422.9 | Underground Cable
| 1103 | 34.5 kV Collector | 53.2624 | 345 | 34.5 | 89.1335 | 891.3352 | Combined Equip MVA | 101.4 | 1014 | Jumper: DS to Main Bus*
| C1152 | Cap Bank Feeder | 16.5 | 345 | 34.5 | 27.6124 | 276.124 | Combined Equip MVA | 27.6124 | 276.124 | Jumper: Cap to Switcher
| C1153 | Cap Bank Feeder | 16.5 | 345 | 34.5 | 27.6124 | 276.124 | Combined Equip MVA | 27.6124 | 276.124 | Jumper: Cap to Switcher
| C1150 | Capacitor Switch Feeder | 33 | 345 | 34.5 | 55.2248 | 552.2481 | Combined Equip MVA | 79.6 | 796 | Relay Amps
| R1151 | Reactor Feeder | 12 | 345 | 34.5 | 20.0817 | 200.8175 | Combined Equip MVA | 60 | 600 | Switcher
| R1150 | Reactor Switch Feeder | 12 | 345 | 34.5 | 20.0817 | 200.8175 | Combined Equip MVA | 79.6 | 796 | Relay Amps
| 1150 | 34.5 kV Capacitor/Reactor Collector | 33 | 345 | 34.5 | 55.2248 | 552.2481 | Combined Equip MVA | 79.6 | 796 | Relay Amps
| 1201A | 34.5 kV Feeder | 23.1576 | 345 | 34.5 | 38.7537 | 387.537 | Combined Equip MVA | 42.29 | 422.9 | Underground Cable
| 1201B | 34.5 kV Feeder | 23.1576 | 345 | 34.5 | 38.7537 | 387.537 | Combined Equip MVA | 42.29 | 422.9 | Underground Cable
| 1201 | 34.5 kV Collector | 46.3151 | 345 | 34.5 | 77.5074 | 775.0741 | Combined Equip MVA | 101.4 | 1014 | Jumper: DS to Main Bus*
| 1202A | 34.5 kV Feeder | 23.1576 | 345 | 34.5 | 38.7537 | 387.537 | Combined Equip MVA | 42.29 | 422.9 | Underground Cable
| 1202B | 34.5 kV Feeder | 23.1576 | 345 | 34.5 | 38.7537 | 387.537 | Combined Equip MVA | 42.29 | 422.9 | Underground Cable
| 1202 | 34.5 kV Collector | 46.3151 | 345 | 34.5 | 77.5074 | 775.0741 | Combined Equip MVA | 101.4 | 1014 | Jumper: DS to Main Bus*
| 1203A | 34.5 kV Feeder | 23.1576 | 345 | 34.5 | 38.7537 | 387.537 | Combined Equip MVA | 42.29 | 422.9 | Underground Cable
| 1203B | 34.5 kV Feeder | 23.1576 | 345 | 34.5 | 38.7537 | 387.537 | Combined Equip MVA | 42.29 | 422.9 | Underground Cable
| 1203 | 34.5 kV Collector | 46.3151 | 345 | 34.5 | 77.5074 | 775.0741 | Combined Equip MVA | 101.4 | 1014 | Jumper: DS to Main Bus*
| C1252 | Cap Bank Feeder | 16.5 | 345 | 34.5 | 27.6124 | 276.124 | Combined Equip MVA | 27.6124 | 276.124 | Jumper: Cap to Switcher
| C1253 | Cap Bank Feeder | 16.5 | 345 | 34.5 | 27.6124 | 276.124 | Combined Equip MVA | 27.6124 | 276.124 | Jumper: Cap to Switcher
| C1250 | Capacitor Switch Feeder | 33 | 345 | 34.5 | 55.2248 | 552.2481 | Combined Equip MVA | 79.6 | 796 | Relay Amps
| R1251 | Reactor Feeder | 12 | 345 | 34.5 | 20.0817 | 200.8175 | Combined Equip MVA | 60 | 600 | Switcher
| R1250 | Reactor Switch Feeder | 12 | 345 | 34.5 | 20.0817 | 200.8175 | Combined Equip MVA | 79.6 | 796 | Relay Amps
| 1250 | 34.5 kV Capacitor/Reactor Collector | 33 | 345 | 34.5 | 55.2248 | 552.2481 | Combined Equip MVA | 79.6 | 796 | Relay Amps
| 1001 | Collector Tie | 157.0409 | 345 | 34.5 | 261.0627 | 2610.6273 | Main Power Transformer | 262.8047 | 2628.0467 | Combined Equip MVA
| TR1 | Main Power Transformer-Normal | 157.0409 | 345 | 34.5 | 261.0627 | 2610.6273 | Main Power Transformer | 262.8047 | 2628.0467 | Combined Equip MVA
| TR2 | Main Power Transformer-Normal | 152.5054 | 345 | 34.5 | 255.2146 | 2552.1463 | Combined Equip MVA | 261.0627 | 2610.6273 | Main Power Transformer
| TR1 | Main Power Transformer-Tie | 309.5463 | 345 | 34.5 | 261.0627 | 2610.6273 | Main Power Transformer | 524 | 5240 | LS XFMR CT
| TR2 | Main Power Transformer-Tie | 309.5463 | 345 | 34.5 | 261.0627 | 2610.6273 | Main Power Transformer | 524 | 5240 | LS XFMR CT
| CYRW | Combined Cheyenne Ridge West Rating | 309.5463 | 345 | 34.5 | 518.0193 | 5180.193 | Combined Equip MVA | 522.2 | 5222 | Main Power Transformer
Cheyenne Ridge Overall | CYR | Combined Overall Rating - Cheyenne Ridge | 568.5313 | 345 | 34.5 | 951.4252 | 9514.2519 | Combined Equip MVA | 1200 | 12000 | Disconnect*
Notes:
* Indicates multiple pieces of equipment at that rating
TEMP Indicates temporary equipment deratings
L7191, L7132, L7107 ratings provided on Rush Creek and Cheyenne Ridge base kv (34.5 kV) for reference. Actual system kV is 345 kV (also provided)
L7191, L7132, L7107 ratings do not include a combined generation equipment MVA value. They only consider ratings provided by Subs Engineering
Date | Revision | Change
2018-08-23 | 1 | Initial Issue
2018-09-28 | 2 | Added information for Pronghorn switching station and line to Missile site per coordination with Subs Engineering.
2019-06-20 | 3 | Updated metering CT rating for line 7107. Nex Most Limiting Element changed.
2019-09-13 | 4 | Temporary Derate of circuits 1102, 1103, and 1104 turbines and cables at Rush Creek 1. Reference PCI Constraint ID 84099
2019-11-18 | 5 | Return circuits 1102, 1103, and 1104 to normal ratings at Rush Creek 1. Reference PCI Constraint ID 84099
2020-03-30 | 6 | Addition of Shortgrass Switching Station. Changed line names to match Subs Engineering Designation. Updated L7107, L7132, L7192 value from Subs Eng.
2020-08-21 | 7 | Addition of Cheyenne Ridge East, Cheyenne Ridge West, and Cheyenne Ridge Overall
2021-08-27 | 8 | L7199, L7191, L7132, L7107, L7192, and L7131 Transferred to Transmission Documentation (removed from spreadsheet)
2023-07-13 | 9 | Updated wire rating between capacitor bank and Switcher for RCW based on manufacturer drawing.
RUSH CREEK RATING CALCULATIONS:
Wind Generator Ratings:
Mk10D |  |  | Mk10C
Wind Generator MW Rating | 2 |  | Wind Generator MW Rating | 2
Inductive (under-excited) MVAR Rating | 0.66 |  | Inductive (under-excited) MVAR Rating | 0.583
Capacitive (over-excited) MVAR Rating | 0.66 |  | Capacitive (over-excited) MVAR Rating | 0.406
Inductive MVA Rating | 2.1061 |  | Inductive MVA Rating | 2.0832
Capacitive MVA Rating | 2.1061 |  | Capacitive MVA Rating | 2.0408
Feeder Ratings
Plant | Feeder | # MK10C | #MK10D | Combined MW | Combined MVAR (Ind) | Combined MVAR (Cap) | Combined MVA | KV | Amps | Underground Cable | Jumper to Disconnect | Disconnect to Bus | Feeder Disconnect | Downstream Most Limiting Current | Downstream Next Most Limiting | Limiting Current | Most Limiting Element | Next Most Limiting Current | Next Most Limiting Element
Rush Creek 1 | 1101A | 13 | 0 | 26 | 7.579 | 5.278 | 27.0821 | 34.5 | 453.2136 | 473.2 | 1209 | 1209 | 1200 | 1200 | 1209 | 453.2136 | Combined Equip MVA | 473.2 | Underground Cable
| 1101B | 10 | 0 | 20 | 5.83 | 4.06 | 20.8324 | 34.5 | 348.6259 | 361.5 | 1209 | 1209 | 1200 | 1200 | 1209 | 348.6259 | Combined Equip MVA | 361.5 | Underground Cable
| 1102A | 0 | 13 | 26 | 8.58 | 8.58 | 27.3791 | 34.5 | 458.1839 | 468.4 | 1209 | 1209 | 1200 | 1200 | 1200 | 458.1839 | Combined Equip MVA | 468.4 | Underground Cable
| 1102B | 0 | 13 | 26 | 8.58 | 8.58 | 27.3791 | 34.5 | 458.1839 | 468.4 | 1209 | 1209 | 1200 | 1200 | 1200 | 458.1839 | Combined Equip MVA | 468.4 | Underground Cable
| 1103A | 0 | 13 | 26 | 8.58 | 8.58 | 27.3791 | 34.5 | 458.1839 | 468.4 | 1209 | 1209 | 1200 | 1200 | 1200 | 458.1839 | Combined Equip MVA | 468.4 | Underground Cable
| 1103B | 0 | 13 | 26 | 8.58 | 8.58 | 27.3791 | 34.5 | 458.1839 | 468.4 | 1209 | 1209 | 1200 | 1200 | 1200 | 458.1839 | Combined Equip MVA | 468.4 | Underground Cable
| 1104A | 0 | 13 | 26 | 8.58 | 8.58 | 27.3791 | 34.5 | 458.1839 | 468.4 | 1209 | 1209 | 1200 | 1200 | 1200 | 458.1839 | Combined Equip MVA | 468.4 | Underground Cable
| 1104B | 0 | 13 | 26 | 8.58 | 8.58 | 27.3791 | 34.5 | 458.1839 | 468.4 | 1209 | 1209 | 1200 | 1200 | 1200 | 458.1839 | Combined Equip MVA | 468.4 | Underground Cable
| 1201A | 1 | 12 | 26 | 8.503 | 8.326 | 27.3551 | 34.5 | 457.7817 | 473.2 | 1209 | 1209 | 1200 | 1200 | 1200 | 457.7817 | Combined Equip MVA | 473.2 | Underground Cable
| 1201B | 3 | 10 | 26 | 8.349 | 7.818 | 27.3076 | 34.5 | 456.9872 | 473.2 | 1209 | 1209 | 1200 | 1200 | 1200 | 456.9872 | Combined Equip MVA | 473.2 | Underground Cable
| 1202A | 0 | 13 | 26 | 8.58 | 8.58 | 27.3791 | 34.5 | 458.1839 | 473.2 | 1209 | 1209 | 1200 | 1200 | 1200 | 458.1839 | Combined Equip MVA | 473.2 | Underground Cable
| 1202B | 0 | 11 | 22 | 7.26 | 7.26 | 23.167 | 34.5 | 387.6941 | 403.6 | 1209 | 1209 | 1200 | 1200 | 1200 | 387.6941 | Combined Equip MVA | 403.6 | Underground Cable
| 1203 | 0 | 13 | 26 | 8.58 | 8.58 | 27.3791 | 34.5 | 458.1839 | 473.2 | 1209 | 1209 | 1200 | 1200 | 1200 | 458.1839 | Combined Equip MVA | 473.2 | Underground Cable
| 1204A | 0 | 13 | 26 | 8.58 | 8.58 | 27.3791 | 34.5 | 458.1839 | 473.2 | 1209 | 1209 | 1200 | 1200 | 1209 | 458.1839 | Combined Equip MVA | 473.2 | Underground Cable
| 1204B | 3 | 10 | 26 | 8.349 | 7.818 | 27.3076 | 34.5 | 456.9872 | 473.2 | 1209 | 1209 | 1200 | 1200 | 1209 | 456.9872 | Combined Equip MVA | 473.2 | Underground Cable
Rush Creek 2 | 2101A | 0 | 2 | 4 | 1.32 | 1.32 | 4.2122 | 34.5 | 70.4898 | 232.5 | 1209 | 1209 | 1200 | 1200 | 1209 | 70.4898 | Combined Equip MVA | 232.5 | Underground Cable
| 2101B | 0 | 11 | 22 | 7.26 | 7.26 | 23.167 | 34.5 | 387.6941 | 403.8 | 1209 | 1209 | 1200 | 1200 | 1209 | 387.6941 | Combined Equip MVA | 403.8 | Underground Cable
| 2101A/B | 0 | 13 | 26 | 8.58 | 8.58 | 27.3791 | 34.5 | 458.1839 | NA | 1209 | 1209 | 1200 | 1200 | 1209 | 458.1839 | Combined Equip MVA | 1200 | Disconnect Switch*
| 2101C | 0 | 11 | 22 | 7.26 | 7.26 | 23.167 | 34.5 | 387.6941 | 403.8 | 1209 | 1209 | 1200 | 1200 | 1209 | 387.6941 | Combined Equip MVA | 403.8 | Underground Cable
| 2102A | 0 | 11 | 22 | 7.26 | 7.26 | 23.167 | 34.5 | 387.6941 | 403.8 | 1209 | 1209 | 1200 | 1200 | 1200 | 387.6941 | Combined Equip MVA | 403.8 | Underground Cable
| 2102B | 0 | 11 | 22 | 7.26 | 7.26 | 23.167 | 34.5 | 387.6941 | 403.8 | 1209 | 1209 | 1200 | 1200 | 1200 | 387.6941 | Combined Equip MVA | 403.8 | Underground Cable
| 2103A | 0 | 11 | 22 | 7.26 | 7.26 | 23.167 | 34.5 | 387.6941 | 403.8 | 1209 | 1209 | 1200 | 1200 | 1200 | 387.6941 | Combined Equip MVA | 403.8 | Underground Cable
| 2103B | 0 | 8 | 16 | 5.28 | 5.28 | 16.8487 | 34.5 | 281.9593 | 309.2 | 1209 | 1209 | 1200 | 1200 | 1200 | 281.9593 | Combined Equip MVA | 309.2 | Underground Cable
| 2104A | 0 | 10 | 20 | 6.6 | 6.6 | 21.0609 | 34.5 | 352.4491 | 364.5 | 1209 | 1209 | 1200 | 1200 | 1200 | 352.4491 | Combined Equip MVA | 364.5 | Underground Cable
| 2104B | 0 | 10 | 20 | 6.6 | 6.6 | 21.0609 | 34.5 | 352.4491 | 364.5 | 1209 | 1209 | 1200 | 1200 | 1200 | 352.4491 | Combined Equip MVA | 364.5 | Underground Cable
| 2105A | 0 | 11 | 22 | 7.26 | 7.26 | 23.167 | 34.5 | 387.6941 | 403.8 | 1209 | 1209 | 1200 | 1200 | 1200 | 387.6941 | Combined Equip MVA | 403.8 | Underground Cable
| 2105B | 0 | 11 | 22 | 7.26 | 7.26 | 23.167 | 34.5 | 387.6941 | 403.8 | 1209 | 1209 | 1200 | 1200 | 1200 | 387.6941 | Combined Equip MVA | 403.8 | Underground Cable
| 2105C | 0 | 3 | 6 | 1.98 | 1.98 | 6.3183 | 34.5 | 105.7347 | 232.5 | 1209 | 1209 | 1200 | 1200 | 1200 | 105.7347 | Combined Equip MVA | 232.5 | Underground Cable
| 2105B/C | 0 | 14 | 28 | 9.24 | 9.24 | 29.4852 | 34.5 | 493.4288 | NA | 1209 | 1209 | 1200 | 1200 | 1200 | 493.4288 | Combined Equip MVA | 1200 | Disconnect Switch*
Feeder Breaker Ratings
Plant | Breaker | Combined MVA |  |  | Bus: Feeder DS to Reactor | Jumper: Bus to Reactor | Reactor | Jumper: Reactor to Bus | Bus: Jumper to DS | Jumper: DS to Breaker | Feeder Side Disconnect | Feeder Side CT | Breaker | Bus Side Disconnect | Bus Side CT | Jumper: Breaker to DS | Jumper: DS to Main Bus | Relay Trip Amps | Downstream Most Limiting Current | Downstream Next Most Limiting | Limiting Current | Most Limiting Element | Next Most Limiting Current | Limiting Element
|  |  | kV | Amps
Rush Creek 1 | 1101 | 47.9145 | 34.5 | 801.8395 | 1484 | 1209 | 1200 | 1209 | 1484 | 1209 | 2000 | 3000 | 2000 | 2000 | 3000 | 1209 | 1209 | 1300 | 4150.3498 | 4500 | 801.8395 | Combined Equip MVA | 1200 | Reactor
| 1102 | 54.7582 | 34.5 | 916.3678 | 1484 | 1209 | 1200 | 1209 | 1484 | 1209 | 1200 | 3000 | 1200 | 1200 | 3000 | 1209 | 1209 | 1300 | 4150.3498 | 4500 | 916.3678 | Combined Equip MVA | 1200 | Reactor*
| 1103 | 54.7582 | 34.5 | 916.3678 | 1484 | 1209 | 1200 | 1209 | 1484 | 1209 | 1200 | 3000 | 1200 | 1200 | 3000 | 1209 | 1209 | 1300 | 4150.3498 | 4500 | 916.3678 | Combined Equip MVA | 1200 | Reactor*
| 1104 | 54.7582 | 34.5 | 916.3678 | 1484 | 1209 | 1200 | 1209 | 1484 | 1209 | 1200 | 3000 | 1200 | 1200 | 3000 | 1209 | 1209 | 1300 | 4150.3498 | 4500 | 916.3678 | Combined Equip MVA | 1200 | Reactor*
| 1201 | 54.6627 | 34.5 | 914.7689 | 1484 | 1209 | 1200 | 1209 | 1484 | 1209 | 1200 | 3000 | 1200 | 1200 | 3000 | 1209 | 1209 | 1300 | 4150.3498 | 4500 | 914.7689 | Combined Equip MVA | 1200 | Reactor*
| 1202 | 50.5461 | 34.5 | 845.878 | 1484 | 1209 | 1200 | 1209 | 1484 | 1209 | 1200 | 3000 | 1200 | 1200 | 3000 | 1209 | 1209 | 1300 | 4150.3498 | 4500 | 845.878 | Combined Equip MVA | 1200 | Reactor*
| 1203 | 27.3791 | 34.5 | 458.1839 | 1484 | 1209 | 1200 | 1209 | 1484 | 1209 | 1200 | 3000 | 1200 | 1200 | 3000 | 1209 | 1209 | 1300 | 4150.3498 | 4500 | 458.1839 | Combined Equip MVA | 1200 | Reactor*
| 1204 | 54.6867 | 34.5 | 915.1711 | 1484 | 1209 | 1200 | 1209 | 1484 | 1209 | 2000 | 3000 | 2000 | 2000 | 3000 | 1209 | 1209 | 1300 | 4150.3498 | 4500 | 915.1711 | Combined Equip MVA | 1200 | Reactor
Rush Creek 2 | 2101 | 50.5461 | 34.5 | 845.878 | 1484 | 1209 | 1200 | 1209 | 1484 | 1209 | 2000 | 3000 | 2000 | 2000 | 3000 | 1209 | 1209 | 1250 | 4150.3498 | 4500 | 845.878 | Combined Equip MVA | 1200 | Reactor
| 2102 | 46.3339 | 34.5 | 775.3881 | 1484 | 1209 | 1200 | 1209 | 1484 | 1209 | 1200 | 3000 | 1200 | 1200 | 3000 | 1209 | 1209 | 1250 | 4150.3498 | 4500 | 775.3881 | Combined Equip MVA | 1200 | Reactor*
| 2103 | 40.0156 | 34.5 | 669.6534 | 1484 | 1209 | 1200 | 1209 | 1484 | 1209 | 1200 | 3000 | 1200 | 1200 | 3000 | 1209 | 1209 | 1250 | 4150.3498 | 4500 | 669.6534 | Combined Equip MVA | 1200 | Reactor*
| 2104 | 42.1217 | 34.5 | 704.8983 | 1484 | 1209 | 1200 | 1209 | 1484 | 1209 | 1200 | 3000 | 1200 | 1200 | 3000 | 1209 | 1209 | 1250 | 4150.3498 | 4500 | 704.8983 | Combined Equip MVA | 1200 | Reactor*
| 2105 | 52.6522 | 34.5 | 881.1229 | 1484 | 1209 | 1200 | 1209 | 1484 | 1209 | 1200 | 3000 | 1200 | 1200 | 3000 | 1209 | 1209 | 1250 | 4150.3498 | 4500 | 881.1229 | Combined Equip MVA | 1200 | Reactor*
Cap Switcher Feeder Ratings
Plant | Switcher | Combined MVA | kV | Amps | Jumper: Cap to Switcher | Switcher | Jumper: Switcher to bus | Downstream Most Limiting Current | Downstream Next Most Limiting | Limiting Current | Most Limiting Element | Next Most Limiting Current | Next Most Limiting Element
Rush Creek 1 | C1153 | 21.7 | 34.5 | 363.145 | 878 | 600 | 1209 | 1471 | 1473 | 363.145 | Combined Equip MVA | 600 | Switcher
| C1154 | 21.7 | 34.5 | 363.145 | 878 | 600 | 1209 | 1471 | 1473 | 363.145 | Combined Equip MVA | 600 | Switcher
| C1155 | 21.7 | 34.5 | 363.145 | 878 | 600 | 1209 | 1471 | 1473 | 363.145 | Combined Equip MVA | 600 | Switcher
| C1253 | 21.7 | 34.5 | 363.145 | 878 | 600 | 1209 | 1471 | 1666.2 | 363.145 | Combined Equip MVA | 600 | Switcher
| C1254 | 21.7 | 34.5 | 363.145 | 878 | 600 | 1209 | 1471 | 1666.2 | 363.145 | Combined Equip MVA | 600 | Switcher
| C1255 | 21.7 | 34.5 | 363.145 | 878 | 600 | 1209 | 1471 | 1666.2 | 363.145 | Combined Equip MVA | 600 | Switcher
Rush Creek 2 | C2153 | 17 | 34.5 | 284.4914 | 878 | 600 | 1209 | 1143 | 1230 | 284.4914 | Combined Equip MVA | 600 | Switcher
| C2154 | 17 | 34.5 | 284.4914 | 878 | 600 | 1209 | 1143 | 1230 | 284.4914 | Combined Equip MVA | 600 | Switcher
| C2155 | 17 | 34.5 | 284.4914 | 878 | 600 | 1209 | 1143 | 1230 | 284.4914 | Combined Equip MVA | 600 | Switcher
Reactor Switcher Feeder Ratings
Plant | Switcher | Combined MVA | kV | Amps | Jumper: Reactor to Bus | Bus | Jumper: Bus to switcher | Switcher | Jumper: switcher to bus | Downstream Most Limiting Current | Downstream Next Most Limiting | Limiting Current | Most Limiting Element | Next Most Limiting Current | Next Limiting Element
Rush Creek 1 | R1151 | 23 | 34.5 | 384.9002 | 1209 | 1484 | 1209 | 600 | 1209 | 770 | 1200 | 384.9002 | Combined Equip MVA | 600 | Switcher
| R1152 | 23 | 34.5 | 384.9002 | 1209 | 1484 | 1209 | 600 | 1209 | 770 | 1200 | 384.9002 | Combined Equip MVA | 600 | Switcher
| R1251 | 23 | 34.5 | 384.9002 | 1209 | 1484 | 1209 | 600 | 1209 | 385 | 1200 | 384.9002 | Combined Equip MVA | 385 | Underground Cable
Rush Creek 2 | R2151 | 24 | 34.5 | 401.635 | 1209 | 1484 | 1209 | 600 | 1209 | 806 | 1200 | 401.635 | Combined Equip MVA | 600 | Switcher
| R2152 | 24 | 34.5 | 401.635 | 1209 | 1484 | 1209 | 600 | 1209 | 806 | 1200 | 401.635 | Combined Equip MVA | 600 | Switcher
Cap Bank and Reactor Feeder Ratings
Plant | Feeder | Combined MVA | kV | Amps | Bus to Disconnect | Jumper: Bus to Disconnect | Disconnect | Underground Cable | Downstream Most Limiting Current | Downstream Next Most Limiting | Limiting Current | Most Limiting Element | Next Most Limiting Current | Next Limiting Element
Rush Creek 1 | 1150C | 65.1 | 34.5 | 1089.4349 | 1981 | 2171 | 2000 | 1473 | 1471 | 1981 | 1089.4349 | Combined Equip MVA | 1471 | Relay Trip Setpoint
| 1250C | 65.1 | 34.5 | 1089.4349 | 1981 | 2171 | 2000 | 1666.2 | 1471 | 1981 | 1089.4349 | Combined Equip MVA | 1471 | Relay Trip Setpoint
| 1150R | 46 | 34.5 | 769.8004 | 1484 | 1209 | 1200 | 770 | 1471 | 1981 | 769.8004 | Combined Equip MVA | 770 | Underground Cable
| 1250R | 23 | 34.5 | 384.9002 | 1484 | 1209 | 1200 | 385 | 1471 | 1981 | 384.9002 | Combined Equip MVA | 385 | Underground Cable
Rush Creek 2 | 2150C | 51 | 34.5 | 853.4743 | 1981 | 2171 | 2000 | 1143 | 1230 | 1981 | 853.4743 | Combined Equip MVA | 1143 | Underground Cable
| 2150R | 48 | 34.5 | 803.2699 | 1484 | 1209 | 1200 | 806 | 1230 | 1981 | 803.2699 | Combined Equip MVA | 806 | Underground Cable
Cap/Reactor Breaker Ratings
Plant | Breaker | Combined MVA | kV | Amps | Bus to Breaker | Jumper: Bus to Breaker | Feeder Side CT | Breaker | Bus Side CT | Jumper: Breaker to Disconnect | Disconnect | Jumper: DS to Bus | Relay Trip Setpoint | Downstream Most Limiting Current | Downstream Next Most Limiting | Limiting Current | Most Limiting Element | Next Most Limiting Current | Limiting Element
Rush Creek 1 | 1150 | 65.1 | 34.5 | 1089.4349 | 1981 | 2171 | 3000 | 2000 | 3000 | 2171 | 2000 | 2171 | 1471 | 4150.3498 | 4500 | 1089.4349 | Combined Equip MVA | 1471 | Relay Trip Setpoint
| 1250 | 65.1 | 34.5 | 1089.4349 | 1981 | 2171 | 3000 | 2000 | 3000 | 2171 | 2000 | 2171 | 1471 | 4150.3498 | 4500 | 1089.4349 | Combined Equip MVA | 1471 | Relay Trip Setpoint
Rush Creek 2 | 2150 | 51 | 34.5 | 853.4743 | 1981 | 2171 | 3000 | 2000 | 3000 | 2171 | 2000 | 2171 | 1230 | 4150.3498 | 4500 | 853.4743 | Combined Equip MVA | 1230 | Relay Trip Setpoint
Main Power Transformer Ratings - Normal Configuration | [45 empty] | Note: hidden cells used to calculate next most limiting element
Plant | Transformer | Combined MVA | kV | Amps | Low Side Main Bus | Jumper: Main to Bus | Bus to DS | Disconnect | Metering CT | Jumper: DS to Xfmr | LS Xfmr CTs | Xfmr MVA Rating | Xfmr HS kVolt | Xfmr LS kVolt | Xfmr Turns Ratio | Xfmr LS Current Rating | HS Xfmr CTs | LS value of HS CTs | Jumper: Xfmr to Bus | LS value of Jumper | Bus | LS value of Bus | Jumper: Bus to Bkr | LS Value of Jumper | Xfmr side Bkr CTs | LS value of CTs | Breaker | LS value of Breaker | Line side Bkr CTs | LS value of CTs | Jumper: Bkr to DS | LS value of Jumper | Disconnect Switch | LS Value of DS | Low Bus to Line DS | LS value of Bus | Riser to High Bus | LS value of Riser | High Bus to Line DS | LS value of Bus | Riser to High Bus | LS value of Riser | Relay Trip Amps | LS Relay Trip Amps | Downstream Most Limiting Current | Downstream Next Most Limiting | Limiting Current | Most Limiting Element | Amps | Low Side Main Bus | Jumper: Main to Bus | Bus to DS | Disconnect | Metering CT | Jumper: DS to Xfmr | LS Xfmr CTs | [15 empty] | Downstream Most Limiting Current | Downstream Next Most Limiting | Next Most Limiting Current | Next Most Limiting Element
[57 empty] | Xfmr LS Current Rating | LS value of HS CTs | LS value of Jumper | LS value of Bus | LS Value of Jumper | LS value of CTs | LS value of Breaker | LS value of CTs | LS value of Jumper | LS Value of DS | LS value of Bus | LS value of Riser | LS value of Bus | LS value of Riser | LS Relay Trip Amps
Rush Creek 1 | XFMR T1 | 238.0322 | 34.5 | 3983.4195 | 5554 | 6328 | 5554 | 5000 | 4500 | 6328 | 6000 | 248 | 345 | 34.5 | 10 | 4150.3498 | 800 | 8000 | 2034 | 20340 | 3850 | 38500 | 2034 | 20340 | 2000 | 20000 | 2000 | 20000 | 2000 | 20000 | 2034 | 20340 | 1200 | 12000 | NA | NA | NA | NA | NA | NA | NA | NA | 706 | 7060 | 12000 | 20340 | 3983.4195 | Combined Equip MVA | 3983.4195 | 5554 | 6328 | 5554 | 5000 | 4500 | 6328 | 6000 | 4150.3498 | 8000 | 20340 | 38500 | 20340 | 20000 | 20000 | 20000 | 20340 | 12000 | NA | NA | NA | NA | 7060 | 12000 | 20340 | 4150.3498 | Main Power Transformer
| XFMR T2 | 215.8313 | 34.5 | 3611.8909 | 5554 | 6328 | 5554 | 5000 | 4500 | 6328 | 6000 | 248 | 345 | 34.5 | 10 | 4150.3498 | 800 | 8000 | 2034 | 20340 | 3850 | 38500 | 2034 | 20340 | 2000 | 20000 | 2000 | 20000 | 2000 | 20000 | 2034 | 20340 | 1200 | 12000 | 3850 | 38500 | 3962 | 39620 | 3850 | 38500 | 3962 | 39620 | 706 | 7060 | 12000 | 20340 | 3611.8909 | Combined Equip MVA | 3611.8909 | 5554 | 6328 | 5554 | 5000 | 4500 | 6328 | 6000 | 4150.3498 | 8000 | 20340 | 38500 | 20340 | 20000 | 20000 | 20000 | 20340 | 12000 | 38500 | 39620 | 38500 | 39620 | 7060 | 12000 | 20340 | 4150.3498 | Main Power Transformer
Rush Creek 2 | XFMR T1 | 252.3429 | 34.5 | 4222.9062 | 5554 | 6328 | 5554 | 5000 | 4500 | 6328 | 6000 | 248 | 345 | 34.5 | 10 | 4150.3498 | 800 | 8000 | 2034 | 20340 | 3850 | 38500 | 2034 | 20340 | 2000 | 20000 | 2000 | 20000 | 2000 | 20000 | 2034 | 20340 | 1200 | 12000 | NA | NA | NA | NA | NA | NA | NA | NA | 508 | 5080 | 12000 | 20340 | 4150.3498 | Main Power Transformer | 4222.9062 | 5554 | 6328 | 5554 | 5000 | 4500 | 6328 | 6000 | 4150.3498 | 8000 | 20340 | 38500 | 20340 | 20000 | 20000 | 20000 | 20340 | 12000 | NA | NA | NA | NA | 5080 | 12000 | 20340 | 4222.9062 | Combined Equip MVA
Bus Tie Switch Rating
Plant | Switch | Combined MVA | kV | Amps | Switch CTs | Bus | Disconnect | Downstream Most Limiting Current | Downstream Next Most Limiting | Limiting Current | Most Limiting Equipment | Next Most Limiting Current | Next Most Limiting Element
Rush Creek 1 | 1001M | 238.0322 | 34.5 | 3983.4195 | 6000 | 5554 | 5000 | 4150.3498 | 4500 | 3983.4195 | Combined Equip MVA | 4150.3498 | Main Power Transformer
Rush Creek 2 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
Main Power Transformer Ratings - Bus Tie Configuration
Plant | Transformer | Combined MVA | kV | Amps | Limiting Element from Normal Config | Next Most Limiting Element from Normal Config | Downstream Most Limiting Current | Downstream Next Most Limiting | Limiting Current | Most Limiting Element | Next Most Limiting Current | Next Most Limiting Element
Rush Creek 1 | XFMR T1 | 362.542 | 34.5 | 6067.0651 | 4150.3498 | 4500 | 8300.6995 | 12000 | 4150.3498 | Main Power Transformer | 4500 | Metering CT
| XFMR T2 | 362.542 | 34.5 | 6067.0651 | 4150.3498 | 4500 | 8300.6995 | 12000 | 4150.3498 | Main Power Transformer | 4500 | Metering CT
Rush Creek 2 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
Plant Overall Rating
Plant | Combined MVA | kV | Amps | Bus from CB | Jumper to Wave Trap | Wave Trap | Jumper: Bus/Trap to DS | Disconnect Switch | Conductor to T- line | Relay Trip Amps | Value from Subs Eng | Step Up Xfmr Ratio | Xfmr MVA | Amps- Low Side | Xfmr LS Current Rating | Bus-LS | Jumper - LS | Wave Trap | Jumper - LS | Disconnnect - LS | Conductor - LS | Relay Trip-LS | Subs Eng - LS | Most Limiting Current | Most Limiting Element | Next Most Limiting Current | Next Most Limiting Element
Rush Creek 1 | 457.2976 | 345 | 765.278 | 3850 | NA | NA | 2034 | 1200 | 2034 | NA | TRANSFERRED TO SUBS | 10 | 496 | 7652.7795 | 8300.6995 | 38500 | NA | NA | 20340 | 12000 | 20340 | NA | TRANSFERRED TO SUBS | 7652.7795 | Combined Equip MVA | 8300.6995 | Main Power Transformer
Rush Creek 2 | 252.3429 | 345 | 422.2906 | 3850 | NA | NA | 2034 | 1200 | 2034 | NA | TRANSFERRED TO SUBS | 10 | 248 | 4222.9062 | 4150.3498 | 38500 | NA | NA | 20340 | 12000 | 20340 | NA | TRANSFERRED TO SUBS | 4150.3498 | Main Power Transformer | 4222.9062 | Combined Equip MVA
CHEYENNE RIDGE RATING CALCULATIONS
Wind Generator Ratings:
V110 |  |  | V120
Wind Generator MW Rating | 2 |  | Wind Generator MW Rating | 2.2
Inductive (under-excited) MVAR Rating | 0.583 |  | Inductive (under-excited) MVAR Rating | 0.723
Capacitive (over-excited) MVAR Rating | 0.406 |  | Capacitive (over-excited) MVAR Rating | 0.723
Inductive MVA Rating | 2.0832 |  | Inductive MVA Rating | 2.3158
Capacitive MVA Rating | 2.0408 |  | Capacitive MVA Rating | 2.3158
Feeder Ratings
Plant | Feeder | V110 | V120 | Combined MW | Combined MVAR (Ind) | Combined MVAR (Cap) | Combined MVA | KV | Amps | Underground Cable | Jumper: Feeder to Disconnect | Feeder Disconnect | Jumper: Disconnect to Bus | Downstream Most Limiting Current | Downstream Next Most Limiting | Limiting Current | Most Limiting Element | Next Most Limiting Current | Next Most Limiting Element
Cheyenne Rigde East | 2101A | 8 | 3 | 22.6 | 6.833 | 5.417 | 23.6104 | 34.5 | 395.1147 | 422.9 | 1014 | 600 | 1014 | 1014 | 1014 | 395.1147 | Combined Equip MVA | 422.9 | Underground Cable
| 2101B | 0 | 10 | 22 | 7.23 | 7.23 | 23.1576 | 34.5 | 387.537 | 422.9 | 1014 | 600 | 1014 | 1014 | 1014 | 387.537 | Combined Equip MVA | 422.9 | Underground Cable
| 2102A | 8 | 3 | 22.6 | 6.833 | 5.417 | 23.6104 | 34.5 | 395.1147 | 422.9 | 1014 | 600 | 1014 | 1014 | 1014 | 395.1147 | Combined Equip MVA | 422.9 | Underground Cable
| 2102B | 11 | 0 | 22 | 6.413 | 4.466 | 22.9156 | 34.5 | 383.4884 | 422.9 | 1014 | 600 | 1014 | 1014 | 1014 | 383.4884 | Combined Equip MVA | 422.9 | Underground Cable
| 2103A | 0 | 4 | 8.8 | 2.892 | 2.892 | 9.263 | 34.5 | 155.0148 | 316.6 | 1014 | 600 | 1014 | 1014 | 1014 | 155.0148 | Combined Equip MVA | 316.6 | Underground Cable
| 2103B | 0 | 10 | 22 | 7.23 | 7.23 | 23.1576 | 34.5 | 387.537 | 422.9 | 1014 | 600 | 1014 | 1014 | 1014 | 387.537 | Combined Equip MVA | 422.9 | Underground Cable
| 2201A | 0 | 10 | 22 | 7.23 | 7.23 | 23.1576 | 34.5 | 387.537 | 422.9 | 1014 | 600 | 1014 | 1014 | 1014 | 387.537 | Combined Equip MVA | 422.9 | Underground Cable
| 2201B | 0 | 10 | 22 | 7.23 | 7.23 | 23.1576 | 34.5 | 387.537 | 422.9 | 1014 | 600 | 1014 | 1014 | 1014 | 387.537 | Combined Equip MVA | 422.9 | Underground Cable
| 2202 | 0 | 10 | 22 | 7.23 | 7.23 | 23.1576 | 34.5 | 387.537 | 422.9 | 1014 | 600 | 1014 | 1014 | 1014 | 387.537 | Combined Equip MVA | 422.9 | Underground Cable
| 2203A | 0 | 10 | 22 | 7.23 | 7.23 | 23.1576 | 34.5 | 387.537 | 422.9 | 1014 | 600 | 1014 | 1014 | 1014 | 387.537 | Combined Equip MVA | 422.9 | Underground Cable
| 2203B | 0 | 10 | 22 | 7.23 | 7.23 | 23.1576 | 34.5 | 387.537 | 422.9 | 1014 | 600 | 1014 | 1014 | 1014 | 387.537 | Combined Equip MVA | 422.9 | Underground Cable
Cheyenne Ridge West | 1101A | 0 | 8 | 17.6 | 5.784 | 5.784 | 18.5261 | 34.5 | 310.0296 | 348.6 | 1014 | 600 | 1014 | 1014 | 1014 | 310.0296 | Combined Equip MVA | 348.6 | Underground Cable
| 1101B | 0 | 8 | 17.6 | 5.784 | 5.784 | 18.5261 | 34.5 | 310.0296 | 348.6 | 1014 | 600 | 1014 | 1014 | 1014 | 310.0296 | Combined Equip MVA | 348.6 | Underground Cable
| 1101C | 0 | 7 | 15.4 | 5.061 | 5.061 | 16.2103 | 34.5 | 271.2759 | 348.6 | 1014 | 600 | 1014 | 1014 | 1014 | 271.2759 | Combined Equip MVA | 348.6 | Underground Cable
| 1102A | 0 | 8 | 17.6 | 5.784 | 5.784 | 18.5261 | 34.5 | 310.0296 | 348.6 | 1014 | 600 | 1014 | 1014 | 1014 | 310.0296 | Combined Equip MVA | 348.6 | Underground Cable
| 1102B | 0 | 8 | 17.6 | 5.784 | 5.784 | 18.5261 | 34.5 | 310.0296 | 348.6 | 1014 | 600 | 1014 | 1014 | 1014 | 310.0296 | Combined Equip MVA | 348.6 | Underground Cable
| 1103A | 0 | 7 | 15.4 | 5.061 | 5.061 | 16.2103 | 34.5 | 271.2759 | 348.6 | 1014 | 600 | 1014 | 1014 | 1014 | 271.2759 | Combined Equip MVA | 348.6 | Underground Cable
| 1103B | 0 | 8 | 17.6 | 5.784 | 5.784 | 18.5261 | 34.5 | 310.0296 | 348.6 | 1014 | 600 | 1014 | 1014 | 1014 | 310.0296 | Combined Equip MVA | 348.6 | Underground Cable
| 1103C | 0 | 8 | 17.6 | 5.784 | 5.784 | 18.5261 | 34.5 | 310.0296 | 422.9 | 1014 | 600 | 1014 | 1014 | 1014 | 310.0296 | Combined Equip MVA | 422.9 | Underground Cable
| 1201A | 0 | 10 | 22 | 7.23 | 7.23 | 23.1576 | 34.5 | 387.537 | 422.9 | 1014 | 600 | 1014 | 1014 | 1014 | 387.537 | Combined Equip MVA | 422.9 | Underground Cable
| 1201B | 0 | 10 | 22 | 7.23 | 7.23 | 23.1576 | 34.5 | 387.537 | 422.9 | 1014 | 600 | 1014 | 1014 | 1014 | 387.537 | Combined Equip MVA | 422.9 | Underground Cable
| 1202A | 0 | 10 | 22 | 7.23 | 7.23 | 23.1576 | 34.5 | 387.537 | 422.9 | 1014 | 600 | 1014 | 1014 | 1014 | 387.537 | Combined Equip MVA | 422.9 | Underground Cable
| 1202B | 0 | 10 | 22 | 7.23 | 7.23 | 23.1576 | 34.5 | 387.537 | 422.9 | 1014 | 600 | 1014 | 1014 | 1014 | 387.537 | Combined Equip MVA | 422.9 | Underground Cable
| 1203A | 0 | 10 | 22 | 7.23 | 7.23 | 23.1576 | 34.5 | 387.537 | 422.9 | 1014 | 600 | 1014 | 1014 | 1014 | 387.537 | Combined Equip MVA | 422.9 | Underground Cable
| 1203B | 0 | 10 | 22 | 7.23 | 7.23 | 23.1576 | 34.5 | 387.537 | 422.9 | 1014 | 600 | 1014 | 1014 | 1014 | 387.537 | Combined Equip MVA | 422.9 | Underground Cable
Feeder Breaker Ratings
Plant | Breaker | Combined MVA |  |  | Bus: Feeder to Jumper | Bus: Jumper to Breaker | Feeder Side CT | Breaker | Bus Side CT | Jumper: Breaker to DS | Bus Side Disconnect | Jumper: DS to Main Bus | Relay Trip | Downstream Most Limiting Current | Downstream Next Most Limiting | Limiting Current | Most Limiting Element | Next Most Limiting Current | Limiting Element
|  |  | kV | Amps
Cheyenne Ridge East | 2101 | 46.7679 | 34.5 | 782.6517 | 1226 | 1014 | 4000 | 1200 | 4000 | 1014 | 1200 | 1014 | 1128 | 2610.6273 | 3000 | 782.6517 | Combined Equip MVA | 1014 | Jumper: DS to Main Bus*
| 2102 | 46.526 | 34.5 | 778.6031 | 1226 | 1014 | 4000 | 1200 | 4000 | 1014 | 1200 | 1014 | 1128 | 2610.6273 | 3000 | 778.6031 | Combined Equip MVA | 1014 | Jumper: DS to Main Bus*
| 2103 | 32.4206 | 34.5 | 542.5518 | 1226 | 1014 | 4000 | 1200 | 4000 | 1014 | 1200 | 1014 | 1128 | 2610.6273 | 3000 | 542.5518 | Combined Equip MVA | 1014 | Jumper: DS to Main Bus*
| 2201 | 46.3151 | 34.5 | 775.0741 | 1226 | 1014 | 4000 | 1200 | 4000 | 1014 | 1200 | 1014 | 1128 | 2610.6273 | 3000 | 775.0741 | Combined Equip MVA | 1014 | Jumper: DS to Main Bus*
| 2202 | 23.1576 | 34.5 | 387.537 | 1226 | 1014 | 4000 | 1200 | 4000 | 1014 | 1200 | 1014 | 1128 | 2610.6273 | 3000 | 387.537 | Combined Equip MVA | 1014 | Jumper: DS to Main Bus*
| 2203 | 46.3151 | 34.5 | 775.0741 | 1226 | 1014 | 4000 | 1200 | 4000 | 1014 | 1200 | 1014 | 1128 | 2610.6273 | 3000 | 775.0741 | Combined Equip MVA | 1014 | Jumper: DS to Main Bus*
Cheyenne Ridge West | 1101 | 53.2624 | 34.5 | 891.3352 | 1226 | 1014 | 4000 | 1200 | 4000 | 1014 | 1200 | 1014 | 1284 | 2610.6273 | 3000 | 891.3352 | Combined Equip MVA | 1014 | Jumper: DS to Main Bus*
| 1102 | 37.0521 | 34.5 | 620.0592 | 1226 | 1014 | 4000 | 1200 | 4000 | 1014 | 1200 | 1014 | 1284 | 2610.6273 | 3000 | 620.0592 | Combined Equip MVA | 1014 | Jumper: DS to Main Bus*
| 1103 | 53.2624 | 34.5 | 891.3352 | 1226 | 1014 | 4000 | 1200 | 4000 | 1014 | 1200 | 1014 | 1284 | 2610.6273 | 3000 | 891.3352 | Combined Equip MVA | 1014 | Jumper: DS to Main Bus*
| 1201 | 46.3151 | 34.5 | 775.0741 | 1226 | 1014 | 4000 | 1200 | 4000 | 1014 | 1200 | 1014 | 1284 | 2610.6273 | 3000 | 775.0741 | Combined Equip MVA | 1014 | Jumper: DS to Main Bus*
| 1202 | 46.3151 | 34.5 | 775.0741 | 1226 | 1014 | 4000 | 1200 | 4000 | 1014 | 1200 | 1014 | 1284 | 2610.6273 | 3000 | 775.0741 | Combined Equip MVA | 1014 | Jumper: DS to Main Bus*
| 1203 | 46.3151 | 34.5 | 775.0741 | 1226 | 1014 | 4000 | 1200 | 4000 | 1014 | 1200 | 1014 | 1284 | 2610.6273 | 3000 | 775.0741 | Combined Equip MVA | 1014 | Jumper: DS to Main Bus*
Cap Switcher Feeder Ratings
Plant | Switcher | Combined MVA | kV | Amps | Jumper: Cap to Switcher | Switcher | Jumper: Switcher to Bus | Disconnect | Bus: Disconnect to Riser | Riser Bus | Downstream Most Limiting Current | Downstream Next Most Limiting | Limiting Current | Most Limiting Element | Next Most Limiting Current | Next Most Limiting Element
Cheyenne Ridge East | C2152 | 12.5 | 34.5 | 209.1849 | 209.1849 | 600 | 1014 | 1200 | 3175 | 3256 | 636 | 1014 | 209.1849 | Combined Equip MVA | 209.1849 | Jumper: Cap to Switcher
| C2153 | 12.5 | 34.5 | 209.1849 | 209.1849 | 600 | 1014 | 1200 | 3175 | 3256 | 636 | 1014 | 209.1849 | Combined Equip MVA | 209.1849 | Jumper: Cap to Switcher
| C2252 | 12.5 | 34.5 | 209.1849 | 209.1849 | 600 | 1014 | 1200 | 3175 | 3256 | 636 | 1014 | 209.1849 | Combined Equip MVA | 209.1849 | Jumper: Cap to Switcher
| C2253 | 12.5 | 34.5 | 209.1849 | 209.1849 | 600 | 1014 | 1200 | 3175 | 3256 | 636 | 1014 | 209.1849 | Combined Equip MVA | 209.1849 | Jumper: Cap to Switcher
Cheyenne Ridge West | C1152 | 16.5 | 34.5 | 276.124 | 276.124 | 600 | 1014 | 1200 | 3175 | 3256 | 796 | 1014 | 276.124 | Combined Equip MVA | 276.124 | Jumper: Cap to Switcher
| C1153 | 16.5 | 34.5 | 276.124 | 276.124 | 600 | 1014 | 1200 | 3175 | 3256 | 796 | 1014 | 276.124 | Combined Equip MVA | 276.124 | Jumper: Cap to Switcher
| C1252 | 16.5 | 34.5 | 276.124 | 276.124 | 600 | 1014 | 1200 | 3175 | 3256 | 796 | 1014 | 276.124 | Combined Equip MVA | 276.124 | Jumper: Cap to Switcher
| C1253 | 16.5 | 34.5 | 276.124 | 276.124 | 600 | 1014 | 1200 | 3175 | 3256 | 796 | 1014 | 276.124 | Combined Equip MVA | 276.124 | Jumper: Cap to Switcher
Reactor Switcher Feeder Ratings
Plant | Switcher | Combined MVA | kV | Amps | Jumper: Reactor to Bus | Bus | Jumper: Bus to Switcher | Switcher | Jumper: Switcher to Disconnect | Disconnect | Bus: Disconnect to Riser | Riser Bus | Downstream Most Limiting Current | Downstream Next Most Limiting | Limiting Current | Most Limiting Element | Next Most Limiting Current | Next Limiting Element
Cheyenne Ridge East | R2151 | 13 | 34.5 | 217.5523 | 1014 | 1226 | 1014 | 600 | 1014 | 1200 | 3175 | 3256 | 636 | 1014 | 217.5523 | Combined Equip MVA | 600 | Switcher
| R2251 | 13 | 34.5 | 217.5523 | 1014 | 1226 | 1014 | 600 | 1014 | 1200 | 3175 | 3256 | 636 | 1014 | 217.5523 | Combined Equip MVA | 600 | Switcher
Cheyenne Ridge West | R1151 | 12 | 34.5 | 200.8175 | 1014 | 1226 | 1014 | 600 | 1014 | 1200 | 3175 | 3256 | 796 | 1014 | 200.8175 | Combined Equip MVA | 600 | Switcher
| R1251 | 12 | 34.5 | 200.8175 | 1014 | 1226 | 1014 | 600 | 1014 | 1200 | 3175 | 3256 | 796 | 1014 | 200.8175 | Combined Equip MVA | 600 | Switcher
Cap Bank and Reactor Feeder Ratings
Plant | Feeder | Combined MVA | kV | Amps | Cap and Reactor Bus | Jumper: Bus to Breaker | Downstream Most Limiting Current | Downstream Next Most Limiting | Limiting Current | Most Limiting Element | Next Most Limiting Current | Next Limiting Element
Cheyenne Ridge East | 2150C | 25 | 34.5 | 418.3698 | 3175 | 1014 | 636 | 1014 | 418.3698 | Combined Equip MVA | 636 | Relay Amps
| 2150R | 13 | 34.5 | 217.5523 | 3175 | 1014 | 636 | 1014 | 217.5523 | Combined Equip MVA | 636 | Relay Amps
| 2250C | 25 | 34.5 | 418.3698 | 3175 | 1014 | 636 | 1014 | 418.3698 | Combined Equip MVA | 636 | Relay Amps
| 2250R | 13 | 34.5 | 217.5523 | 3175 | 1014 | 636 | 1014 | 217.5523 | Combined Equip MVA | 636 | Relay Amps
Cheyenne Ridge West | 1150C | 33 | 34.5 | 552.2481 | 3175 | 1014 | 796 | 1014 | 552.2481 | Combined Equip MVA | 796 | Relay Amps
| 1150R | 12 | 34.5 | 200.8175 | 3175 | 1014 | 796 | 1014 | 200.8175 | Combined Equip MVA | 796 | Relay Amps
| 1250C | 33 | 34.5 | 552.2481 | 3175 | 1014 | 796 | 1014 | 552.2481 | Combined Equip MVA | 796 | Relay Amps
| 1250R | 12 | 34.5 | 200.8175 | 3175 | 1014 | 796 | 1014 | 200.8175 | Combined Equip MVA | 796 | Relay Amps
Cap/Reactor Breaker Ratings
Plant | Breaker | Combined MVA | kV | Amps | Bus to Breaker | Jumper: Bus to Breaker | Feeder Side CT | Breaker | Bus Side CT | Jumper: Breaker to Disconnect | Disconnect | Jumper: Disconnect to Bus | Relay Trip | Downstream Most Limiting Current | Downstream Next Most Limiting | Limiting Current | Most Limiting Element | Next Most Limiting Current | Limiting Element
Cheyenne Ridge East | 2150 | 25 | 34.5 | 418.3698 | 3175 | 1014 | 4000 | 1200 | 4000 | 1014 | 1200 | 1014 | 636 | 2610.6273 | 3000 | 418.3698 | Combined Equip MVA | 636 | Relay Amps
| 2250 | 25 | 34.5 | 418.3698 | 3175 | 1014 | 4000 | 1200 | 4000 | 1014 | 1200 | 1014 | 636 | 2610.6273 | 3000 | 418.3698 | Combined Equip MVA | 636 | Relay Amps
Cheyenne Ridge West | 1150 | 33 | 34.5 | 552.2481 | 3175 | 1014 | 4000 | 1200 | 4000 | 1014 | 1200 | 1014 | 796 | 2610.6273 | 3000 | 552.2481 | Combined Equip MVA | 796 | Relay Amps
| 1250 | 33 | 34.5 | 552.2481 | 3175 | 1014 | 4000 | 1200 | 4000 | 1014 | 1200 | 1014 | 796 | 2610.6273 | 3000 | 552.2481 | Combined Equip MVA | 796 | Relay Amps
Main Power Transformer Ratings - Normal Configuration
Plant | Transformer | Combined MVA | kV | Amps | Bus | Jumper: Bus to main Bus | Bus to Disconnect | Bus CT | Bus to Disconnect | Disconnect | Jumper: Bus to Breaker | Feeder side CTs | Breaker | XFMR side CT | Jumper: Breaker to Disconnect | Disconnect | Jumper: Disconnect to XFMR | LS XFMR CT | LS Value of HS CT | LS Value of HS Jumper | LS Value of HS Bus | LS Value of HS Jumper | LS Value of HS Breaker XFMR Side CTs | LS Value of HS Breaker | LS Value of HS Breaker Line Side CTs | LS Value of HS Jumper | LS Value of HS Disconnect | LS Value of HS Bus | LS Value of HS Riser | XFMR Amps LS | Relay Trip | LS Value of Downstream Most Limiting Current | LS Value of Downstream Next Most Limiting | Limiting Current | Most Limiting Element | Next Most Limiting Current | Next Most Limiting Element | Array LS Value of Downstream Next Most Limiting
Cheyenne Ridge East | XFMR TR1 | 133.1306 | 34.5 | 2227.9125 | 3175 | 3042 | 3175 | 4500 | 3175 | 3000 | 3042 | 4000 | 3000 | 4000 | 3042 | 3000 | 3042 | 5240 | 6000 | 17060 | 31750 | 17060 | 40000 | 20000 | 40000 | 17060 | 12000 | 31750 | 32560 | 2610.6273 | 6328 | 12000 | 12000 | 2227.9125 | Combined Equip MVA | 2610.6273 | Main Power Transformer | 12000 | 12000
| XFMR TR2 | 125.8544 | 34.5 | 2106.1465 | 3175 | 3042 | 3175 | 4500 | 3175 | 3000 | 3042 | 4000 | 3000 | 4000 | 3042 | 3000 | 3042 | 5240 | 6000 | 17060 | 31750 | 17060 | 40000 | 20000 | 40000 | 17060 | 12000 | 31750 | 32560 | 2610.6273 | 6328 | 12000 | 12000 | 2106.1465 | Combined Equip MVA | 2610.6273 | Main Power Transformer | 12000 | 12000
Cheyenne Ridge West | XFMR TR1 | 157.0409 | 34.5 | 2628.0467 | 3175 | 3042 | 3175 | 4500 | 3175 | 3000 | 3042 | 4000 | 3000 | 4000 | 3042 | 3000 | 3042 | 5240 | 6000 | 17060 | 31750 | 17060 | 40000 | 20000 | 40000 | 17060 | 12000 | 31750 | 32560 | 2610.6273 | 7464 | 12000 | 12000 | 2610.6273 | Main Power Transformer | 2628.0467 | Combined Equip MVA | 12000 | 12000
| XFMR TR2 | 152.5054 | 34.5 | 2552.1463 | 3175 | 3042 | 3175 | 4500 | 3175 | 3000 | 3042 | 4000 | 3000 | 4000 | 3042 | 3000 | 3042 | 5240 | 6000 | 17060 | 31750 | 17060 | 40000 | 20000 | 40000 | 17060 | 12000 | 31750 | 32560 | 2610.6273 | 7464 | 12000 | 12000 | 2552.1463 | Combined Equip MVA | 2610.6273 | Main Power Transformer | 12000 | 12000
Bus Tie Switch Rating
Plant | Breaker | Combined MVA | kV | Amps | Bus to Disconnect | Disconnect | Jumper: Disconnect to Breaker | Breaker CTs Upstream Side | Breaker | Breaker CTs Downstream Side | Breaker CTs Downstream Side | Jumper: Breaker to Disconnect | Disconnect | Bus to Disconnect | Downstream Most Limiting Current | Downstream Next Most Limiting | Limiting Current | Most Limiting Equipment | Next Most Limiting Current | Next Most Limiting Element
Cheyenne Ridge East | 2001 | 133.1306 | 34.5 | 2227.9125 | 3175 | 3000 | 3042 | 4000 | 3000 | 4000 | 4000 | 3042 | 3000 | 3175 | 2610.6273 | 3000 | 2227.9125 | Combined Equip MVA | 2610.6273 | Main Power Transformer
Cheyenne Ridge West | 1001 | 157.0409 | 34.5 | 2628.0467 | 3175 | 3000 | 3042 | 4000 | 3000 | 4000 | 4000 | 3042 | 3000 | 3175 | 2610.6273 | 3000 | 2610.6273 | Main Power Transformer | 2628.0467 | Combined Equip MVA
Main Power Transformer Ratings - Bus Tie Configuration
Plant | Transformer | Transformer MVA | kV | Amps | Limiting Element from Normal Config | Next Most Limiting Element from Normal Config | LS Value of Downstream Most Limiting Current | LS Value of Downstream Next Most Limiting | Limiting Current | Most Limiting Element | Next Most Limiting Current | Next Most Limiting Element
Cheyenne Ridge East | XFMR T1 | 258.985 | 34.5 | 4334.059 | 2610.6273 | 5240 | 12000 | 17060 | 2610.6273 | Main Power Transformer | 5240 | LS XFMR CT
| XFMR T2 | 258.985 | 34.5 | 4334.059 | 2610.6273 | 5240 | 12000 | 17060 | 2610.6273 | Main Power Transformer | 5240 | LS XFMR CT
Cheyenne Ridge West | XFMR T1 | 309.5463 | 34.5 | 5180.193 | 2610.6273 | 5240 | 12000 | 12000 | 2610.6273 | Main Power Transformer | 5240 | LS XFMR CT
| XFMR T2 | 309.5463 | 34.5 | 5180.193 | 2610.6273 | 5240 | 12000 | 12000 | 2610.6273 | Main Power Transformer | 5240 | LS XFMR CT
Transmission Line Rating
Plant | Line | Combined MVA | kV | Amps | Bus: Riser to Disconnect | Disconnect | Jumper: Disconnect to Wave Trap | Wave Trap | Jumper: Wave Trap to 7215 Line | T-line 7215 | HS XFMR AMPS | LS Value of Most Limiting Current | Most Limiting Element | LS Value of Next Most Limiting Current | Next Most Limiting Element
Cheyenne Ridge East | 7215 | 258.985 | 345 | 433.4059 | 3175 | 1200 | 1706 | 3000 | 1706 | 2412 | 522.2 | 4334.059 | Combined Equip MVA | 5222 | Main Power Transformer
Plant | Line | Combined MVA | kV | Amps | T-line 7215 | Jumper: T-line 7215 to Wave Trap | Wave Trap | Jumper: Wave Trap to Disconnect | Disconnect | Jumper: Disconnect to Breaker | Breaker CTs 7215 Side | Breaker | Breaker CTs 7199 Side | Jumper: Breaker to Disconnect | Disconnect | Bus: Disconnect to Disconnect | Disconnect | Jumper: Disconnect to Wave Trap | Wave Trap | Jumper: Wave Trap to 7199 Line | Subs Engineering | LS Value of Most Limiting Current | Most Limiting Element | LS Value of Next Most Limiting Current | Next Most Limiting Element
Cheyenne Ridge Overall | 7199 | 568.5313 | 345 | 951.4252 | 2412 | 1706 | 3000 | 1706 | 1200 | 1706 | 4000 | 2000 | 4000 | 1706 | 1200 | 3175 | 1200 | 1706 | 3000 | 1706 | 1200 | 9514.2519 | Combined Equip MVA | 12000 | Disconnect*
Plant | Line | Combined MVA | kV | Amps | Bus: Riser to Disconnect | Disconnect | Jumper: Disconnect to Wave Trap | Wave Trap | Jumper: Wave Trap to 7199 Line | T-line 7261 | HS XFMR AMPS | LS Value of Most Limiting Current | Most Limiting Element | LS Value of Next Most Limiting Current | Next Most Limiting Element
Cheyenne Ridge West Ovall | 7215 | 309.5463 | 345 | 518.0193 | 3175 | 1200 | 1706 | 3000 | 1706 | Transferred to Subs | 522.2 | 5180.193 | Combined Equip MVA | 5222 | Main Power Transformer
Note on B6: Author: 34.5 kV Feeder
Note on B7: Author: 34.5 kV Feeder
Note on B8: Author: 34.5 kV Collector at sub
Note on B9: Author: 34.5 kV Feeder
Note on B10: Author: 34.5 kV Feeder
Note on B11: Author: 34.5 kV Collector at sub
Note on B12: Author: 34.5 kV Feeder
Note on B13: Author: 34.5 kV Feeder
Note on B14: Author: 34.5 kV Collector at sub
Note on B15: Author: 34.5 kV Feeder
Note on B16: Author: 34.5 kV Feeder
Note on B17: Author: 34.5 kV Collector at sub
Note on B18: Author: Feeder to 1153 Cap Bank
Note on B19: Author: Feeder to 1154 Cap Bank
Note on B20: Author: Feeder to 1155 Cap Bank
Note on B21: Author: Feeder to 1150 capacitor switches
Note on B22: Author: Feeder to 1151 Reactor
Note on B23: Author: Feeder to 1152 Reactor
Note on B24: Author: Feeder to 1150 shunt reactor switchers.
Note on B25: Author: Cap/Reactor 34.5 kV Feeder
Note on B26: Author: 34.5 kV Feeder
Note on B27: Author: 34.5 kV Feeder
Note on B28: Author: 34.5 kV Collector at sub
Note on B29: Author: 34.5 kV Feeder
Note on B30: Author: 34.5 kV Feeder
Note on B31: Author: 34.5 kV Collector at sub
Note on B32: Author: 34.5 Kv Feeder
Note on B33: Author: 1203 34.5 kV breaker
Note on B34: Author: 34.5 kV Feeder
Note on B35: Author: 34.5 kV Feeder
Note on B36: Author: 34.5 kV Collector at sub
Note on B37: Author: Feeder to 1253 Cap Bank
Note on B38: Author: Feeer to 1254 Cap Bank
Note on B39: Author: Feeder to 1255 Cap Bank
Note on B40: Author: Feeder to 1250 Cap Switcher
Note on B41: Author: Feeder to reactor
Note on B42: Author: Feeder to reactor switcher
Note on B43: Author: Cap/Reactor 34.5 kV Feeder
Note on B44: Author: Rating of the bus tie disconnect switch loads, which can have the full load from one bus connected
Note on B45: Author: Step up transformer with normal configuration
Note on B46: Author: Step up transformer with normal configuration
Note on B47: Author: Step up transformer with 34.5 kV bus tie
Note on B48: Author: Step up transformer with 34.5 kV bus tie
Note on B49: Author: Combined rating of all equipment, attached to 345 kV line to pronghorn switchyard.
Note on B52: Author: 2101A and 2101B feeders connect before the feeder disconnect. Combined rating
Note on B67: Author: 2105B and 2105C feeders connect before the feeder disconnect. Combined rating
Note on B109: Author: All feeders connected to Bus 1 are combined.
Note on B110: Author: All feeders connected to Bus 2 are combined.
Note on B111: Author: Rating in this configuration is limited to MPT MVA
Note on B112: Author: Rating in this configuration is limited to MPT MVA
Note on B147: Author: All feeders connected to Bus 1 are combined.
Note on B148: Author: All feeders connected to Bus 2 are combined.
Note on B149: Author: Rating in this configuration is limited to MPT MVA
Note on B150: Author: Rating in this configuration is limited to MPT MVA
Note on A174: Author: Refer to Reactive Capability curves provided in PSCo A&R TSA Ex. D.1.1.b General Specification
Note on D174: Author: Refer to Reactive Capability curves provided in PSCo A&R TSA Ex. D.1.1.a General Specification
Note on C182: Author: Refer to email "2018.8.2 Rush Creek Info" detailing the location of the installed turbines.
Note on H182: Author: Uses largest of MVAR values
Note on B184: Author: 34.5 kV Feeder
Note on K184: Author: 1250 MCM AL Cable, 35 kV, Direct Buried. Rate per Engineering study RC1-COL-MVC-R0.pdf
Note on L184: Author: Reference DRCW01-ESEQ-E71002 SH5 1272 AAC 1 per Phase Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls Normal Summer Rating
Note on M184: Author: Reference DRCW01-ESEQ-E71002 SH5 1272 AAC 1 per Phase Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls Normal Summer Rating
Note on N184: Author: Reference DRCW01-ESMV-E01001 SH1 DS1101A
Note on B185: Author: 34.5 kV Feeder
Note on K185: Author: 750 MCM AL Cable, 35 kV, Direct Buried. Rate per Engineering study RC1-COL-MVC-R0.pdf
Note on L185: Author: Reference DRCW01-ESEQ-E71002 SH5 1272 AAC 1 per Phase Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls Normal Summer Rating
Note on M185: Author: Reference DRCW01-ESEQ-E71002 SH5 1272 AAC 1 per Phase Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls Normal Summer Rating
Note on N185: Author: Reference DRCW01-ESMV-E01001 SH1 DS1101B
Note on B186: Author: 34.5 kV Feeder
Note on K186: Author: 1250 MCM AL Cable, 35 kV, Direct Buried. Rate per Engineering study RC1-COL-MVC-R0.pdf
Note on L186: Author: Reference DRCW01-ESEQ-E71002 SH4 1272 AAC 1 per Phase Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls Normal Summer Rating
Note on M186: Author: Reference DRCW01-ESEQ-E71002 SH4 1272 AAC 1 per Phase Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls Normal Summer Rating
Note on N186: Author: Reference DRCW01-ESEQ-E71002 SH4 DRCW01-ESEQ-E41001 SH1 DS1102A
Note on B187: Author: 34.5 kV Feeder
Note on K187: Author: 1250 MCM AL Cable, 35 kV, Direct Buried. Rate per Engineering study RC1-COL-MVC-R0.pdf
Note on L187: Author: Reference DRCW01-ESEQ-E71002 SH4 1272 AAC 1 per Phase Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls Normal Summer Rating
Note on M187: Author: Reference DRCW01-ESEQ-E71002 SH4 1272 AAC 1 per Phase Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls Normal Summer Rating
Note on N187: Author: Reference DRCW01-ESEQ-E71002 SH4 DRCW01-ESEQ-E41001 SH1 DS1102B
Note on B188: Author: 34.5 kV Feeder
Note on K188: Author: 1250 MCM AL Cable, 35 kV, Direct Buried. Rate per Engineering study RC1-COL-MVC-R0.pdf
Note on L188: Author: Reference DRCW01-ESEQ-E71002 SH4 1272 AAC 1 per Phase Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls Normal Summer Rating
Note on M188: Author: Reference DRCW01-ESEQ-E71002 SH4 1272 AAC 1 per Phase Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls Normal Summer Rating
Note on N188: Author: Reference DRCW01-ESEQ-E71002 SH4 DRCW01-ESEQ-E41001 SH1 DS1103A
Note on B189: Author: 34.5 kV Feeder
Note on K189: Author: 1250 MCM AL Cable, 35 kV, Direct Buried. Rate per Engineering study RC1-COL-MVC-R0.pdf
Note on L189: Author: Reference DRCW01-ESEQ-E71002 SH4 1272 AAC 1 per Phase Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls Normal Summer Rating
Note on M189: Author: Reference DRCW01-ESEQ-E71002 SH4 1272 AAC 1 per Phase Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls Normal Summer Rating
Note on N189: Author: Reference DRCW01-ESEQ-E71002 SH4 DRCW01-ESEQ-E41001 SH1 DS1103B
Note on B190: Author: 34.5 kV Feeder
Note on K190: Author: 1250 MCM AL Cable, 35 kV, Direct Buried. Rate per Engineering study RC1-COL-MVC-R0.pdf
Note on L190: Author: Reference DRCW01-ESEQ-E71002 SH4 1272 AAC 1 per Phase Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls Normal Summer Rating
Note on M190: Author: Reference DRCW01-ESEQ-E71002 SH4 1272 AAC 1 per Phase Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls Normal Summer Rating
Note on N190: Author: Reference DRCW01-ESEQ-E71002 SH4 DRCW01-ESEQ-E41001 SH1 DS1104A
Note on B191: Author: 34.5 kV Feeder
Note on K191: Author: 1250 MCM AL Cable, 35 kV, Direct Buried. Rate per Engineering study RC1-COL-MVC-R0.pdf
Note on L191: Author: Reference DRCW01-ESEQ-E71002 SH4 1272 AAC 1 per Phase Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls Normal Summer Rating
Note on M191: Author: Reference DRCW01-ESEQ-E71002 SH4 1272 AAC 1 per Phase Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls Normal Summer Rating
Note on N191: Author: Reference DRCW01-ESEQ-E71002 SH4 DRCW01-ESEQ-E41001 SH1 DS1104B
Note on B192: Author: 34.5 kV Feeder
Note on K192: Author: 1250 MCM AL Cable, 35 kV, Direct Buried. Rate per Engineering study RC1-COL-MVC-R0.pdf
Note on L192: Author: Reference DRCW01-ESEQ-E71002 SH4 1272 AAC 1 per Phase Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls Normal Summer Rating
Note on M192: Author: Reference DRCW01-ESEQ-E71002 SH4 1272 AAC 1 per Phase Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls Normal Summer Rating
Note on N192: Author: Reference DRCW01-ESEQ-E71002 SH4 DRCW01-ESEQ-E41001 SH1 DS1201A
Note on B193: Author: 34.5 kV Feeder
Note on K193: Author: 1250 MCM AL Cable, 35 kV, Direct Buried. Rate per Engineering study RC1-COL-MVC-R0.pdf
Note on L193: Author: Reference DRCW01-ESEQ-E71002 SH4 1272 AAC 1 per Phase Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls Normal Summer Rating
Note on M193: Author: Reference DRCW01-ESEQ-E71002 SH4 1272 AAC 1 per Phase Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls Normal Summer Rating
Note on N193: Author: Reference DRCW01-ESEQ-E71002 SH4 DRCW01-ESEQ-E41001 SH1 DS1201B
Note on B194: Author: 34.5 kV Feeder
Note on K194: Author: 1250 MCM AL Cable, 35 kV, Direct Buried. Rate per Engineering study RC1-COL-MVC-R0.pdf
Note on L194: Author: Reference DRCW01-ESEQ-E71002 SH4 1272 AAC 1 per Phase Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls Normal Summer Rating
Note on M194: Author: Reference DRCW01-ESEQ-E71002 SH4 1272 AAC 1 per Phase Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls Normal Summer Rating
Note on N194: Author: Reference DRCW01-ESEQ-E71002 SH4 DRCW01-ESEQ-E41001 SH1 DS1202A
Note on B195: Author: 34.5 kV Feeder
Note on K195: Author: 1250 MCM AL Cable, 35 kV, Direct Buried. Rate per Engineering study RC1-COL-MVC-R0.pdf
Note on L195: Author: Reference DRCW01-ESEQ-E71002 SH4 1272 AAC 1 per Phase Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls Normal Summer Rating
Note on M195: Author: Reference DRCW01-ESEQ-E71002 SH4 1272 AAC 1 per Phase Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls Normal Summer Rating
Note on N195: Author: Reference DRCW01-ESEQ-E71002 SH4 DRCW01-ESEQ-E41001 SH1 DS1202B
Note on B196: Author: 34.5 kV Collector at sub
Note on K196: Author: 1250 MCM AL Cable, 35 kV, Direct Buried. Rate per Engineering study RC1-COL-MVC-R0.pdf
Note on L196: Author: Reference DRCW01-ESEQ-E71002 SH6 1272 AAC 1 per Phase Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls Normal Summer Rating
Note on M196: Author: Reference DRCW01-ESEQ-E71002 SH6 1272 AAC 1 per Phase Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls Normal Summer Rating
Note on N196: Author: Reference DRCW01-ESEQ-E71002 SH6 DRCW01-ESEQ-E41001 SH1 DS1203 and DS1203F
Note on B197: Author: 34.5 kV Feeder
Note on K197: Author: 1250 MCM AL Cable, 35 kV, Direct Buried. Rate per Engineering study RC1-COL-MVC-R0.pdf
Note on L197: Author: Reference DRCW01-ESEQ-E71002 SH4 1272 AAC 1 per Phase Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls Normal Summer Rating
Note on M197: Author: Reference DRCW01-ESEQ-E71002 SH4 1272 AAC 1 per Phase Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls Normal Summer Rating
Note on N197: Author: Reference DRCW01-ESEQ-E71002 SH4 DRCW01-ESEQ-E41001 SH1 DS1204A
Note on B198: Author: 34.5 kV Feeder
Note on K198: Author: 1250 MCM AL Cable, 35 kV, Direct Buried. Rate per Engineering study RC1-COL-MVC-R0.pdf
Note on L198: Author: Reference DRCW01-ESEQ-E71002 SH4 1272 AAC 1 per Phase Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls Normal Summer Rating
Note on M198: Author: Reference DRCW01-ESEQ-E71002 SH4 1272 AAC 1 per Phase Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls Normal Summer Rating
Note on N198: Author: Reference DRCW01-ESEQ-E71002 SH4 DRCW01-ESEQ-E41001 SH1 DS1204B
Note on K199: Author: 500 MCM cable Rate per engineering study RC2-COL-MVC-R0.pdf
Note on L199: Author: Reference DRCW02-ESEQ-E72002 SH6 1272 AAC 1 per Phase Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls Normal Summer Rating
Note on M199: Author: Reference DRCW02-ESEQ-E72002 SH6 1272 AAC 1 per Phase Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls Normal Summer Rating
Note on N199: Author: Reference DRCW02-ESMV-E002001 SH1 DRCW02-ESEQ-E72002 SH6 DS2101B
Note on K200: Author: 1250 MCM cable Rate per engineering study RC2-COL-MVC-R0.pdf
Note on L200: Author: Reference DRCW02-ESEQ-E72002 SH6 1272 AAC 1 per Phase Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls Normal Summer Rating
Note on M200: Author: Reference DRCW02-ESEQ-E72002 SH6 1272 AAC 1 per Phase Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls Normal Summer Rating
Note on N200: Author: Reference DRCW02-ESMV-E002001 SH1 DRCW02-ESEQ-E72002 SH6 DS2101B
Note on B201: Author: 2101A and 2101B feeders connect before the feeder disconnect. Combined rating
Note on L201: Author: Reference DRCW02-ESEQ-E72002 SH6 1272 AAC 1 per Phase Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls Normal Summer Rating
Note on M201: Author: Reference DRCW02-ESEQ-E72002 SH6 1272 AAC 1 per Phase Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls Normal Summer Rating
Note on N201: Author: Reference DRCW02-ESMV-E002001 SH1 DRCW02-ESEQ-E72002 SH6 DS2101B
Note on K202: Author: 1250 MCM cable Rate per engineering study RC2-COL-MVC-R0.pdf
Note on L202: Author: Reference DRCW02-ESEQ-E72002 SH6 1272 AAC 1 per Phase Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls Normal Summer Rating
Note on M202: Author: Reference DRCW02-ESEQ-E72002 SH6 1272 AAC 1 per Phase Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls Normal Summer Rating
Note on N202: Author: Reference DRCW02-ESMV-E002001 SH1 DRCW02-ESEQ-E72002 SH6 DS2101A
Note on K203: Author: 1250 MCM cable Rate per engineering study RC2-COL-MVC-R0.pdf
Note on L203: Author: Reference DRCW02-ESEQ-E72002 SH4 1272 AAC 1 per Phase Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls Normal Summer Rating
Note on M203: Author: Reference DRCW02-ESEQ-E72002 SH4 1272 AAC 1 per Phase Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls Normal Summer Rating
Note on N203: Author: Reference DRCW02-ESMV-E002001 SH1 DRCW02-ESEQ-E72002 SH4 DS2102A
Note on K204: Author: 1250 MCM cable Rate per engineering study RC2-COL-MVC-R0.pdf
Note on L204: Author: Reference DRCW02-ESEQ-E72002 SH4 1272 AAC 1 per Phase Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls Normal Summer Rating
Note on M204: Author: Reference DRCW02-ESEQ-E72002 SH4 1272 AAC 1 per Phase Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls Normal Summer Rating
Note on N204: Author: Reference DRCW02-ESMV-E002001 SH1 DRCW02-ESEQ-E72002 SH4 DS2102B
Note on K205: Author: 1250 MCM cable Rate per engineering study RC2-COL-MVC-R0.pdf
Note on L205: Author: Reference DRCW02-ESEQ-E72002 SH5 1272 AAC 1 per Phase Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls Normal Summer Rating
Note on M205: Author: Reference DRCW02-ESEQ-E72002 SH5 1272 AAC 1 per Phase Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls Normal Summer Rating
Note on N205: Author: Reference DRCW02-ESMV-E002001 SH1 DRCW02-ESEQ-E72002 SH5 DS2103A
Note on K206: Author: 750 MCM cable Rate per engineering study RC2-COL-MVC-R0.pdf
Note on L206: Author: Reference DRCW02-ESEQ-E72002 SH5 1272 AAC 1 per Phase Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls Normal Summer Rating
Note on M206: Author: Reference DRCW02-ESEQ-E72002 SH5 1272 AAC 1 per Phase Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls Normal Summer Rating
Note on N206: Author: Reference DRCW02-ESMV-E002001 SH1 DRCW02-ESEQ-E72002 SH5 DS2103B
Note on K207: Author: 1250 MCM cable Rate per engineering study RC2-COL-MVC-R0.pdf
Note on L207: Author: Reference DRCW02-ESEQ-E72002 SH4 1272 AAC 1 per Phase Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls Normal Summer Rating
Note on M207: Author: Reference DRCW02-ESEQ-E72002 SH4 1272 AAC 1 per Phase Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls Normal Summer Rating
Note on N207: Author: Reference DRCW02-ESMV-E002001 SH1 DRCW02-ESEQ-E72002 SH4 DS2104A
Note on K208: Author: 1250 MCM cable Rate per engineering study RC2-COL-MVC-R0.pdf
Note on L208: Author: Reference DRCW02-ESEQ-E72002 SH4 1272 AAC 1 per Phase Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls Normal Summer Rating
Note on M208: Author: Reference DRCW02-ESEQ-E72002 SH4 1272 AAC 1 per Phase Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls Normal Summer Rating
Note on N208: Author: Reference DRCW02-ESMV-E002001 SH1 DRCW02-ESEQ-E72002 SH4 DS2104B
Note on K209: Author: 1250 MCM cable Rate per engineering study RC2-COL-MVC-R0.pdf
Note on L209: Author: Reference DRCW02-ESEQ-E72002 SH6 1272 AAC 1 per Phase Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls Normal Summer Rating
Note on M209: Author: Reference DRCW02-ESEQ-E72002 SH6 1272 AAC 1 per Phase Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls Normal Summer Rating
Note on N209: Author: Reference DRCW02-ESMV-E002001 SH1 DRCW02-ESEQ-E72002 SH6 DS2105A
Note on K210: Author: 1250 MCM cable Rate per engineering study RC2-COL-MVC-R0.pdf
Note on L210: Author: Reference DRCW02-ESEQ-E72002 SH6 1272 AAC 1 per Phase Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls Normal Summer Rating
Note on M210: Author: Reference DRCW02-ESEQ-E72002 SH6 1272 AAC 1 per Phase Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls Normal Summer Rating
Note on N210: Author: Reference DRCW02-ESMV-E002001 SH1 DRCW02-ESEQ-E72002 SH6 DS2105B
Note on K211: Author: 500 MCM cable Rate per engineering study RC2-COL-MVC-R0.pdf
Note on L211: Author: Reference DRCW02-ESEQ-E72002 SH6 1272 AAC 1 per Phase Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls Normal Summer Rating
Note on M211: Author: Reference DRCW02-ESEQ-E72002 SH6 1272 AAC 1 per Phase Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls Normal Summer Rating
Note on N211: Author: Reference DRCW02-ESMV-E002001 SH1 DRCW02-ESEQ-E72002 SH6 DS2105B
Note on B212: Author: 2105B and 2105C feeders connect before the feeder disconnect. Combined rating
Note on L212: Author: Reference DRCW02-ESEQ-E72002 SH6 1272 AAC 1 per Phase Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls Normal Summer Rating
Note on M212: Author: Reference DRCW02-ESEQ-E72002 SH6 1272 AAC 1 per Phase Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls Normal Summer Rating
Note on N212: Author: Reference DRCW02-ESMV-E002001 SH1 DRCW02-ESEQ-E72002 SH6 DS2105B
Note on F217: Author: Reference DRCW01-ESMV-E01001 SH1 DRCW01-ESEQ-41001 SH1 2" SCH40 Al Tube Bus Rate per XEL-EVD-Facility Rating Supplement-Table-Tubular and Square Conductor.xls. Normal summer rating @ 4 ft/s
Note on G217: Author: Reference DRCW01-ESMV-E01001 SH1 DRCW01-ESEQ-41001 SH1 1272 AAC Conductor 1/ph Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls. Normal summer rating @ 4 ft/s
Note on H217: Author: Reference DRCW01-ESMV-E01001 SH1 DRCW01-ESEQ-41001 SH1 Current Limiting Reactor, 1200A, 1/ph
Note on I217: Author: Reference DRCW01-ESMV-E01001 SH1 DRCW01-ESEQ-41001 SH1 1272 AAC Conductor 1/ph Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls. Normal summer rating @ 4 ft/s
Note on J217: Author: Reference DRCW01-ESMV-E01001 SH1 DRCW01-ESEQ-41001 SH1 2" SCH40 Al Tube Bus - Both horizontal and vertical sections Rate per XEL-EVD-Facility Rating Supplement-Table-Tubular and Square Conductor.xls. Normal summer rating @ 4 ft/s
Note on K217: Author: Reference DRCW01-ESMV-E01001 SH1 DRCW01-ESEQ-41001 SH1 DRCW01-ESEQ-E71002 SH1 1272 AAC Conductor 1/ph Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls. Normal summer rating @ 4 ft/s
Note on L217: Author: Reference DRCW01-ESMV-E01001 SH2 DRCW01-ESEQ-41001 SH1 Disconnect Switch, 2000A, 1101F
Note on M217: Author: CT on feeder side of breaker 3000/5 amp MRCT at 3000 amp tap. Reference DRCW01-ESPT-E81001 SH2
Note on N217: Author: Reference DRCW01-ESMV-E01001 SH2 DRCW01-ESEQ-41001 SH1
Note on O217: Author: Reference DRCW01-ESMV-E01001 SH2 DRCW01-ESEQ-41001 SH1 Disconnect Switch, 2000A, 1101M
Note on P217: Author: CT on bus side of feeder breaker 3000/5 amp MRCT at 3000 amp tap. Reference DRCW01-ESPT-E81001 SH2
Note on Q217: Author: Reference DRCW01-ESMV-E01001 SH1 DRCW01-ESEQ-41001 SH1 DRCW01-ESEQ-E71002 SH1 1272 AAC Conductor 1/ph Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls. Normal summer rating @ 4 ft/s
Note on R217: Author: Reference DRCW01-ESMV-E01001 SH1 DRCW01-ESEQ-41001 SH1 DRCW01-ESEQ-E71002 SH1 1272 AAC Conductor 1/ph Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls. Normal summer rating @ 4 ft/s
Note on S217: Author: 51 pickup: 1300 A Primary 50 pickup: 1800 A Primary
Note on F218: Author: Reference DRCW01-ESMV-E01001 SH1 DRCW01-ESEQ-41001 SH1 2" SCH40 Al Tube Bus Rate per XEL-EVD-Facility Rating Supplement-Table-Tubular and Square Conductor.xls. Normal summer rating @ 4 ft/s
Note on G218: Author: Reference DRCW01-ESMV-E01001 SH1 DRCW01-ESEQ-41001 SH1 1272 AAC Conductor 1/ph Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls. Normal summer rating @ 4 ft/s
Note on H218: Author: Reference DRCW01-ESMV-E01001 SH1 DRCW01-ESEQ-41001 SH1 Current Limiting Reactor, 1200A, 1/ph
Note on I218: Author: Reference DRCW01-ESMV-E01001 SH1 DRCW01-ESEQ-41001 SH1 1272 AAC Conductor 1/ph Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls. Normal summer rating @ 4 ft/s
Note on J218: Author: Reference DRCW01-ESMV-E01001 SH1 DRCW01-ESEQ-41001 SH1 2" SCH40 Al Tube Bus - Both horizontal and vertical sections Rate per XEL-EVD-Facility Rating Supplement-Table-Tubular and Square Conductor.xls. Normal summer rating @ 4 ft/s
Note on K218: Author: Reference DRCW01-ESMV-E01001 SH1 DRCW01-ESEQ-41001 SH1 DRCW01-ESEQ-E71002 SH1 1272 AAC Conductor 1/ph Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls. Normal summer rating @ 4 ft/s
Note on L218: Author: Reference DRCW01-ESMV-E01001 SH2 DRCW01-ESEQ-41001 SH1 Disconnect Switch, 1200A, DS1102F
Note on M218: Author: CT on feeder side of breaker 3000/5 amp MRCT at 3000 amp tap. Reference DRCW01-ESPT-E81001 SH2
Note on N218: Author: Reference DRCW01-ESMV-E01001 SH2 DRCW01-ESEQ-41001 SH1
Note on O218: Author: Reference DRCW01-ESMV-E01001 SH2 DRCW01-ESEQ-41001 SH1 Disconnect Switch, 1200A, DS1102M
Note on P218: Author: CT on bus side of feeder breaker 3000/5 amp MRCT at 3000 amp tap. Reference DRCW01-ESPT-E81001 SH2
Note on Q218: Author: Reference DRCW01-ESMV-E01001 SH1 DRCW01-ESEQ-41001 SH1 DRCW01-ESEQ-E71002 SH1 1272 AAC Conductor 1/ph Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls. Normal summer rating @ 4 ft/s
Note on R218: Author: Reference DRCW01-ESMV-E01001 SH1 DRCW01-ESEQ-41001 SH1 DRCW01-ESEQ-E71002 SH1 1272 AAC Conductor 1/ph Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls. Normal summer rating @ 4 ft/s
Note on S218: Author: 51 pickup: 1300 A Primary 50 pickup: 1800 A Primary
Note on F219: Author: Reference DRCW01-ESMV-E01001 SH1 DRCW01-ESEQ-41001 SH1 2" SCH40 Al Tube Bus Rate per XEL-EVD-Facility Rating Supplement-Table-Tubular and Square Conductor.xls. Normal summer rating @ 4 ft/s
Note on G219: Author: Reference DRCW01-ESMV-E01001 SH1 DRCW01-ESEQ-41001 SH1 1272 AAC Conductor 1/ph Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls. Normal summer rating @ 4 ft/s
Note on H219: Author: Reference DRCW01-ESMV-E01001 SH1 DRCW01-ESEQ-41001 SH1 Current Limiting Reactor, 1200A, 1/ph
Note on I219: Author: Reference DRCW01-ESMV-E01001 SH1 DRCW01-ESEQ-41001 SH1 1272 AAC Conductor 1/ph Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls. Normal summer rating @ 4 ft/s
Note on J219: Author: Reference DRCW01-ESMV-E01001 SH1 DRCW01-ESEQ-41001 SH1 2" SCH40 Al Tube Bus - Both horizontal and vertical sections Rate per XEL-EVD-Facility Rating Supplement-Table-Tubular and Square Conductor.xls. Normal summer rating @ 4 ft/s
Note on K219: Author: Reference DRCW01-ESMV-E01001 SH1 DRCW01-ESEQ-41001 SH1 DRCW01-ESEQ-E71002 SH1 1272 AAC Conductor 1/ph Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls. Normal summer rating @ 4 ft/s
Note on L219: Author: Reference DRCW01-ESMV-E01001 SH2 DRCW01-ESEQ-41001 SH1 Disconnect Switch, 1200A, DS1103F
Note on M219: Author: CT on feeder side of breaker 3000/5 amp MRCT at 3000 amp tap. Reference DRCW01-ESPT-E81001 SH2
Note on N219: Author: Reference DRCW01-ESMV-E01001 SH2 DRCW01-ESEQ-41001 SH1
Note on O219: Author: Reference DRCW01-ESMV-E01001 SH2 DRCW01-ESEQ-41001 SH1 Disconnect Switch, 1200A, DS1103M
Note on P219: Author: CT on bus side of feeder breaker 3000/5 amp MRCT at 3000 amp tap. Reference DRCW01-ESPT-E81001 SH2
Note on Q219: Author: Reference DRCW01-ESMV-E01001 SH1 DRCW01-ESEQ-41001 SH1 DRCW01-ESEQ-E71002 SH1 1272 AAC Conductor 1/ph Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls. Normal summer rating @ 4 ft/s
Note on R219: Author: Reference DRCW01-ESMV-E01001 SH1 DRCW01-ESEQ-41001 SH1 DRCW01-ESEQ-E71002 SH1 1272 AAC Conductor 1/ph Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls. Normal summer rating @ 4 ft/s
Note on S219: Author: 51 pickup: 1300 A Primary 50 pickup: 1800 A Primary
Note on F220: Author: Reference DRCW01-ESMV-E01001 SH1 DRCW01-ESEQ-41001 SH1 2" SCH40 Al Tube Bus Rate per XEL-EVD-Facility Rating Supplement-Table-Tubular and Square Conductor.xls. Normal summer rating @ 4 ft/s
Note on G220: Author: Reference DRCW01-ESMV-E01001 SH1 DRCW01-ESEQ-41001 SH1 1272 AAC Conductor 1/ph Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls. Normal summer rating @ 4 ft/s
Note on H220: Author: Reference DRCW01-ESMV-E01001 SH1 DRCW01-ESEQ-41001 SH1 Current Limiting Reactor, 1200A, 1/ph
Note on I220: Author: Reference DRCW01-ESMV-E01001 SH1 DRCW01-ESEQ-41001 SH1 1272 AAC Conductor 1/ph Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls. Normal summer rating @ 4 ft/s
Note on J220: Author: Reference DRCW01-ESMV-E01001 SH1 DRCW01-ESEQ-41001 SH1 2" SCH40 Al Tube Bus - Both horizontal and vertical sections Rate per XEL-EVD-Facility Rating Supplement-Table-Tubular and Square Conductor.xls. Normal summer rating @ 4 ft/s
Note on K220: Author: Reference DRCW01-ESMV-E01001 SH1 DRCW01-ESEQ-41001 SH1 DRCW01-ESEQ-E71002 SH1 1272 AAC Conductor 1/ph Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls. Normal summer rating @ 4 ft/s
Note on L220: Author: Reference DRCW01-ESMV-E01001 SH2 DRCW01-ESEQ-41001 SH1 Disconnect Switch, 1200A, DS1104F
Note on M220: Author: CT on feeder side of breaker 3000/5 amp MRCT at 3000 amp tap. Reference DRCW01-ESPT-E81001 SH2
Note on N220: Author: Reference DRCW01-ESMV-E01001 SH2 DRCW01-ESEQ-41001 SH1
Note on O220: Author: Reference DRCW01-ESMV-E01001 SH2 DRCW01-ESEQ-41001 SH1 Disconnect Switch, 1200A, DS1104M
Note on P220: Author: CT on bus side of feeder breaker 3000/5 amp MRCT at 3000 amp tap. Reference DRCW01-ESPT-E81001 SH2
Note on Q220: Author: Reference DRCW01-ESMV-E01001 SH1 DRCW01-ESEQ-41001 SH1 DRCW01-ESEQ-E71002 SH1 1272 AAC Conductor 1/ph Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls. Normal summer rating @ 4 ft/s
Note on R220: Author: Reference DRCW01-ESMV-E01001 SH1 DRCW01-ESEQ-41001 SH1 DRCW01-ESEQ-E71002 SH1 1272 AAC Conductor 1/ph Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls. Normal summer rating @ 4 ft/s
Note on S220: Author: 51 pickup: 1300 A Primary 50 pickup: 1800 A Primary
Note on F221: Author: Reference DRCW01-ESMV-E01001 SH1 DRCW01-ESEQ-41001 SH1 2" SCH40 Al Tube Bus Rate per XEL-EVD-Facility Rating Supplement-Table-Tubular and Square Conductor.xls. Normal summer rating @ 4 ft/s
Note on G221: Author: Reference DRCW01-ESMV-E01001 SH1 DRCW01-ESEQ-41001 SH1 1272 AAC Conductor 1/ph Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls. Normal summer rating @ 4 ft/s
Note on H221: Author: Reference DRCW01-ESMV-E01001 SH1 DRCW01-ESEQ-41001 SH1 Current Limiting Reactor, 1200A, 1/ph
Note on I221: Author: Reference DRCW01-ESMV-E01001 SH1 DRCW01-ESEQ-41001 SH1 1272 AAC Conductor 1/ph Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls. Normal summer rating @ 4 ft/s
Note on J221: Author: Reference DRCW01-ESMV-E01001 SH1 DRCW01-ESEQ-41001 SH1 2" SCH40 Al Tube Bus - Both horizontal and vertical sections Rate per XEL-EVD-Facility Rating Supplement-Table-Tubular and Square Conductor.xls. Normal summer rating @ 4 ft/s
Note on K221: Author: Reference DRCW01-ESMV-E01001 SH1 DRCW01-ESEQ-41001 SH1 DRCW01-ESEQ-E71002 SH1 1272 AAC Conductor 1/ph Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls. Normal summer rating @ 4 ft/s
Note on L221: Author: Reference DRCW01-ESMV-E01001 SH2 DRCW01-ESEQ-41001 SH1 Disconnect Switch, 1200A, DS1201F
Note on M221: Author: CT on feeder side of breaker 3000/5 amp MRCT at 3000 amp tap. Reference DRCW01-ESPT-E81001 SH2
Note on N221: Author: Reference DRCW01-ESMV-E01001 SH2 DRCW01-ESEQ-41001 SH1
Note on O221: Author: Reference DRCW01-ESMV-E01001 SH2 DRCW01-ESEQ-41001 SH1 Disconnect Switch, 1200A, DS1201M
Note on P221: Author: CT on bus side of feeder breaker 3000/5 amp MRCT at 3000 amp tap. Reference DRCW01-ESPT-E81001 SH2
Note on Q221: Author: Reference DRCW01-ESMV-E01001 SH1 DRCW01-ESEQ-41001 SH1 DRCW01-ESEQ-E71002 SH1 1272 AAC Conductor 1/ph Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls. Normal summer rating @ 4 ft/s
Note on R221: Author: Reference DRCW01-ESMV-E01001 SH1 DRCW01-ESEQ-41001 SH1 DRCW01-ESEQ-E71002 SH1 1272 AAC Conductor 1/ph Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls. Normal summer rating @ 4 ft/s
Note on S221: Author: 51 pickup: 1300 A Primary 50 pickup: 1800 A Primary
Note on F222: Author: Reference DRCW01-ESMV-E01001 SH1 DRCW01-ESEQ-41001 SH1 2" SCH40 Al Tube Bus Rate per XEL-EVD-Facility Rating Supplement-Table-Tubular and Square Conductor.xls. Normal summer rating @ 4 ft/s
Note on G222: Author: Reference DRCW01-ESMV-E01001 SH1 DRCW01-ESEQ-41001 SH1 1272 AAC Conductor 1/ph Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls. Normal summer rating @ 4 ft/s
Note on H222: Author: Reference DRCW01-ESMV-E01001 SH1 DRCW01-ESEQ-41001 SH1 Current Limiting Reactor, 1200A, 1/ph
Note on I222: Author: Reference DRCW01-ESMV-E01001 SH1 DRCW01-ESEQ-41001 SH1 1272 AAC Conductor 1/ph Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls. Normal summer rating @ 4 ft/s
Note on J222: Author: Reference DRCW01-ESMV-E01001 SH1 DRCW01-ESEQ-41001 SH1 2" SCH40 Al Tube Bus - Both horizontal and vertical sections Rate per XEL-EVD-Facility Rating Supplement-Table-Tubular and Square Conductor.xls. Normal summer rating @ 4 ft/s
Note on K222: Author: Reference DRCW01-ESMV-E01001 SH1 DRCW01-ESEQ-41001 SH1 DRCW01-ESEQ-E71002 SH1 1272 AAC Conductor 1/ph Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls. Normal summer rating @ 4 ft/s
Note on L222: Author: Reference DRCW01-ESMV-E01001 SH2 DRCW01-ESEQ-41001 SH1 Disconnect Switch, 1200A, DS1202F
Note on M222: Author: CT on feeder side of breaker 3000/5 amp MRCT at 3000 amp tap. Reference DRCW01-ESPT-E81001 SH2
Note on N222: Author: Reference DRCW01-ESMV-E01001 SH2 DRCW01-ESEQ-41001 SH1
Note on O222: Author: Reference DRCW01-ESMV-E01001 SH2 DRCW01-ESEQ-41001 SH1 Disconnect Switch, 1200A, DS1202M
Note on P222: Author: CT on bus side of feeder breaker 3000/5 amp MRCT at 3000 amp tap. Reference DRCW01-ESPT-E81001 SH2
Note on Q222: Author: Reference DRCW01-ESMV-E01001 SH1 DRCW01-ESEQ-41001 SH1 DRCW01-ESEQ-E71002 SH1 1272 AAC Conductor 1/ph Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls. Normal summer rating @ 4 ft/s
Note on R222: Author: Reference DRCW01-ESMV-E01001 SH1 DRCW01-ESEQ-41001 SH1 DRCW01-ESEQ-E71002 SH1 1272 AAC Conductor 1/ph Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls. Normal summer rating @ 4 ft/s
Note on S222: Author: 51 pickup: 1300 A Primary 50 pickup: 1800 A Primary
Note on F223: Author: Reference DRCW01-ESMV-E01001 SH1 DRCW01-ESEQ-41001 SH1 2" SCH40 Al Tube Bus Rate per XEL-EVD-Facility Rating Supplement-Table-Tubular and Square Conductor.xls. Normal summer rating @ 4 ft/s
Note on G223: Author: Reference DRCW01-ESMV-E01001 SH1 DRCW01-ESEQ-41001 SH1 1272 AAC Conductor 1/ph Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls. Normal summer rating @ 4 ft/s
Note on H223: Author: Reference DRCW01-ESMV-E01001 SH1 DRCW01-ESEQ-41001 SH1 Current Limiting Reactor, 1200A, 1/ph
Note on I223: Author: Reference DRCW01-ESMV-E01001 SH1 DRCW01-ESEQ-41001 SH1 1272 AAC Conductor 1/ph Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls. Normal summer rating @ 4 ft/s
Note on J223: Author: Reference DRCW01-ESMV-E01001 SH1 DRCW01-ESEQ-41001 SH1 2" SCH40 Al Tube Bus - Both horizontal and vertical sections Rate per XEL-EVD-Facility Rating Supplement-Table-Tubular and Square Conductor.xls. Normal summer rating @ 4 ft/s
Note on K223: Author: Reference DRCW01-ESMV-E01001 SH1 DRCW01-ESEQ-41001 SH1 DRCW01-ESEQ-E71002 SH1 1272 AAC Conductor 1/ph Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls. Normal summer rating @ 4 ft/s
Note on L223: Author: Reference DRCW01-ESEQ-E71002 SH6 DRCW01-ESEQ-E41001 SH1 DS1203 and DS1203F
Note on M223: Author: CT on feeder side of breaker 3000/5 amp MRCT at 3000 amp tap. Reference DRCW01-ESPT-E81001 SH2
Note on N223: Author: Reference DRCW01-ESEQ-E71002 SH6 DRCW01-ESEQ-E41001 SH1
Note on O223: Author: Reference DRCW01-ESEQ-E71002 SH6 DRCW01-ESEQ-E41001 SH1 DS1203M
Note on P223: Author: CT on bus side of feeder breaker 3000/5 amp MRCT at 3000 amp tap. Reference DRCW01-ESPT-E81001 SH2
Note on Q223: Author: Reference DRCW01-ESMV-E01001 SH1 DRCW01-ESEQ-41001 SH1 DRCW01-ESEQ-E71002 SH1 1272 AAC Conductor 1/ph Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls. Normal summer rating @ 4 ft/s
Note on R223: Author: Reference DRCW01-ESMV-E01001 SH1 DRCW01-ESEQ-41001 SH1 DRCW01-ESEQ-E71002 SH1 1272 AAC Conductor 1/ph Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls. Normal summer rating @ 4 ft/s
Note on S223: Author: 51 pickup: 1300 A Primary 50 pickup: 1800 A Primary
Note on F224: Author: Reference DRCW01-ESMV-E01001 SH1 DRCW01-ESEQ-41001 SH1 2" SCH40 Al Tube Bus Rate per XEL-EVD-Facility Rating Supplement-Table-Tubular and Square Conductor.xls. Normal summer rating @ 4 ft/s
Note on G224: Author: Reference DRCW01-ESMV-E01001 SH1 DRCW01-ESEQ-41001 SH1 1272 AAC Conductor 1/ph Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls. Normal summer rating @ 4 ft/s
Note on H224: Author: Reference DRCW01-ESMV-E01001 SH1 DRCW01-ESEQ-41001 SH1 Current Limiting Reactor, 1200A, 1/ph
Note on I224: Author: Reference DRCW01-ESMV-E01001 SH1 DRCW01-ESEQ-41001 SH1 1272 AAC Conductor 1/ph Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls. Normal summer rating @ 4 ft/s
Note on J224: Author: Reference DRCW01-ESMV-E01001 SH1 DRCW01-ESEQ-41001 SH1 2" SCH40 Al Tube Bus - Both horizontal and vertical sections Rate per XEL-EVD-Facility Rating Supplement-Table-Tubular and Square Conductor.xls. Normal summer rating @ 4 ft/s
Note on K224: Author: Reference DRCW01-ESMV-E01001 SH1 DRCW01-ESEQ-41001 SH1 DRCW01-ESEQ-E71002 SH1 1272 AAC Conductor 1/ph Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls. Normal summer rating @ 4 ft/s
Note on L224: Author: Reference DRCW01-ESMV-E01001 SH2 DRCW01-ESEQ-41001 SH1 Disconnect Switch, 2000A, 1204F
Note on M224: Author: CT on feeder side of breaker 3000/5 amp MRCT at 3000 amp tap. Reference DRCW01-ESPT-E81001 SH2
Note on N224: Author: Reference DRCW01-ESMV-E01001 SH2 DRCW01-ESEQ-41001 SH1
Note on O224: Author: Reference DRCW01-ESMV-E01001 SH2 DRCW01-ESEQ-41001 SH1 Disconnect Switch, 1200A, DS1204M
Note on P224: Author: CT on bus side of feeder breaker 3000/5 amp MRCT at 3000 amp tap. Reference DRCW01-ESPT-E81001 SH2
Note on Q224: Author: Reference DRCW01-ESMV-E01001 SH1 DRCW01-ESEQ-41001 SH1 DRCW01-ESEQ-E71002 SH1 1272 AAC Conductor 1/ph Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls. Normal summer rating @ 4 ft/s
Note on R224: Author: Reference DRCW01-ESMV-E01001 SH1 DRCW01-ESEQ-41001 SH1 DRCW01-ESEQ-E71002 SH1 1272 AAC Conductor 1/ph Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls. Normal summer rating @ 4 ft/s
Note on S224: Author: 51 pickup: 1300 A Primary 50 pickup: 1800 A Primary
Note on F225: Author: Reference DRCW02-ESMV-E02001 SH1 DRCW02-ESEQ-42001 SH1 2" SCH40 Al Tube Bus Rate per XEL-EVD-Facility Rating Supplement-Table-Tubular and Square Conductor.xls. Normal summer rating @ 4 ft/s
Note on G225: Author: Reference DRCW02-ESMV-E02001 SH1 DRCW02-ESEQ-42001 SH1 1272 AAC Conductor 1/ph Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls. Normal summer rating @ 4 ft/s
Note on H225: Author: Reference DRCW02-ESMV-E02001 SH1 DRCW02-ESEQ-42001 SH1 Current Limiting Reactor, 1200A, 1/ph
Note on I225: Author: Reference DRCW02-ESMV-E02001 SH1 DRCW02-ESEQ-42001 SH1 1272 AAC Conductor 1/ph Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls. Normal summer rating @ 4 ft/s
Note on J225: Author: Reference DRCW02-ESMV-E02001 SH1 DRCW02-ESEQ-42001 SH1 2" SCH40 Al Tube Bus - Both horizontal and vertical sections Rate per XEL-EVD-Facility Rating Supplement-Table-Tubular and Square Conductor.xls. Normal summer rating @ 4 ft/s
Note on K225: Author: Reference DRCW02-ESMV-E02001 SH1 DRCW02-ESEQ-42001 SH1 DRCW02-ESEQ-E72002 SH1 1272 AAC Conductor 1/ph Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls. Normal summer rating @ 4 ft/s
Note on L225: Author: Reference DRCW02-ESMV-E02001 SH2 DRCW02-ESEQ-42001 SH1 Disconnect Switch, 2000A, 2101F
Note on M225: Author: CT on feeder side of breaker 3000/5 amp MRCT at 3000 amp tap. Reference DRCW02-ESPT-E82001 SH2
Note on N225: Author: Reference DRCW02-ESMV-E02001 SH2 DRCW02-ESEQ-42001 SH1
Note on O225: Author: Reference DRCW02-ESMV-E02001 SH2 DRCW02-ESEQ-42001 SH1 Disconnect Switch, 2000A, 2101M
Note on P225: Author: CT on bus side of breaker 3000/5 amp MRCT at 3000 amp tap. Reference DRCW02-ESPT-E82001 SH2
Note on Q225: Author: Reference DRCW02-ESMV-E02001 SH1 DRCW02-ESEQ-42001 SH1 DRCW02-ESEQ-E72002 SH1 1272 AAC Conductor 1/ph Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls. Normal summer rating @ 4 ft/s
Note on R225: Author: Reference DRCW02-ESMV-E02001 SH1 DRCW02-ESEQ-42001 SH1 DRCW02-ESEQ-E72002 SH1 1272 AAC Conductor 1/ph Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls. Normal summer rating @ 4 ft/s
Note on S225: Author: 51 Pickup: 1250A 50 Pickup: 2304A
Note on F226: Author: Reference DRCW02-ESMV-E02001 SH1 DRCW02-ESEQ-42001 SH1 2" SCH40 Al Tube Bus Rate per XEL-EVD-Facility Rating Supplement-Table-Tubular and Square Conductor.xls. Normal summer rating @ 4 ft/s
Note on G226: Author: Reference DRCW02-ESMV-E02001 SH1 DRCW02-ESEQ-42001 SH1 1272 AAC Conductor 1/ph Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls. Normal summer rating @ 4 ft/s
Note on H226: Author: Reference DRCW02-ESMV-E02001 SH1 DRCW02-ESEQ-42001 SH1 Current Limiting Reactor, 1200A, 1/ph
Note on I226: Author: Reference DRCW02-ESMV-E02001 SH1 DRCW02-ESEQ-42001 SH1 1272 AAC Conductor 1/ph Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls. Normal summer rating @ 4 ft/s
Note on J226: Author: Reference DRCW02-ESMV-E02001 SH1 DRCW02-ESEQ-42001 SH1 2" SCH40 Al Tube Bus - Both horizontal and vertical sections Rate per XEL-EVD-Facility Rating Supplement-Table-Tubular and Square Conductor.xls. Normal summer rating @ 4 ft/s
Note on K226: Author: Reference DRCW02-ESMV-E02001 SH1 DRCW02-ESEQ-42001 SH1 DRCW02-ESEQ-E72002 SH1 1272 AAC Conductor 1/ph Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls. Normal summer rating @ 4 ft/s
Note on L226: Author: Reference DRCW02-ESMV-E02001 SH2 DRCW02-ESEQ-42001 SH1 2102F
Note on M226: Author: CT on feeder side of breaker 3000/5 amp MRCT at 3000 amp tap. Reference DRCW02-ESPT-E82001 SH2
Note on N226: Author: Reference DRCW02-ESMV-E02001 SH2 DRCW02-ESEQ-42001 SH1
Note on O226: Author: Reference DRCW02-ESMV-E02001 SH2 DRCW02-ESEQ-42001 SH1 2102M
Note on P226: Author: CT on bus side of breaker 3000/5 amp MRCT at 3000 amp tap. Reference DRCW02-ESPT-E82001 SH2
Note on Q226: Author: Reference DRCW02-ESMV-E02001 SH1 DRCW02-ESEQ-42001 SH1 DRCW02-ESEQ-E72002 SH1 1272 AAC Conductor 1/ph Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls. Normal summer rating @ 4 ft/s
Note on R226: Author: Reference DRCW02-ESMV-E02001 SH1 DRCW02-ESEQ-42001 SH1 DRCW02-ESEQ-E72002 SH1 1272 AAC Conductor 1/ph Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls. Normal summer rating @ 4 ft/s
Note on S226: Author: 51 Pickup: 1250A 50 Pickup: 2304A
Note on F227: Author: Reference DRCW02-ESMV-E02001 SH1 DRCW02-ESEQ-42001 SH1 2" SCH40 Al Tube Bus Rate per XEL-EVD-Facility Rating Supplement-Table-Tubular and Square Conductor.xls. Normal summer rating @ 4 ft/s
Note on G227: Author: Reference DRCW02-ESMV-E02001 SH1 DRCW02-ESEQ-42001 SH1 1272 AAC Conductor 1/ph Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls. Normal summer rating @ 4 ft/s
Note on H227: Author: Reference DRCW02-ESMV-E02001 SH1 DRCW02-ESEQ-42001 SH1 Current Limiting Reactor, 1200A, 1/ph
Note on I227: Author: Reference DRCW02-ESMV-E02001 SH1 DRCW02-ESEQ-42001 SH1 1272 AAC Conductor 1/ph Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls. Normal summer rating @ 4 ft/s
Note on J227: Author: Reference DRCW02-ESMV-E02001 SH1 DRCW02-ESEQ-42001 SH1 2" SCH40 Al Tube Bus - Both horizontal and vertical sections Rate per XEL-EVD-Facility Rating Supplement-Table-Tubular and Square Conductor.xls. Normal summer rating @ 4 ft/s
Note on K227: Author: Reference DRCW02-ESMV-E02001 SH1 DRCW02-ESEQ-42001 SH1 DRCW02-ESEQ-E72002 SH1 1272 AAC Conductor 1/ph Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls. Normal summer rating @ 4 ft/s
Note on L227: Author: Reference DRCW02-ESMV-E02001 SH2 DRCW02-ESEQ-42001 SH1 2103F
Note on M227: Author: CT on feeder side of breaker 3000/5 amp MRCT at 3000 amp tap. Reference DRCW02-ESPT-E82001 SH2
Note on N227: Author: Reference DRCW02-ESMV-E02001 SH2 DRCW02-ESEQ-42001 SH1
Note on O227: Author: Reference DRCW02-ESMV-E02001 SH2 DRCW02-ESEQ-42001 SH1 2103M
Note on P227: Author: CT on bus side of breaker 3000/5 amp MRCT at 3000 amp tap. Reference DRCW02-ESPT-E82001 SH2
Note on Q227: Author: Reference DRCW02-ESMV-E02001 SH1 DRCW02-ESEQ-42001 SH1 DRCW02-ESEQ-E72002 SH1 1272 AAC Conductor 1/ph Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls. Normal summer rating @ 4 ft/s
Note on R227: Author: Reference DRCW02-ESMV-E02001 SH1 DRCW02-ESEQ-42001 SH1 DRCW02-ESEQ-E72002 SH1 1272 AAC Conductor 1/ph Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls. Normal summer rating @ 4 ft/s
Note on S227: Author: 51 Pickup: 1250A 50 Pickup: 2304A
Note on F228: Author: Reference DRCW02-ESMV-E02001 SH1 DRCW02-ESEQ-42001 SH1 2" SCH40 Al Tube Bus Rate per XEL-EVD-Facility Rating Supplement-Table-Tubular and Square Conductor.xls. Normal summer rating @ 4 ft/s
Note on G228: Author: Reference DRCW02-ESMV-E02001 SH1 DRCW02-ESEQ-42001 SH1 1272 AAC Conductor 1/ph Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls. Normal summer rating @ 4 ft/s
Note on H228: Author: Reference DRCW02-ESMV-E02001 SH1 DRCW02-ESEQ-42001 SH1 Current Limiting Reactor, 1200A, 1/ph
Note on I228: Author: Reference DRCW02-ESMV-E02001 SH1 DRCW02-ESEQ-42001 SH1 1272 AAC Conductor 1/ph Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls. Normal summer rating @ 4 ft/s
Note on J228: Author: Reference DRCW02-ESMV-E02001 SH1 DRCW02-ESEQ-42001 SH1 2" SCH40 Al Tube Bus - Both horizontal and vertical sections Rate per XEL-EVD-Facility Rating Supplement-Table-Tubular and Square Conductor.xls. Normal summer rating @ 4 ft/s
Note on K228: Author: Reference DRCW02-ESMV-E02001 SH1 DRCW02-ESEQ-42001 SH1 DRCW02-ESEQ-E72002 SH1 1272 AAC Conductor 1/ph Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls. Normal summer rating @ 4 ft/s
Note on L228: Author: Reference DRCW02-ESMV-E02001 SH2 DRCW02-ESEQ-42001 SH1 2104F
Note on M228: Author: CT on feeder side of breaker 3000/5 amp MRCT at 3000 amp tap. Reference DRCW02-ESPT-E82001 SH2
Note on N228: Author: Reference DRCW02-ESMV-E02001 SH2 DRCW02-ESEQ-42001 SH1
Note on O228: Author: Reference DRCW02-ESMV-E02001 SH2 DRCW02-ESEQ-42001 SH1 2104M
Note on P228: Author: CT on bus side of breaker 3000/5 amp MRCT at 3000 amp tap. Reference DRCW02-ESPT-E82001 SH2
Note on Q228: Author: Reference DRCW02-ESMV-E02001 SH1 DRCW02-ESEQ-42001 SH1 DRCW02-ESEQ-E72002 SH1 1272 AAC Conductor 1/ph Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls. Normal summer rating @ 4 ft/s
Note on R228: Author: Reference DRCW02-ESMV-E02001 SH1 DRCW02-ESEQ-42001 SH1 DRCW02-ESEQ-E72002 SH1 1272 AAC Conductor 1/ph Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls. Normal summer rating @ 4 ft/s
Note on S228: Author: 51 Pickup: 1250A 50 Pickup: 2304A
Note on F229: Author: Reference DRCW02-ESMV-E02001 SH1 DRCW02-ESEQ-42001 SH1 2" SCH40 Al Tube Bus Rate per XEL-EVD-Facility Rating Supplement-Table-Tubular and Square Conductor.xls. Normal summer rating @ 4 ft/s
Note on G229: Author: Reference DRCW02-ESMV-E02001 SH1 DRCW02-ESEQ-42001 SH1 1272 AAC Conductor 1/ph Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls. Normal summer rating @ 4 ft/s
Note on H229: Author: Reference DRCW02-ESMV-E02001 SH1 DRCW02-ESEQ-42001 SH1 Current Limiting Reactor, 1200A, 1/ph
Note on I229: Author: Reference DRCW02-ESMV-E02001 SH1 DRCW02-ESEQ-42001 SH1 1272 AAC Conductor 1/ph Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls. Normal summer rating @ 4 ft/s
Note on J229: Author: Reference DRCW02-ESMV-E02001 SH1 DRCW02-ESEQ-42001 SH1 2" SCH40 Al Tube Bus - Both horizontal and vertical sections Rate per XEL-EVD-Facility Rating Supplement-Table-Tubular and Square Conductor.xls. Normal summer rating @ 4 ft/s
Note on K229: Author: Reference DRCW02-ESMV-E02001 SH1 DRCW02-ESEQ-42001 SH1 DRCW02-ESEQ-E72002 SH1 1272 AAC Conductor 1/ph Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls. Normal summer rating @ 4 ft/s
Note on L229: Author: Reference DRCW02-ESMV-E02001 SH2 DRCW02-ESEQ-42001 SH1 2105F
Note on M229: Author: CT on feeder side of breaker 3000/5 amp MRCT at 3000 amp tap. Reference DRCW02-ESPT-E82001 SH2
Note on N229: Author: Reference DRCW02-ESMV-E02001 SH2 DRCW02-ESEQ-42001 SH1
Note on O229: Author: Reference DRCW02-ESMV-E02001 SH2 DRCW02-ESEQ-42001 SH1 2105M
Note on P229: Author: CT on bus side of breaker 3000/5 amp MRCT at 3000 amp tap. Reference DRCW02-ESPT-E82001 SH2
Note on Q229: Author: Reference DRCW02-ESMV-E02001 SH1 DRCW02-ESEQ-42001 SH1 DRCW02-ESEQ-E72002 SH1 1272 AAC Conductor 1/ph Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls. Normal summer rating @ 4 ft/s
Note on R229: Author: Reference DRCW02-ESMV-E02001 SH1 DRCW02-ESEQ-42001 SH1 DRCW02-ESEQ-E72002 SH1 1272 AAC Conductor 1/ph Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls. Normal summer rating @ 4 ft/s
Note on S229: Author: 51 Pickup: 1250A 50 Pickup: 2304A
Note on C234: Author: Cap bank MVAR rating Reference DRCW01-ESGA-E01001 SH1
Note on F234: Author: From Drawing CEB17012 SH.1 Connection is 750MCM Aluminum. Referencing XEL-EVD-Facility Rating Supplement- table - Bare Overhead Conductor summer rataing is 737A at 4ft /sec wind speed
Note on G234: Author: Cap Switcher 1153 Reference DRCW01-ESMV-E01001 SH5
Note on H234: Author: Reference DRCW01-ESMV-E01001 SH5 DRCW01-ESEQ-41001 SH1 1272 AAC Conductor 1/ph Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls. Normal summer rating @ 4 ft/s
Note on C235: Author: Cap bank MVAR rating Reference DRCW01-ESGA-E01001 SH1
Note on F235: Author: From Drawing CEB17012 SH.1 Connection is 750MCM Aluminum. Referencing XEL-EVD-Facility Rating Supplement- table - Bare Overhead Conductor summer rataing is 737A at 4ft /sec wind speed
Note on G235: Author: Cap Switcher 1154 Reference DRCW01-ESMV-E01001 SH5
Note on H235: Author: Reference DRCW01-ESMV-E01001 SH5 DRCW01-ESEQ-41001 SH1 1272 AAC Conductor 1/ph Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls. Normal summer rating @ 4 ft/s
Note on C236: Author: Cap bank MVAR rating Reference DRCW01-ESGA-E01001 SH1
Note on F236: Author: From Drawing CEB17012 SH.1 Connection is 750MCM Aluminum. Referencing XEL-EVD-Facility Rating Supplement- table - Bare Overhead Conductor summer rataing is 737A at 4ft /sec wind speed
Note on G236: Author: Cap Switcher 1155 Reference DRCW01-ESMV-E01001 SH5
Note on H236: Author: Reference DRCW01-ESMV-E01001 SH5 DRCW01-ESEQ-41001 SH1 1272 AAC Conductor 1/ph Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls. Normal summer rating @ 4 ft/s
Note on C237: Author: Cap bank MVAR rating Reference DRCW01-ESGA-E01001 SH1
Note on F237: Author: From Drawing CEB17012 SH.1 Connection is 750MCM Aluminum. Referencing XEL-EVD-Facility Rating Supplement- table - Bare Overhead Conductor summer rataing is 737A at 4ft /sec wind speed
Note on G237: Author: Cap Switcher 1253 Reference DRCW01-ESMV-E01001 SH4
Note on H237: Author: Reference DRCW01-ESMV-E01001 SH4 DRCW01-ESEQ-41001 SH1 1272 AAC Conductor 1/ph Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls. Normal summer rating @ 4 ft/s
Note on C238: Author: Cap bank MVAR rating Reference DRCW01-ESGA-E01001 SH1
Note on F238: Author: From Drawing CEB17012 SH.1 Connection is 750MCM Aluminum. Referencing XEL-EVD-Facility Rating Supplement- table - Bare Overhead Conductor summer rataing is 737A at 4ft /sec wind speed
Note on G238: Author: Cap Switcher 1254 Reference DRCW01-ESMV-E01001 SH4
Note on H238: Author: Reference DRCW01-ESMV-E01001 SH4 DRCW01-ESEQ-41001 SH1 1272 AAC Conductor 1/ph Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls. Normal summer rating @ 4 ft/s
Note on C239: Author: Cap bank MVAR rating Reference DRCW01-ESGA-E01001 SH1
Note on F239: Author: From Drawing CEB17012 SH.1 Connection is 750MCM Aluminum. Referencing XEL-EVD-Facility Rating Supplement- table - Bare Overhead Conductor summer rataing is 737A at 4ft /sec wind speed
Note on G239: Author: Cap Switcher 1255 Reference DRCW01-ESMV-E01001 SH4
Note on H239: Author: Reference DRCW01-ESMV-E01001 SH4 DRCW01-ESEQ-41001 SH1 1272 AAC Conductor 1/ph Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls. Normal summer rating @ 4 ft/s
Note on C240: Author: Cap bank MVAR rating Reference DRCW02-ESGA-E02001 SH1
Note on F240: Author: From Drawing CEB17012 SH.1 Connection is 750MCM Aluminum. Referencing XEL-EVD-Facility Rating Supplement- table - Bare Overhead Conductor summer rataing is 737A at 4ft /sec wind speed
Note on G240: Author: Cap Switcher 2153 Reference DRCW01-ESMV-E01001 SH4
Note on H240: Author: Reference DRCW02-ESMV-E02001 SH4 DRCW02-ESEQ-42001 SH1 1272 AAC Conductor 1/ph Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls. Normal summer rating @ 4 ft/s
Note on C241: Author: Cap bank MVAR rating Reference DRCW02-ESGA-E02001 SH1
Note on F241: Author: From Drawing CEB17012 SH.1 Connection is 750MCM Aluminum. Referencing XEL-EVD-Facility Rating Supplement- table - Bare Overhead Conductor summer rataing is 737A at 4ft /sec wind speed
Note on G241: Author: Cap Switcher 2154 Reference DRCW01-ESMV-E01001 SH4
Note on H241: Author: Reference DRCW02-ESMV-E02001 SH4 DRCW02-ESEQ-42001 SH1 1272 AAC Conductor 1/ph Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls. Normal summer rating @ 4 ft/s
Note on C242: Author: Cap bank MVAR rating Reference DRCW02-ESGA-E02001 SH1
Note on F242: Author: From Drawing CEB17012 SH.1 Connection is 750MCM Aluminum. Referencing XEL-EVD-Facility Rating Supplement- table - Bare Overhead Conductor summer rataing is 737A at 4ft /sec wind speed
Note on G242: Author: Cap Switcher 2155 Reference DRCW01-ESMV-E01001 SH4
Note on H242: Author: Reference DRCW02-ESMV-E02001 SH4 DRCW02-ESEQ-42001 SH1 1272 AAC Conductor 1/ph Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls. Normal summer rating @ 4 ft/s
Note on C247: Author: Reference DRCW01-ESGA-E01001 SH1
Note on F247: Author: Reference DRCW01-ESMV-E01001 SH3 DRCW01-ESEQ-41001 SH1 1272 AAC Conductor 1/ph Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls. Normal summer rating @ 4 ft/s
Note on G247: Author: Reference DRCW01-ESMV-E01001 SH3 DRCW01-ESEQ-41001 SH1 2" SCH40 Al Tube Bus Rate per XEL-EVD-Facility Rating Supplement-Table-Tubular and Square Conductor.xls. Normal summer rating @ 4 ft/s
Note on H247: Author: Reference DRCW01-ESMV-E01001 SH3 DRCW01-ESEQ-41001 SH1 1272 AAC Conductor 1/ph Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls. Normal summer rating @ 4 ft/s
Note on I247: Author: Reactor Switcher 1151 Reference DRCW01-ESMV-E01001 SH3
Note on J247: Author: Reference DRCW01-ESMV-E01001 SH3 DRCW01-ESEQ-41001 SH1 1272 AAC Conductor 1/ph Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls. Normal summer rating @ 4 ft/s
Note on C248: Author: Reference DRCW01-ESGA-E01001 SH1
Note on F248: Author: Reference DRCW01-ESMV-E01001 SH3 DRCW01-ESEQ-41001 SH1 1272 AAC Conductor 1/ph Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls. Normal summer rating @ 4 ft/s
Note on G248: Author: Reference DRCW01-ESMV-E01001 SH3 DRCW01-ESEQ-41001 SH1 2" SCH40 Al Tube Bus Rate per XEL-EVD-Facility Rating Supplement-Table-Tubular and Square Conductor.xls. Normal summer rating @ 4 ft/s
Note on H248: Author: Reference DRCW01-ESMV-E01001 SH3 DRCW01-ESEQ-41001 SH1 1272 AAC Conductor 1/ph Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls. Normal summer rating @ 4 ft/s
Note on I248: Author: Reactor Switcher 1152 Reference DRCW01-ESMV-E01001 SH3
Note on J248: Author: Reference DRCW01-ESMV-E01001 SH3 DRCW01-ESEQ-41001 SH1 1272 AAC Conductor 1/ph Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls. Normal summer rating @ 4 ft/s
Note on C249: Author: Reference DRCW01-ESGA-E01001 SH1
Note on F249: Author: Reference DRCW01-ESMV-E01001 SH3 DRCW01-ESEQ-41001 SH1 1272 AAC Conductor 1/ph Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls. Normal summer rating @ 4 ft/s
Note on G249: Author: Reference DRCW01-ESMV-E01001 SH3 DRCW01-ESEQ-41001 SH1 2" SCH40 Al Tube Bus Rate per XEL-EVD-Facility Rating Supplement-Table-Tubular and Square Conductor.xls. Normal summer rating @ 4 ft/s
Note on H249: Author: Reference DRCW01-ESMV-E01001 SH3 DRCW01-ESEQ-41001 SH1 1272 AAC Conductor 1/ph Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls. Normal summer rating @ 4 ft/s
Note on I249: Author: Reactor Switcher 1251 Reference DRCW01-ESMV-E01001 SH3
Note on J249: Author: Reference DRCW01-ESMV-E01001 SH3 DRCW01-ESEQ-41001 SH1 1272 AAC Conductor 1/ph Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls. Normal summer rating @ 4 ft/s
Note on C250: Author: Reference DRCW02-ESGA-E02001 SH1
Note on F250: Author: Reference DRCW02-ESMV-E02001 SH3 DRCW02-ESEQ-42001 SH1 1272 AAC Conductor 1/ph Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls. Normal summer rating @ 4 ft/s
Note on G250: Author: Reference DRCW02-ESMV-E02001 SH3 DRCW02-ESEQ-42001 SH1 2" SCH40 Al Tube Bus Rate per XEL-EVD-Facility Rating Supplement-Table-Tubular and Square Conductor.xls. Normal summer rating @ 4 ft/s
Note on H250: Author: Reference DRCW02-ESMV-E02001 SH3 DRCW02-ESEQ-42001 SH1 1272 AAC Conductor 1/ph Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls. Normal summer rating @ 4 ft/s
Note on I250: Author: Reactor Switcher 2151 Reference DRCW02-ESMV-E02001 SH3
Note on J250: Author: Reference DRCW02-ESMV-E02001 SH3 DRCW02-ESEQ-42001 SH1 1272 AAC Conductor 1/ph Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls. Normal summer rating @ 4 ft/s
Note on C251: Author: Reference DRCW02-ESGA-E02001 SH1
Note on F251: Author: Reference DRCW02-ESMV-E02001 SH3 DRCW02-ESEQ-42001 SH1 1272 AAC Conductor 1/ph Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls. Normal summer rating @ 4 ft/s
Note on G251: Author: Reference DRCW02-ESMV-E02001 SH3 DRCW02-ESEQ-42001 SH1 2" SCH40 Al Tube Bus Rate per XEL-EVD-Facility Rating Supplement-Table-Tubular and Square Conductor.xls. Normal summer rating @ 4 ft/s
Note on H251: Author: Reference DRCW02-ESMV-E02001 SH3 DRCW02-ESEQ-42001 SH1 1272 AAC Conductor 1/ph Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls. Normal summer rating @ 4 ft/s
Note on I251: Author: Reactor Switcher 2152 Reference DRCW02-ESMV-E02001 SH3
Note on J251: Author: Reference DRCW02-ESMV-E02001 SH3 DRCW02-ESEQ-42001 SH1 1272 AAC Conductor 1/ph Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls. Normal summer rating @ 4 ft/s
Note on F256: Author: Reference: DRCW01-ESMV-E01001SH5 DRCW01-ESEQ-41001 SH1 2.5" SCH40 Al Tube Bus Rate per XEL-EVD-Facility Rating Supplement-Table-Tubular and Square Conductor.xls. Normal summer rating @ 4 ft/s
Note on G256: Author: Reference DRCW01-ESEQ-E71002 SH3 DRCW01-ESEQ-41001 SH1 1272 AAC Conductor 2/ph Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls. Normal summer rating @ 4 ft/s, double conductor, derated
Note on H256: Author: Reference: DRCW01-ESGA-E01001 SH1 DS1150C
Note on I256: Author: Reference DRCW01-ESEQ-E71002 SH3 3-1250MCM Cables Rate per pg 4 of Rush Creek-1-East Cap Bank Conduit Detail Rev. 1. (for west cap bank). 491A per circuit
Note on F257: Author: DRCW01-ESMV-E01001SH4 DRCW01-ESEQ-41001 SH1 2.5" SCH40 Al Tube Bus Rate per XEL-EVD-Facility Rating Supplement-Table-Tubular and Square Conductor.xls. Normal summer rating @ 4 ft/s
Note on G257: Author: Reference DRCW01-ESEQ-E71002 SH3 DRCW01-ESEQ-41001 SH1 1272 AAC Conductor 2/ph Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls. Normal summer rating @ 4 ft/s, double conductor, derated
Note on H257: Author: Reference: DRCW01-ESGA-E01001 SH1 DS1250C
Note on I257: Author: Reference DRCW01-ESEQ-E71002 SH3 3-1250MCM Cables Rate per RC1 East Side Cap Bank - Pedestrian Trenwa.xlsx 555.4 Amps per circuit
Note on F258: Author: Reference DRCW01-ESEQ-E71002 SH8 DRCW01-ESEQ-41001 SH1 2" SCH40 Al Tube Bus Rate per XEL-EVD-Facility Rating Supplement-Table-Tubular and Square Conductor.xls. Normal summer rating @ 4 ft/s
Note on G258: Author: Reference DRCW01-ESEQ-71002 SH8 DRCW01-ESEQ-41001 SH1 1272 AAC Conductor 1/ph Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls. Normal summer rating @ 4 ft/s
Note on H258: Author: Reference: DRCW01-ESGA-E01001 SH1 DS1150R
Note on I258: Author: Reference: DRCW01-ESEQ-E71002 SH8 2-1250MCM AL cable Rate per "Rush Creek In Line Reactors Scenario.xlsx"
Note on F259: Author: Reference DRCW01-ESEQ-E71002 SH3 DRCW01-ESEQ-41001 SH1 2" SCH40 Al Tube Bus Rate per XEL-EVD-Facility Rating Supplement-Table-Tubular and Square Conductor.xls. Normal summer rating @ 4 ft/s
Note on G259: Author: Reference DRCW01-ESEQ-71002 SH3 DRCW01-ESEQ-41001 SH1 1272 AAC Conductor 1/ph Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls. Normal summer rating @ 4 ft/s
Note on H259: Author: Reference: DRCW01-ESGA-E01001 SH1 DS1250R
Note on I259: Author: Reference: DRCW01-ESEQ-E71002 SH3 1-1250MCM AL cable Rate per "Rush Creek In Line Reactors Scenario.xlsx"
Note on F260: Author: Reference DRCW02-ESEQ-E72002 SH3 DRCW02-ESEQ-42001 SH1 2.5" SCH40 Al Tube Bus Rate per XEL-EVD-Facility Rating Supplement-Table-Tubular and Square Conductor.xls. Normal summer rating @ 4 ft/s
Note on G260: Author: Reference DRCW02-ESEQ-E72002 SH3 DRCW02-ESEQ-42001 SH1 1272 AAC Conductor 2/ph Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls. Normal summer rating @ 4 ft/s, double conductor, derated
Note on H260: Author: Reference: DRCW02-ESGA-E02001 SH1 DS2150C
Note on I260: Author: Reference DRCW02-ESEQ-E72002 SH3 3-1250MCM Cables Rate per RC2 Cap Bank 21 Inches apart.xlsx 381 A per circuit
Note on F261: Author: Reference DRCW02-ESEQ-E72002 SH3 DRCW02-ESEQ-42001 SH1 2" SCH40 Al Tube Bus Rate per XEL-EVD-Facility Rating Supplement-Table-Tubular and Square Conductor.xls. Normal summer rating @ 4 ft/s
Note on G261: Author: Reference DRCW02-ESEQ-72002 SH3 DRCW01-ESEQ-41001 SH1 1272 AAC Conductor 1/ph Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls. Normal summer rating @ 4 ft/s
Note on H261: Author: Reference: DRCW02-ESGA-E02001 SH1 DS2150R
Note on I261: Author: Reference DRCW02-ESEQ-E72002 SH3 2-1250MCM Cables Rate per "Rush Creek 2 In Line Reactors.xlsx" 2*403A per circuit
Note on F266: Author: Reference: DRCW01-ESMV-E01001SH2 DRCW01-ESEQ-41001 SH1 2.5" SCH40 Al Tube Bus Rate per XEL-EVD-Facility Rating Supplement-Table-Tubular and Square Conductor.xls. Normal summer rating @ 4 ft/s
Note on G266: Author: Reference DRCW01-ESMV-E01001 SH2 DRCW01-ESEQ-41001 SH1 1272 AAC Conductor 2/ph Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls. Normal summer rating @ 4 ft/s, double conductor, derated
Note on H266: Author: CT on feeder side of breaker 3000/5 amp MRCT at 3000 amp tap. Reference DRCW01-ESPT-E81001 SH2
Note on I266: Author: Reference: DRCW01-ESMV-E01001 SH2 VCB1150
Note on J266: Author: CT on bus side of feeder breaker 3000/5 amp MRCT at 3000 amp tap. Reference DRCW01-ESPT-E81001 SH2
Note on K266: Author: Reference DRCW01-ESEQ-E71002 SH1 DRCW01-ESEQ-41001 SH1 1272 AAC Conductor 2/ph Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls. Normal summer rating @ 4 ft/s, double conductor, derated
Note on L266: Author: Reference: DRCW01-ESMV-E01001 SH2 DS1150M
Note on M266: Author: Reference DRCW01-ESEQ-E71002 SH1 DRCW01-ESEQ-41001 SH1 1272 AAC Conductor 2/ph Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls. Normal summer rating @ 4 ft/s, double conductor, derated
Note on N266: Author: 50 Element PU: 2000A 51 Element PU: 1471
Note on F267: Author: Reference: DRCW01-ESMV-E01001SH2 DRCW01-ESEQ-41001 SH1 2.5" SCH40 Al Tube Bus Rate per XEL-EVD-Facility Rating Supplement-Table-Tubular and Square Conductor.xls. Normal summer rating @ 4 ft/s
Note on G267: Author: Reference DRCW01-ESMV-E01001 SH2 DRCW01-ESEQ-41001 SH1 1272 AAC Conductor 2/ph Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls. Normal summer rating @ 4 ft/s, double conductor, derated
Note on H267: Author: CT on feeder side of breaker 3000/5 amp MRCT at 3000 amp tap. Reference DRCW01-ESPT-E81001 SH3
Note on I267: Author: Reference: DRCW01-ESMV-E01001 SH2 VCB1150
Note on J267: Author: CT on bus side of feeder breaker 3000/5 amp MRCT at 3000 amp tap. Reference DRCW01-ESPT-E81001 SH3
Note on K267: Author: Reference DRCW01-ESEQ-E71002 SH1 DRCW01-ESEQ-41001 SH1 1272 AAC Conductor 2/ph Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls. Normal summer rating @ 4 ft/s, double conductor, derated
Note on L267: Author: Reference: DRCW01-ESMV-E01001 SH2 DS1250M
Note on M267: Author: Reference DRCW01-ESEQ-E71002 SH1 DRCW01-ESEQ-41001 SH1 1272 AAC Conductor 2/ph Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls. Normal summer rating @ 4 ft/s, double conductor, derated
Note on N267: Author: 50 Element PU: 2000A 51 Element PU: 1471
Note on F268: Author: Reference: DRCW02-ESMV-E02001SH2 DRCW02-ESEQ-42001 SH1 2.5" SCH40 Al Tube Bus Rate per XEL-EVD-Facility Rating Supplement-Table-Tubular and Square Conductor.xls. Normal summer rating @ 4 ft/s
Note on G268: Author: Reference DRCW02-ESMV-E02001 SH2 DRCW02-ESEQ-42001 SH1 1272 AAC Conductor 2/ph Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls. Normal summer rating @ 4 ft/s, double conductor, derated
Note on H268: Author: CT on feeder side of breaker 3000/5 amp MRCT at 3000 amp tap. Reference DRCW02-ESPT-E82001 SH2
Note on I268: Author: Reference: DRCW02-ESMV-E02001 SH2 VCB2150
Note on J268: Author: CT on feeder side of breaker 3000/5 amp MRCT at 3000 amp tap. Reference DRCW02-ESPT-E82001 SH2
Note on K268: Author: Reference DRCW02-ESEQ-E72002 SH1 DRCW02-ESEQ-42001 SH1 1272 AAC Conductor 2/ph Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls. Normal summer rating @ 4 ft/s, double conductor, derated
Note on L268: Author: Reference: DRCW02-ESMV-E02001 SH2 DS2150M
Note on M268: Author: Reference DRCW02-ESEQ-E72002 SH1 DRCW02-ESEQ-42001 SH1 1272 AAC Conductor 2/ph Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls. Normal summer rating @ 4 ft/s, double conductor, derated
Note on N268: Author: 50 Element PU: 2560A 51 Element PU: 1230A
Note on C273: Author: Includes feeders 1101-1104 and MVAR from 1150. Evaluates the largest MVA from capacitive or inductive contributions (turbines and caps/reactors included)
Note on F273: Author: Reference: DRCW01-ESMV-E01001 SH2 DRCW01-ESEQ-41001 SH1 6" SCH80 Al Tube Bus Rate per XEL-EVD-Facility Rating Supplement-Table-Tubular and Square Conductor.xls. Normal summer rating @ 4 ft/s
Note on G273: Author: Reference DRCW01-ESMV-E01001 SH1 DRCW01-ESEQ-41001 SH1 2000 AAC Conductor 4/ph 8" spacing Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls. Normal summer rating @ 4 ft/s, quadruple conductor
Note on H273: Author: Reference: DRCW01-ESMV-E01001 SH2 DRCW01-ESEQ-41001 SH1 6" SCH80 Al Tube Bus Rate per XEL-EVD-Facility Rating Supplement-Table-Tubular and Square Conductor.xls. Normal summer rating @ 4 ft/s
Note on I273: Author: DS1100M Reference: DRCW01-ESMV-E01001
Note on J273: Author: Reference: DRCW01-ESPT-E81001 SH1 GIFD36-13.00.PDF Metering CTs on GSU side of 1100M switch. 1500/5 CT with Rating Factor = 3.0
Note on K273: Author: Reference DRCW01-ESMV-E01001 SH1 DRCW01-ESEQ-41001 SH1 2000 AAC Conductor 4/ph 8" spacing Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls. Normal summer rating @ 4 ft/s, quadruple conductor
Note on L273: Author: Reference: DRCW01-ESPT-E81001 MPT BCT Name Plate 3000/5 CTs with TRF = 2.0
Note on R273: Author: Reference: DRCW01-ESPT-E81001 MPT BCT Name Plate 400/5 CTs with TRF = 2.
Note on T273: Author: Reference: DRCW01-ESHV-E01001 SH1 (2) 954 AAC Magnolia 8" spacing Value from Transmission's XEL-EVD-Facility Rating Supplement Table - Bare Overhead Conductor. @4ft per second and normal summer rating.
Note on V273: Author: Reference: DRCW01-ESHV-E01001 SH1 5" Al Tube, sch40 Value from Transmission's XEL-EVD-Facility Rating Supplement Table - Tubular and square conductor. @4ft per second and normal summer rating
Note on X273: Author: Reference: DRCW01-ESHV-E01001 SH1 (2) 954 AAC Magnolia 8" spacing Value from Transmission's XEL-EVD-Facility Rating Supplement Table - Bare Overhead Conductor. @4ft per second and normal summer rating.
Note on Z273: Brady Nunn: Reference: DRCW01-ESPT-E81001 SH1
Note on AB273: Author: Reference: DRCW01-ESHV-E01001 SH1
Note on AD273: Brady Nunn: Reference: DRCW01-ESPT-E81001 SH1
Note on AF273: Author: Reference: DRCW01-ESHV-E01001 SH1 (2) 954 AAC Magnolia 8" spacing Value from Transmission's XEL-EVD-Facility Rating Supplement Table - Bare Overhead Conductor. @4ft per second and normal summer rating.
Note on AH273: Author: Reference: DRCW01-ESHV-E01001 SH1
Note on AS273: Author: 51 PU set at 706 A Primary (HS)
Note on C274: Author: Includes feeders 1201-1204 and MVAR from 1250. Evaluates the largest MVA from capacitive or inductive contributions (turbines and caps/reactors included)
Note on F274: Author: Reference: DRCW01-ESMV-E01001 SH2 DRCW01-ESEQ-41001 SH1 6" SCH80 Al Tube Bus Rate per XEL-EVD-Facility Rating Supplement-Table-Tubular and Square Conductor.xls. Normal summer rating @ 4 ft/s
Note on G274: Author: Reference DRCW01-ESMV-E01001 SH1 DRCW01-ESEQ-41001 SH1 2000 AAC Conductor 4/ph 8" spacing Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls. Normal summer rating @ 4 ft/s, quadruple conductor
Note on H274: Author: Reference: DRCW01-ESMV-E01001 SH2 DRCW01-ESEQ-41001 SH1 6" SCH80 Al Tube Bus Rate per XEL-EVD-Facility Rating Supplement-Table-Tubular and Square Conductor.xls. Normal summer rating @ 4 ft/s
Note on I274: Author: DS1200M Reference: DRCW01-ESMV-E01001
Note on J274: Author: Reference: DRCW01-ESPT-E81001 SH1 GIFD36-13.00.PDF Metering CTs on GSU side of 1100M switch. 1500/5 CT with Rating Factor = 3.0
Note on K274: Author: Reference DRCW01-ESMV-E01001 SH1 DRCW01-ESEQ-41001 SH1 2000 AAC Conductor 4/ph 8" spacing Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls. Normal summer rating @ 4 ft/s, quadruple conductor
Note on L274: Author: Reference: DRCW01-ESPT-E81001 MPT BCT Name Plate 3000/5 CTs with TRF = 2.0
Note on R274: Author: Reference: DRCW01-ESPT-E81001 MPT BCT Name Plate 400/5 CTs with TRF = 2.
Note on T274: Author: Reference: DRCW01-ESHV-E01001 SH1 (2) 954 AAC Magnolia 8" spacing Value from Transmission's XEL-EVD-Facility Rating Supplement Table - Bare Overhead Conductor. @4ft per second and normal summer rating.
Note on V274: Author: Reference: DRCW01-ESHV-E01001 SH1 5" Al Tube, sch40 Value from Transmission's XEL-EVD-Facility Rating Supplement Table - Tubular and square conductor. @4ft per second and normal summer rating
Note on X274: Author: Reference: DRCW01-ESHV-E01001 SH1 (2) 954 AAC Magnolia 8" spacing Value from Transmission's XEL-EVD-Facility Rating Supplement Table - Bare Overhead Conductor. @4ft per second and normal summer rating.
Note on Z274: Brady Nunn: Reference: DRCW01-ESPT-E81001 SH1
Note on AB274: Author: Reference: DRCW01-ESHV-E01001 SH1
Note on AD274: Brady Nunn: Reference: DRCW01-ESPT-E81001 SH1
Note on AF274: Author: Reference: DRCW01-ESHV-E01001 SH1 (2) 954 AAC Magnolia 8" spacing Value from Transmission's XEL-EVD-Facility Rating Supplement Table - Bare Overhead Conductor. @4ft per second and normal summer rating.
Note on AH274: Author: Reference: DRCW01-ESHV-E01001 SH1
Note on AJ274: Author: Reference: DRCW01-ESHV-E01001 SH1 5" Al Tube, sch40 Value from Transmission's XEL-EVD-Facility Rating Supplement Table - Tubular and square conductor. @4ft per second and normal summer rating
Note on AL274: Author: Reference: DRCW01-ESHV-E01001 SH1 DRCW01-ESEQ-E71002 SH1 (2) 2-1/2" Al tube risers Value from Transmission's XEL-EVD-Facility Rating Supplement Table - Tubular and square conductor. @4ft per second and normal summer rating
Note on AN274: Author: Reference: DRCW01-ESHV-E01001 SH1 DRCW01-ESHV-E01001 SH2 5" Al Tube, sch40 Value from Transmission's XEL-EVD-Facility Rating Supplement Table - Tubular and square conductor. @4ft per second and normal summer rating
Note on AP274: Author: Reference: DRCW01-ESHV-E01001 SH1 DRCW01-ESEQ-E71002 SH1 (2) 2-1/2" Al tube risers Value from Transmission's XEL-EVD-Facility Rating Supplement Table - Tubular and square conductor. @4ft per second and normal summer rating
Note on AS274: Author: 51 PU set at 706 A Primary (HS)
Note on C275: Author: Includes turbine feeders and MVAR from 2150. Evaluates the largest MVA from capacitive or inductive contributions (turbines and caps/reactors included)
Note on F275: Author: Reference: DRCW02-ESMV-E02001 SH2 DRCW02-ESEQ-42001 SH1 6" SCH80 Al Tube Bus Rate per XEL-EVD-Facility Rating Supplement-Table-Tubular and Square Conductor.xls. Normal summer rating @ 4 ft/s
Note on G275: Author: Reference DRCW02-ESMV-E02001 SH1 DRCW02-ESEQ-42001 SH1 2000 AAC Conductor 4/ph 8" spacing Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls. Normal summer rating @ 4 ft/s, quadruple conductor
Note on H275: Author: Reference: DRCW02-ESMV-E02001 SH1 DRCW02-ESEQ-42001 SH1 6" SCH80 Al Tube Bus Rate per XEL-EVD-Facility Rating Supplement-Table-Tubular and Square Conductor.xls. Normal summer rating @ 4 ft/s
Note on I275: Author: DS2100M Reference: DRCW02-ESMV-E02001 SH1
Note on J275: Author: Reference: DRCW02-ESPT-E82001 SH1 GIFD36-13.00.PDF Metering CTs on GSU side of 1100M switch. 1500/5 CT with Rating Factor = 3.0
Note on K275: Author: Reference DRCW02-ESMV-E02001 SH1 DRCW02-ESEQ-42001 SH1 2000 AAC Conductor 4/ph 8" spacing Rate per XEL-EVD-Facility Rating Supplement-Table-Bare Overhead Conductor.xls. Normal summer rating @ 4 ft/s, quadruple conductor
Note on L275: Author: Reference: DRCW02-ESPT-E82001 SH1 MPT BCT Name Plate 3000/5 CTs with TRF = 2.0
Note on R275: Author: Reference: DRCW02-ESPT-E82001 SH1 MPT BCT Name Plate 400/5 CTs with TRF = 2.0
Note on T275: Author: Reference: DRCW02-ESHV-E02001 SH1 (2) 954 AAC Magnolia 8" spacing Value from Transmission's XEL-EVD-Facility Rating Supplement Table - Bare Overhead Conductor. @4ft per second and normal summer rating.
Note on V275: Author: Reference: DRCW02-ESHV-E02001 SH1 5" Al Tube, sch40 Value from Transmission's XEL-EVD-Facility Rating Supplement Table - Tubular and square conductor. @4ft per second and normal summer rating
Note on X275: Author: Reference: DRCW02-ESHV-E02001 SH1 (2) 954 AAC Magnolia 8" spacing Value from Transmission's XEL-EVD-Facility Rating Supplement Table - Bare Overhead Conductor. @4ft per second and normal summer rating.
Note on Z275: Brady Nunn: Reference: DRCW02-ESPT-E82001 SH1
Note on AB275: Author: Reference: DRCW02-ESHV-E02001 SH1
Note on AD275: Brady Nunn: Reference: DRCW02-ESPT-E82001 SH1
Note on AF275: Author: Reference: DRCW02-ESHV-E02001 SH1 (2) 954 AAC Magnolia 8" spacing Value from Transmission's XEL-EVD-Facility Rating Supplement Table - Bare Overhead Conductor. @4ft per second and normal summer rating.
Note on AH275: Author: Reference: DRCW02-ESHV-E02001 SH1
Note on AS275: Author: 51 PU set at 706 A Primary (HS)
Note on C280: Author: Load from all connected sources on bus 1 (larger than bus 2 and maximum the tie will see)
Note on F280: Author: 3000/5 CTs on either side of 1001M disconnect switch TRF=2.0 Reference: DRCW01-ESMV-E01001 SH2 DRCW01-ESEQ-E41001 SH1
Note on G280: Author: Reference: DRCW01-ESMV-E01001 SH2 DRCW01-ESEQ-41001 SH1 6" SCH80 Al Tube Bus Rate per XEL-EVD-Facility Rating Supplement-Table-Tubular and Square Conductor.xls. Normal summer rating @ 4 ft/s
Note on H280: Author: 1001M disconnect switch Reference: DRCW01-ESMV-E01001 SH2 DRCW01-ESEQ-E41001 SH1
Note on F284: Author: Does not include the combined MVA rating from the normal configuration as that is replaced with the increase from the bus tie
Note on G284: Author: Does not include the combined MVA rating from the normal configuration as that is replaced with the increase from the bus tie
Note on C286: Author: Maximum amount of MVA that can be connected, limited by the kirk key system Includes the 5 largest turbine feeders included in the kirk key system (1102,1103,1104,1201,1204) and 1203 along with the cap/reactor bank feeders from both buses. Evaluates the largest MVA from capacitive or inductive contributions (turbines and caps/reactors included)
Note on C287: Author: Maximum amount of MVA that can be connected, limited by the kirk key system Includes the 5 largest turbine feeders included in the kirk key system (1102,1103,1104,1201,1204) and 1203 along with the cap/reactor bank feeders from both buses. Evaluates the largest MVA from capacitive or inductive contributions (turbines and caps/reactors included)
Note on B293: Author: Rating of all wind turbines and reactive sources. Evaluates the largest MVA from capacitive or inductive contributions (turbines and caps/reactors included)
Note on E293: Author: Reference: DRCW01-ESHV-E01001 SH1 5" Al Tube, sch40 Value from Transmission's XEL-EVD-Facility Rating Supplement Table - Tubular and square conductor. @4ft per second and normal summer rating
Note on H293: Author: Reference: DRCW01-ESHV-E01001 SH1 (2) 954 AAC Magnolia 8" spacing Value from Transmission's XEL-EVD-Facility Rating Supplement Table - Bare Overhead Conductor. @4ft per second and normal summer rating.
Note on I293: Author: Reference: DRCW01-ESHV-E01001 SH1
Note on J293: Author: Reference: DRCW01-ESHV-E01001 SH1 (2) 954 AAC Magnolia 8" spacing Value from Transmission's XEL-EVD-Facility Rating Supplement Table - Bare Overhead Conductor. @4ft per second and normal summer rating.
Note on L293: Author: T-line transferred to Transmission documentation
Note on N293: Author: Combined rating of both transformers
Note on B294: Author: Rating of all wind turbines and reactive sources. Evaluates the largest MVA from capacitive or inductive contributions (turbines and caps/reactors included)
Note on E294: Author: Reference: DRCW02-ESHV-E02001 SH1 5" Al Tube, sch40 Value from Transmission's XEL-EVD-Facility Rating Supplement Table - Tubular and square conductor. @4ft per second and normal summer rating
Note on F294: Author: Reference: DRCW02-ESHV-E02001 SH1 (2) 954 AAC Magnolia 8" spacing Value from Transmission's XEL-EVD-Facility Rating Supplement Table - Bare Overhead Conductor. @4ft per second and normal summer rating. Wave Trap removed with the addition of Shortgrass.
Note on G294: Author: Reference DRCW02-ESGA-E02001 SH1 Wave Trap removed with addition of Shortgrass switching station. Pulled from ratings in Rev6
Note on H294: Author: Reference: DRCW02-ESHV-E02001 SH1 (2) 954 AAC Magnolia 8" spacing Value from Transmission's XEL-EVD-Facility Rating Supplement Table - Bare Overhead Conductor. @4ft per second and normal summer rating.
Note on I294: Author: Reference: DRCW02-ESHV-E02001 SH1
Note on J294: Author: Reference: DRCW02-ESHV-E02001 SH1 (2) 954 AAC Magnolia 8" spacing Value from Transmission's XEL-EVD-Facility Rating Supplement Table - Bare Overhead Conductor. @4ft per second and normal summer rating.
Note on L294: Author:
Note on A302: Author: Reference: Cheyenne Ridge TSA Ex. D.1.1.a General Specification (V110).pdf
Note on D302: Author: Reference: Cheyenne Ridge TSA Ex. D.1.1.c General Specification (V120).pdf
Note on B310: Author: 34.5 KV UG Feeders
Note on C310: Author: Reference: Cheyenne East and West Collection System One-line.pdf
Note on D310: Author: Reference: Cheyenne East and West Collection System One-line.pdf
Note on K312: Author: Reference: 1250 MCM MV Cable ampacity from ACYR00-ESMV-MVC-R0 Bore Cymcap Results
Note on L312: Author: 1272 MCM Narcissus Summer (normal) @ 2 ft/sec XEL-EVD-Facility-Rating-Supplement---Table---Bare-Overhead-Conductor.xls ACYR00-SIMD-E01005.pdf DCYR01-ESMV-E0E001 SH. 1
Note on M312: Author: Reference: DCYR01-ESMV-E0E001 SH. 1 ACYR00-SIMD-E01005.pdf
Note on N312: Author: 1272 MCM Narcissus Summer (normal) @ 2 ft/sec XEL-EVD-Facility-Rating-Supplement---Table---Bare-Overhead-Conductor.xls ACYR00-SIMD-E01005.pdf DCYR01-ESMV-E0E001 SH. 1
Note on K313: Author: Reference: 1250 MCM MV Cable ampacity from ACYR00-ESMV-MVC-R0 Bore Cymcap Results
Note on L313: Author: 1272 MCM Narcissus Summer (normal) @ 2 ft/sec XEL-EVD-Facility-Rating-Supplement---Table---Bare-Overhead-Conductor.xls ACYR00-SIMD-E01005.pdf DCYR01-ESMV-E0E001 SH. 1
Note on M313: Author: Reference: DCYR01-ESMV-E0E001 SH. 1 ACYR00-SIMD-E01005.pdf
Note on N313: Author: 1272 MCM Narcissus Summer (normal) @ 2 ft/sec XEL-EVD-Facility-Rating-Supplement---Table---Bare-Overhead-Conductor.xls ACYR00-SIMD-E01005.pdf DCYR01-ESMV-E0E001 SH. 1
Note on K314: Author: Reference: 1250 MCM MV Cable ampacity from ACYR00-ESMV-MVC-R0 Bore Cymcap Results
Note on L314: Author: 1272 MCM Narcissus Summer (normal) @ 2 ft/sec XEL-EVD-Facility-Rating-Supplement---Table---Bare-Overhead-Conductor.xls ACYR00-SIMD-E01005.pdf DCYR01-ESMV-E0E001 SH. 1
Note on M314: Author: Reference: DCYR01-ESMV-E0E001 SH. 1 ACYR00-SIMD-E01005.pdf
Note on N314: Author: 1272 MCM Narcissus Summer (normal) @ 2 ft/sec XEL-EVD-Facility-Rating-Supplement---Table---Bare-Overhead-Conductor.xls ACYR00-SIMD-E01005.pdf DCYR01-ESMV-E0E001 SH. 1
Note on K315: Author: Reference: 1250 MCM MV Cable ampacity from ACYR00-ESMV-MVC-R0 Bore Cymcap Results
Note on L315: Author: 1272 MCM Narcissus Summer (normal) @ 2 ft/sec XEL-EVD-Facility-Rating-Supplement---Table---Bare-Overhead-Conductor.xls ACYR00-SIMD-E01005.pdf DCYR01-ESMV-E0E001 SH. 1
Note on M315: Author: Reference: DCYR01-ESMV-E0E001 SH. 1 ACYR00-SIMD-E01005.pdf
Note on N315: Author: 1272 MCM Narcissus Summer (normal) @ 2 ft/sec XEL-EVD-Facility-Rating-Supplement---Table---Bare-Overhead-Conductor.xls ACYR00-SIMD-E01005.pdf DCYR01-ESMV-E0E001 SH. 1
Note on K316: Author: Reference: 750 MCM MV Cable ampacity from ACYR00-ESMV-MVC-R0 Bore Cymcap Results
Note on L316: Author: 1272 MCM Narcissus Summer (normal) @ 2 ft/sec XEL-EVD-Facility-Rating-Supplement---Table---Bare-Overhead-Conductor.xls ACYR00-SIMD-E01005.pdf DCYR01-ESMV-E0E001 SH. 1
Note on M316: Author: Reference: DCYR01-ESMV-E0E001 SH. 1 ACYR00-SIMD-E01005.pdf
Note on N316: Author: 1272 MCM Narcissus Summer (normal) @ 2 ft/sec XEL-EVD-Facility-Rating-Supplement---Table---Bare-Overhead-Conductor.xls ACYR00-SIMD-E01005.pdf DCYR01-ESMV-E0E001 SH. 1
Note on K317: Author: Reference: 1250 MCM MV Cable ampacity from ACYR00-ESMV-MVC-R0 Bore Cymcap Results
Note on L317: Author: 1272 MCM Narcissus Summer (normal) @ 2 ft/sec XEL-EVD-Facility-Rating-Supplement---Table---Bare-Overhead-Conductor.xls ACYR00-SIMD-E01005.pdf DCYR01-ESMV-E0E001 SH. 1
Note on M317: Author: Reference: DCYR01-ESMV-E0E001 SH. 1 ACYR00-SIMD-E01005.pdf
Note on N317: Author: 1272 MCM Narcissus Summer (normal) @ 2 ft/sec XEL-EVD-Facility-Rating-Supplement---Table---Bare-Overhead-Conductor.xls ACYR00-SIMD-E01005.pdf DCYR01-ESMV-E0E001 SH. 1
Note on K318: Author: Reference: 1250 MCM MV Cable ampacity from ACYR00-ESMV-MVC-R0 Bore Cymcap Results
Note on L318: Author: 1272 MCM Narcissus Summer (normal) @ 2 ft/sec XEL-EVD-Facility-Rating-Supplement---Table---Bare-Overhead-Conductor.xls ACYR00-SIMD-E01005.pdf DCYR01-ESMV-E0E001 SH. 1
Note on M318: Author: Reference: DCYR01-ESMV-E0E001 SH. 1 ACYR00-SIMD-E01005.pdf
Note on N318: Author: 1272 MCM Narcissus Summer (normal) @ 2 ft/sec XEL-EVD-Facility-Rating-Supplement---Table---Bare-Overhead-Conductor.xls ACYR00-SIMD-E01005.pdf DCYR01-ESMV-E0E001 SH. 1
Note on K319: Author: Reference: 1250 MCM MV Cable ampacity from ACYR00-ESMV-MVC-R0 Bore Cymcap Results
Note on L319: Author: 1272 MCM Narcissus Summer (normal) @ 2 ft/sec XEL-EVD-Facility-Rating-Supplement---Table---Bare-Overhead-Conductor.xls ACYR00-SIMD-E01005.pdf DCYR01-ESMV-E0E001 SH. 1
Note on M319: Author: Reference: DCYR01-ESMV-E0E001 SH. 1 ACYR00-SIMD-E01005.pdf
Note on N319: Author: 1272 MCM Narcissus Summer (normal) @ 2 ft/sec XEL-EVD-Facility-Rating-Supplement---Table---Bare-Overhead-Conductor.xls ACYR00-SIMD-E01005.pdf DCYR01-ESMV-E0E001 SH. 1
Note on K320: Author: Reference: 1250 MCM MV Cable ampacity from ACYR00-ESMV-MVC-R0 Bore Cymcap Results
Note on L320: Author: 1272 MCM Narcissus Summer (normal) @ 2 ft/sec XEL-EVD-Facility-Rating-Supplement---Table---Bare-Overhead-Conductor.xls ACYR00-SIMD-E01005.pdf DCYR01-ESMV-E0E001 SH. 1
Note on M320: Author: Reference: DCYR01-ESMV-E0E001 SH. 1 ACYR00-SIMD-E01005.pdf
Note on N320: Author: 1272 MCM Narcissus Summer (normal) @ 2 ft/sec XEL-EVD-Facility-Rating-Supplement---Table---Bare-Overhead-Conductor.xls ACYR00-SIMD-E01005.pdf DCYR01-ESMV-E0E001 SH. 1
Note on K321: Author: Reference: 1250 MCM MV Cable ampacity from ACYR00-ESMV-MVC-R0 Bore Cymcap Results
Note on L321: Author: 1272 MCM Narcissus Summer (normal) @ 2 ft/sec XEL-EVD-Facility-Rating-Supplement---Table---Bare-Overhead-Conductor.xls ACYR00-SIMD-E01005.pdf DCYR01-ESMV-E0E001 SH. 1
Note on M321: Author: Reference: DCYR01-ESMV-E0E001 SH. 1 ACYR00-SIMD-E01005.pdf
Note on N321: Author: 1272 MCM Narcissus Summer (normal) @ 2 ft/sec XEL-EVD-Facility-Rating-Supplement---Table---Bare-Overhead-Conductor.xls ACYR00-SIMD-E01005.pdf DCYR01-ESMV-E0E001 SH. 1
Note on K322: Author: Reference: 1250 MCM MV Cable ampacity from ACYR00-ESMV-MVC-R0 Bore Cymcap Results
Note on L322: Author: 1272 MCM Narcissus Summer (normal) @ 2 ft/sec XEL-EVD-Facility-Rating-Supplement---Table---Bare-Overhead-Conductor.xls ACYR00-SIMD-E01005.pdf DCYR01-ESMV-E0E001 SH. 1
Note on M322: Author: Reference: DCYR01-ESMV-E0E001 SH. 1 ACYR00-SIMD-E01005.pdf
Note on N322: Author: 1272 MCM Narcissus Summer (normal) @ 2 ft/sec XEL-EVD-Facility-Rating-Supplement---Table---Bare-Overhead-Conductor.xls ACYR00-SIMD-E01005.pdf DCYR01-ESMV-E0E001 SH. 1
Note on K323: Author: Reference: 1250 MCM MV Cable ampacity from ACYR00-ESMV-MVC-R0 Direct Buried Cymcap Results
Note on L323: Author: 1272 MCM Narcissus Summer (normal) @ 2 ft/sec XEL-EVD-Facility-Rating-Supplement---Table---Bare-Overhead-Conductor.xls DCYR01-ESMV-E0W001 SH. 1 ACYR00-SIMD-E01005.pdf
Note on M323: Author: Reference: DCYR01-ESMV-E0W001 SH. 1 ACYR00-SIMD-E01005.pdf
Note on N323: Author: 1272 MCM Narcissus Summer (normal) @ 2 ft/sec XEL-EVD-Facility-Rating-Supplement---Table---Bare-Overhead-Conductor.xls DCYR01-ESMV-E0W001 SH. 1 ACYR00-SIMD-E01005.pdf
Note on K324: Author: Reference: 1250 MCM MV Cable ampacity from ACYR00-ESMV-MVC-R0 Direct Buried Cymcap Results
Note on L324: Author: 1272 MCM Narcissus Summer (normal) @ 2 ft/sec XEL-EVD-Facility-Rating-Supplement---Table---Bare-Overhead-Conductor.xls DCYR01-ESMV-E0W001 SH. 1 ACYR00-SIMD-E01005.pdf
Note on M324: Author: Reference: DCYR01-ESMV-E0W001 SH. 1 ACYR00-SIMD-E01005.pdf
Note on N324: Author: 1272 MCM Narcissus Summer (normal) @ 2 ft/sec XEL-EVD-Facility-Rating-Supplement---Table---Bare-Overhead-Conductor.xls DCYR01-ESMV-E0W001 SH. 1 ACYR00-SIMD-E01005.pdf
Note on K325: Author: Reference: 1250 MCM MV Cable ampacity from ACYR00-ESMV-MVC-R0 Direct Buried Cymcap Results
Note on L325: Author: 1272 MCM Narcissus Summer (normal) @ 2 ft/sec XEL-EVD-Facility-Rating-Supplement---Table---Bare-Overhead-Conductor.xls DCYR01-ESMV-E0W001 SH. 1 ACYR00-SIMD-E01005.pdf
Note on M325: Author: Reference: DCYR01-ESMV-E0W001 SH. 1 ACYR00-SIMD-E01005.pdf
Note on N325: Author: 1272 MCM Narcissus Summer (normal) @ 2 ft/sec XEL-EVD-Facility-Rating-Supplement---Table---Bare-Overhead-Conductor.xls DCYR01-ESMV-E0W001 SH. 1 ACYR00-SIMD-E01005.pdf
Note on K326: Author: Reference: 1250 MCM MV Cable ampacity from ACYR00-ESMV-MVC-R0 Direct Buried Cymcap Results
Note on L326: Author: 1272 MCM Narcissus Summer (normal) @ 2 ft/sec XEL-EVD-Facility-Rating-Supplement---Table---Bare-Overhead-Conductor.xls DCYR01-ESMV-E0W001 SH. 1 ACYR00-SIMD-E01005.pdf
Note on M326: Author: Reference: DCYR01-ESMV-E0W001 SH. 1 ACYR00-SIMD-E01005.pdf
Note on N326: Author: 1272 MCM Narcissus Summer (normal) @ 2 ft/sec XEL-EVD-Facility-Rating-Supplement---Table---Bare-Overhead-Conductor.xls DCYR01-ESMV-E0W001 SH. 1 ACYR00-SIMD-E01005.pdf
Note on K327: Author: Reference: 1250 MCM MV Cable ampacity from ACYR00-ESMV-MVC-R0
Note on L327: Author: 1272 MCM Narcissus Summer (normal) @ 2 ft/sec XEL-EVD-Facility-Rating-Supplement---Table---Bare-Overhead-Conductor.xls DCYR01-ESMV-E0W001 SH. 1 ACYR00-SIMD-E01005.pdf
Note on M327: Author: Reference: DCYR01-ESMV-E0W001 SH. 1 ACYR00-SIMD-E01005.pdf
Note on N327: Author: 1272 MCM Narcissus Summer (normal) @ 2 ft/sec XEL-EVD-Facility-Rating-Supplement---Table---Bare-Overhead-Conductor.xls DCYR01-ESMV-E0W001 SH. 1 ACYR00-SIMD-E01005.pdf
Note on K328: Author: Reference: 1250 MCM MV Cable ampacity from ACYR00-ESMV-MVC-R0 Direct Buried Cymcap Results
Note on L328: Author: 1272 MCM Narcissus Summer (normal) @ 2 ft/sec XEL-EVD-Facility-Rating-Supplement---Table---Bare-Overhead-Conductor.xls DCYR01-ESMV-E0W001 SH. 1 ACYR00-SIMD-E01005.pdf
Note on M328: Author: Reference: DCYR01-ESMV-E0W001 SH. 1 ACYR00-SIMD-E01005.pdf
Note on N328: Author: 1272 MCM Narcissus Summer (normal) @ 2 ft/sec XEL-EVD-Facility-Rating-Supplement---Table---Bare-Overhead-Conductor.xls DCYR01-ESMV-E0W001 SH. 1 ACYR00-SIMD-E01005.pdf
Note on K329: Author: Reference: 1250 MCM MV Cable ampacity from ACYR00-ESMV-MVC-R0 Direct Buried Cymcap Results
Note on L329: Author: 1272 MCM Narcissus Summer (normal) @ 2 ft/sec XEL-EVD-Facility-Rating-Supplement---Table---Bare-Overhead-Conductor.xls DCYR01-ESMV-E0W001 SH. 1 ACYR00-SIMD-E01005.pdf
Note on M329: Author: Reference: DCYR01-ESMV-E0W001 SH. 1 ACYR00-SIMD-E01005.pdf
Note on N329: Author: 1272 MCM Narcissus Summer (normal) @ 2 ft/sec XEL-EVD-Facility-Rating-Supplement---Table---Bare-Overhead-Conductor.xls DCYR01-ESMV-E0W001 SH. 1 ACYR00-SIMD-E01005.pdf
Note on K330: Author: Reference: 1250 MCM MV Cable ampacity from ACYR00-ESMV-MVC-R0 Bore Cymcap Results
Note on L330: Author: 1272 MCM Narcissus Summer (normal) @ 2 ft/sec XEL-EVD-Facility-Rating-Supplement---Table---Bare-Overhead-Conductor.xls DCYR01-ESMV-E0W001 SH. 1 ACYR00-SIMD-E01005.pdf
Note on M330: Author: Reference: DCYR01-ESMV-E0W001 SH. 1 ACYR00-SIMD-E01005.pdf
Note on N330: Author: 1272 MCM Narcissus Summer (normal) @ 2 ft/sec XEL-EVD-Facility-Rating-Supplement---Table---Bare-Overhead-Conductor.xls DCYR01-ESMV-E0W001 SH. 1 ACYR00-SIMD-E01005.pdf
Note on K331: Author: Reference: 1250 MCM MV Cable ampacity from ACYR00-ESMV-MVC-R0 Bore Cymcap Results
Note on L331: Author: 1272 MCM Narcissus Summer (normall) @ 2 ft/sec XEL-EVD-Facility-Rating-Supplement---Table---Bare-Overhead-Conductor.xls DCYR01-ESMV-E0W001 SH. 1 ACYR00-SIMD-E01005.pdf
Note on M331: Author: Reference: DCYR01-ESMV-E0W001 SH. 1 ACYR00-SIMD-E01005.pdf
Note on N331: Author: 1272 MCM Narcissus Summer (normal) @ 2 ft/sec XEL-EVD-Facility-Rating-Supplement---Table---Bare-Overhead-Conductor.xls DCYR01-ESMV-E0W001 SH. 1 ACYR00-SIMD-E01005.pdf
Note on K332: Author: Reference: 1250 MCM MV Cable ampacity from ACYR00-ESMV-MVC-R0 Bore Cymcap Results Bore Cymcap Results
Note on L332: Author: 1272 MCM Narcissus Summer (normal) @ 2 ft/sec XEL-EVD-Facility-Rating-Supplement---Table---Bare-Overhead-Conductor.xls DCYR01-ESMV-E0W001 SH. 1 ACYR00-SIMD-E01005.pdf
Note on M332: Author: Reference: DCYR01-ESMV-E0W001 SH. 1 ACYR00-SIMD-E01005.pdf
Note on N332: Author: 1272 MCM Narcissus Summer (normal) @ 2 ft/sec XEL-EVD-Facility-Rating-Supplement---Table---Bare-Overhead-Conductor.xls DCYR01-ESMV-E0W001 SH. 1 ACYR00-SIMD-E01005.pdf
Note on K333: Author: Reference: 1250 MCM MV Cable ampacity from ACYR00-ESMV-MVC-R0 Bore Cymcap Results
Note on L333: Author: 1272 MCM Narcissus Summer (normal) @ 2 ft/sec XEL-EVD-Facility-Rating-Supplement---Table---Bare-Overhead-Conductor.xls DCYR01-ESMV-E0W001 SH. 1 ACYR00-SIMD-E01005.pdf
Note on M333: Author: Reference: DCYR01-ESMV-E0W001 SH. 1 ACYR00-SIMD-E01005.pdf
Note on N333: Author: 1272 MCM Narcissus Summer (normal) @ 2 ft/sec XEL-EVD-Facility-Rating-Supplement---Table---Bare-Overhead-Conductor.xls DCYR01-ESMV-E0W001 SH. 1 ACYR00-SIMD-E01005.pdf
Note on K334: Author: Reference: 1250 MCM MV Cable ampacity from ACYR00-ESMV-MVC-R0 Bore Cymcap Results
Note on L334: Author: 1272 MCM Narcissus Summer (normal) @ 2 ft/sec XEL-EVD-Facility-Rating-Supplement---Table---Bare-Overhead-Conductor.xls DCYR01-ESMV-E0W001 SH. 1 ACYR00-SIMD-E01005.pdf
Note on M334: Author: Reference: DCYR01-ESMV-E0W001 SH. 1 ACYR00-SIMD-E01005.pdf
Note on N334: Author: 1272 MCM Narcissus Summer (normal) @ 2 ft/sec XEL-EVD-Facility-Rating-Supplement---Table---Bare-Overhead-Conductor.xls DCYR01-ESMV-E0W001 SH. 1 ACYR00-SIMD-E01005.pdf
Note on K335: Author: Reference: 1250 MCM MV Cable ampacity from ACYR00-ESMV-MVC-R0 Bore Cymcap Results
Note on L335: Author: 1272 MCM Narcissus Summer (normal) @ 2 ft/sec XEL-EVD-Facility-Rating-Supplement---Table---Bare-Overhead-Conductor.xls DCYR01-ESMV-E0W001 SH. 1 ACYR00-SIMD-E01005.pdf
Note on M335: Author: Reference: DCYR01-ESMV-E0W001 SH. 1 ACYR00-SIMD-E01005.pdf
Note on N335: Author: 1272 MCM Narcissus Summer (normal) @ 2 ft/sec XEL-EVD-Facility-Rating-Supplement---Table---Bare-Overhead-Conductor.xls DCYR01-ESMV-E0W001 SH. 1 ACYR00-SIMD-E01005.pdf
Note on K336: Author: Reference: 1250 MCM MV Cable ampacity from ACYR00-ESMV-MVC-R0 Bore Cymcap Results
Note on L336: Author: 1272 MCM Narcissus Summer (normal) @ 2 ft/sec XEL-EVD-Facility-Rating-Supplement---Table---Bare-Overhead-Conductor.xls DCYR01-ESMV-E0W001 SH. 1 ACYR00-SIMD-E01005.pdf
Note on M336: Author: Reference: DCYR01-ESMV-E0W001 SH. 1 ACYR00-SIMD-E01005.pdf
Note on N336: Author: 1272 MCM Narcissus Summer (normal) @ 2 ft/sec XEL-EVD-Facility-Rating-Supplement---Table---Bare-Overhead-Conductor.xls DCYR01-ESMV-E0W001 SH. 1 ACYR00-SIMD-E01005.pdf
Note on F342: Author: Reference: 2" AL. Tube Summer (Normal) 2ft/sec. ACYR00-SIMD-E01005.pdf XEL-EVD-Facility-Rating-Supplement---Table---Tubular-and-Square-Conductor.xls
Note on G342: Author: 1272 MCM Narcissus Summer (normal) @ 2 ft/sec XEL-EVD-Facility-Rating-Supplement---Table---Bare-Overhead-Conductor.xls ACYR00-SIMD-E01005.pdf
Note on K342: Author: 1272 MCM Narcissus Summer (normal) @ 2 ft/sec XEL-EVD-Facility-Rating-Supplement---Table---Bare-Overhead-Conductor.xls ACYR00-SIMD-E01005.pdf
Note on M342: Author: 1272 MCM Narcissus Summer (normal) @ 2 ft/sec XEL-EVD-Facility-Rating-Supplement---Table---Bare-Overhead-Conductor.xls ACYR00-SIMD-E01005.pdf
Note on C344: Author: Combined MVA of Feeders: 2101A and 2101B
Note on F344: Author: Reference: DCYR01-ESMV-E0E001 Sh. 1
Note on G344: Author: Reference: DCYR01-ESMV-E0E001 Sh. 1
Note on H344: Author: Reference: DCYR01-ESPT-E8E001 SH. 2 3007854009-100 .pdf 2000:5A MR (2000:5A TAP) TRF: 2
Note on I344: Author: Reference: 3007854009-100 .pdf DCYR01-ESMV-E0E001 Sh. 1
Note on J344: Author: Reference: DCYR01-ESPT-E8E001 SH. 2 3007854009-100 .pdf 2000:5A MR (2000:5A TAP) TRF: 2
Note on K344: Author: Reference: DCYR01-ESMV-E0E001 Sh. 1
Note on L344: Author: Reference: DCYR01-ESMV-E0E001 Sh. 1
Note on M344: Author: Reference: DCYR01-ESMV-E0E001 Sh. 1
Note on N344: Author: Reference Cheyenne Ridge PRC-025-2 Limiting Relay Element: 50P1P = 508 A - Directional, doesn't apply 50P2P = 1128 A 50P3P = 3640 A
Note on C345: Author: Combined MVA of Feeders: 2102A and 2102B
Note on F345: Author: Reference: DCYR01-ESMV-E0E001 Sh. 1
Note on G345: Author: Reference: DCYR01-ESMV-E0E001 Sh. 1
Note on H345: Author: Reference: DCYR01-ESPT-E8E001 SH.2 3007854009-100 .pdf 2000:5A MR (2000:5A TAP) TRF: 2
Note on I345: Author: Reference: 3007854009-100 .pdf DCYR01-ESMV-E0E001 Sh. 1
Note on J345: Author: Reference: DCYR01-ESPT-E8E001 SH.2 3007854009-100 .pdf 2000:5A MR (2000:5A TAP) TRF: 2
Note on K345: Author: Reference: DCYR01-ESMV-E0E001 Sh. 1
Note on L345: Author: Reference: DCYR01-ESMV-E0E001 Sh. 1
Note on M345: Author: Reference: DCYR01-ESMV-E0E001 Sh. 1
Note on N345: Author: Reference Cheyenne Ridge PRC-025-2 Limiting Relay Element: 50P1P = 508 A Directional, doesn't apply 50P2P = 1128 A 50P3P = 3640 A
Note on C346: Author: Combined MVA of Feeders: 2103A and 2103B
Note on F346: Author: Reference: DCYR01-ESMV-E0E001 Sh. 1
Note on G346: Author: Reference: DCYR01-ESMV-E0E001 Sh. 1
Note on H346: Author: Reference: DCYR01-ESPT-E8E001 SH. 2 3007854009-100 .pdf 2000:5A MR (2000:5A TAP) TRF: 2
Note on I346: Author: Reference: 3007854009-100 .pdf DCYR01-ESMV-E0E001 Sh. 1
Note on J346: Author: Reference: DCYR01-ESPT-E8E001 SH. 2 3007854009-100 .pdf 2000:5A MR (2000:5A TAP) TRF: 2
Note on K346: Author: Reference: DCYR01-ESMV-E0E001 Sh. 1
Note on L346: Author: Reference: DCYR01-ESMV-E0E001 Sh. 1
Note on M346: Author: Reference: DCYR01-ESMV-E0E001 Sh. 1
Note on N346: Author: Reference Cheyenne Ridge PRC-025-2 Limiting Relay Element: 50P1P = 508 A Directional, doesn't apply 50P2P = 1128 A 50P3P = 3640 A
Note on C347: Author: Combined MVA of Feeders: 2201A and 2201B
Note on F347: Author: Reference: DCYR01-ESMV-E0E001 Sh. 1
Note on G347: Author: Reference: DCYR01-ESMV-E0E001 Sh. 1
Note on H347: Author: Reference: DCYR01-ESPT-E8E001 SH. 3 3007854009-100 .pdf 2000:5A MR (2000:5A TAP) TRF: 2
Note on I347: Author: Reference: 3007854009-100 .pdf DCYR01-ESMV-E0E001 Sh. 1
Note on J347: Author: Reference: DCYR01-ESPT-E8E001 SH. 3 3007854009-100 .pdf 2000:5A MR (2000:5A TAP) TRF: 2
Note on K347: Author: Reference: DCYR01-ESMV-E0E001 Sh. 1
Note on L347: Author: Reference: DCYR01-ESMV-E0E001 Sh. 1
Note on M347: Author: Reference: DCYR01-ESMV-E0E001 Sh. 1
Note on N347: Author: Reference Cheyenne Ridge PRC-025-2 Limiting Relay Element: 50P1P = 508 A Directional, doesn't apply 50P2P = 1128 A 50P3P = 3640 A
Note on C348: Author: Combined MVA of Feeder: 2202
Note on F348: Author: Reference: DCYR01-ESMV-E0E001 Sh. 1
Note on G348: Author: Reference: DCYR01-ESMV-E0E001 Sh. 1
Note on H348: Author: Reference: DCYR01-ESPT-E8E001 SH. 3 3007854009-100 .pdf 2000:5A MR (2000:5A TAP) TRF: 2
Note on I348: Author: Reference: 3007854009-100 .pdf DCYR01-ESMV-E0E001 Sh. 1
Note on J348: Author: Reference: DCYR01-ESPT-E8E001 SH. 3 3007854009-100 .pdf 2000:5A MR (2000:5A TAP) TRF: 2
Note on K348: Author: Reference: DCYR01-ESMV-E0E001 Sh. 1
Note on L348: Author: Reference: DCYR01-ESMV-E0E001 Sh. 1
Note on M348: Author: Reference: DCYR01-ESMV-E0E001 Sh. 1
Note on N348: Author: Reference Cheyenne Ridge PRC-025-2 Limiting Relay Element: 50P1P = 508 A Directional, doesn't apply 50P2P = 1128 A 50P3P = 3640 A
Note on C349: Author: Combined MVA of Feeders: 2203A and 2203B
Note on F349: Author: Reference: DCYR01-ESMV-E0E001 Sh. 1
Note on G349: Author: Reference: DCYR01-ESMV-E0E001 Sh. 1
Note on H349: Author: Reference: DCYR01-ESPT-E8E001 SH. 3 3007854009-100 .pdf 2000:5A MR (2000:5A TAP) TRF: 2
Note on I349: Author: Reference: 3007854009-100 .pdf DCYR01-ESMV-E0E001 Sh. 1
Note on J349: Author: Reference: DCYR01-ESPT-E8E001 SH. 3 3007854009-100 .pdf 2000:5A MR (2000:5A TAP) TRF: 2
Note on K349: Author: Reference: DCYR01-ESMV-E0E001 Sh. 1
Note on L349: Author: Reference: DCYR01-ESMV-E0E001 Sh. 1
Note on M349: Author: Reference: DCYR01-ESMV-E0E001 Sh. 1
Note on N349: Author: Reference Cheyenne Ridge PRC-025-2 Limiting Relay Element: 50P1P = 508 A Directional, doesn't apply 50P2P = 1128 A 50P3P = 3640 A
Note on C350: Author: Combined MVA of Feeders: 1101A, 1101B and 1101C
Note on F350: Author: Reference: DCYR01-ESMV-E0W001 Sh. 1
Note on G350: Author: Reference: DCYR01-ESMV-E0W001 Sh. 1
Note on H350: Author: Reference: DCYR01-ESPT-E8W001 SH.2 3007854009-100 .pdf 2000:5A MR (2000:5A TAP) TRF: 2
Note on I350: Author: Reference: 3007854009-100 .pdf DCYR01-ESMV-E0W001 Sh. 1
Note on J350: Author: Reference: DCYR01-ESPT-E8W001 SH.2 3007854009-100 .pdf 2000:5A MR (2000:5A TAP) TRF: 2
Note on K350: Author: Reference: DCYR01-ESMV-E0W001 Sh. 1
Note on L350: Author: Reference: DCYR01-ESMV-E0W001 Sh. 1
Note on M350: Author: Reference: DCYR01-ESMV-E0W001 Sh. 1
Note on N350: Author: Reference Cheyenne Ridge PRC-025-2 Limiting Relay Element: 50P1P = 652 A Directional, doesn't apply 50P2P = 1284 A 50P3P = 4072 A
Note on C351: Author: Combined MVA of Feeders: 1102A and 1102B
Note on F351: Author: Reference: DCYR01-ESMV-E0W001 Sh. 1
Note on G351: Author: Reference: DCYR01-ESMV-E0W001 Sh. 1
Note on H351: Author: Reference: DCYR01-ESPT-E8W001 SH.2 3007854009-100 .pdf 2000:5A MR (2000:5A TAP) TRF: 2
Note on I351: Author: Reference: 3007854009-100 .pdf DCYR01-ESMV-E0W001 Sh. 1
Note on J351: Author: Reference: DCYR01-ESPT-E8W001 SH.2 3007854009-100 .pdf 2000:5A MR (2000:5A TAP) TRF: 2
Note on K351: Author: Reference: DCYR01-ESMV-E0W001 Sh. 1
Note on L351: Author: Reference: DCYR01-ESMV-E0W001 Sh. 1
Note on M351: Author: Reference: DCYR01-ESMV-E0W001 Sh. 1
Note on N351: Author: Reference Cheyenne Ridge PRC-025-2 Limiting Relay Element: 50P1P = 652 A Directional, doesn't apply 50P2P = 1284 A 50P3P = 4072 A
Note on C352: Author: Combined MVA of Feeders: 1103A, 1103B and 1103C
Note on F352: Author: Reference: DCYR01-ESMV-E0W001 Sh. 1
Note on G352: Author: Reference: DCYR01-ESMV-E0W001 Sh. 1
Note on H352: Author: Reference: DCYR01-ESPT-E8W001 SH.2 3007854009-100 .pdf 2000:5A MR (2000:5A TAP) TRF: 2
Note on I352: Author: Reference: 3007854009-100 .pdf DCYR01-ESMV-E0W001 Sh. 1
Note on J352: Author: Reference: DCYR01-ESPT-E8W001 SH.2 3007854009-100 .pdf 2000:5A MR (2000:5A TAP) TRF: 2
Note on K352: Author: Reference: DCYR01-ESMV-E0W001 Sh. 1
Note on L352: Author: Reference: DCYR01-ESMV-E0W001 Sh. 1
Note on M352: Author: Reference: DCYR01-ESMV-E0W001 Sh. 1
Note on N352: Author: Reference Cheyenne Ridge PRC-025-2 Limiting Relay Element: 50P1P = 652 A Directional, doesn't apply 50P2P = 1284 A 50P3P = 4072 A
Note on C353: Author: Combined MVA of Feeders: 1201A and 1201B
Note on F353: Author: Reference: DCYR01-ESMV-E0W001 Sh. 1
Note on G353: Author: Reference: DCYR01-ESMV-E0W001 Sh. 1
Note on H353: Author: Reference: DCYR01-ESPT-E8W001 SH.3 3007854009-100 .pdf 2000:5A MR (2000:5A TAP) TRF: 2
Note on I353: Author: Reference: 3007854009-100 .pdf DCYR01-ESMV-E0W001 Sh. 1
Note on J353: Author: Reference: DCYR01-ESPT-E8W001 SH.3 3007854009-100 .pdf 2000:5A MR (2000:5A TAP) TRF: 2
Note on K353: Author: Reference: DCYR01-ESMV-E0W001 Sh. 1
Note on L353: Author: Reference: DCYR01-ESMV-E0W001 Sh. 1
Note on M353: Author: Reference: DCYR01-ESMV-E0W001 Sh. 1
Note on N353: Author: Reference Cheyenne Ridge PRC-025-2 Limiting Relay Element: 50P1P = 652 A Directional, doesn't apply 50P2P = 1284 A 50P3P = 4072 A
Note on C354: Author: Combined MVA of Feeders: 1202A and 1202B
Note on F354: Author: Reference: DCYR01-ESMV-E0W001 Sh. 1
Note on G354: Author: Reference: DCYR01-ESMV-E0W001 Sh. 1
Note on H354: Author: Reference: DCYR01-ESPT-E8W001 SH.3 3007854009-100 .pdf 2000:5A MR (2000:5A TAP) TRF: 2
Note on I354: Author: Reference: 3007854009-100 .pdf DCYR01-ESMV-E0W001 Sh. 1
Note on J354: Author: Reference: DCYR01-ESPT-E8W001 SH.3 3007854009-100 .pdf 2000:5A MR (2000:5A TAP) TRF: 2
Note on K354: Author: Reference: DCYR01-ESMV-E0W001 Sh. 1
Note on L354: Author: Reference: DCYR01-ESMV-E0W001 Sh. 1
Note on M354: Author: Reference: DCYR01-ESMV-E0W001 Sh. 1
Note on N354: Author: Reference Cheyenne Ridge PRC-025-2 Limiting Relay Element: 50P1P = 652 A Directional, doesn't apply 50P2P = 1284 A 50P3P = 4072 A
Note on C355: Author: Combined MVA of Feeders: 1203A and 1203B
Note on F355: Author: Reference: DCYR01-ESMV-E0W001 Sh. 1
Note on G355: Author: Reference: DCYR01-ESMV-E0W001 Sh. 1
Note on H355: Author: Reference: DCYR01-ESPT-E8W001 SH.3 3007854009-100 .pdf 2000:5A MR (2000:5A TAP) TRF: 2
Note on I355: Author: Reference: 3007854009-100 .pdf DCYR01-ESMV-E0W001 Sh. 1
Note on J355: Author: Reference: DCYR01-ESPT-E8W001 SH.3 3007854009-100 .pdf 2000:5A MR (2000:5A TAP) TRF: 2
Note on K355: Author: Reference: DCYR01-ESMV-E0W001 Sh. 1
Note on L355: Author: Reference: DCYR01-ESMV-E0W001 Sh. 1
Note on M355: Author: Reference: DCYR01-ESMV-E0W001 Sh. 1
Note on N355: Author: Reference Cheyenne Ridge PRC-025-2 Limiting Relay Element: 50P1P = 652 A Directional, doesn't apply 50P2P = 1284 A 50P3P = 4072 A
Note on H359: Author: 1272 MCM Narcissus Summer (normal) @ 2 ft/sec XEL-EVD-Facility-Rating-Supplement---Table---Bare-Overhead-Conductor.xls ACYR00-SIMD-E01005.pdf
Note on C361: Author: Combined MVA of Capacitor Bank: 2152
Note on F361: Author: DCYR01-ESMV-E0E001 SH. 3 Ratings not provided by Cap Bank Manufacuture, rating assumed to be same as generator.
Note on G361: Author: Reference: DCYR01-ESMV-E0E001 SH. 3 Cheyenne-Ridge-Cap-Switcher-Approval-Drawings.pdf
Note on H361: Author: Reference: DCYR01-ESMV-E0E001 SH. 3
Note on I361: Author: Reference: DCYR01-ESMV-E0E001 SH. 3
Note on J361: Author: Reference: 5" AL TUBULAR BUS DCYR01-ESMV-E0E001 XEL-EVD-Facility-Rating-Supplement---Table---Tubular-and-Square-Conductor.xls
Note on K361: Author: (2) 2.5" Al. Bus = 2 * 1628 = 3256 Amps DCYR01-ESMV-E0E001 XEL-EVD-Facility-Rating-Supplement---Table---Tubular-and-Square-Conductor.xls
Note on C362: Author: Combined MVA of Capacitor Bank: 2153
Note on F362: Author: DCYR01-ESMV-E0E001 SH. 3 Ratings not provided by Cap Bank Manufacuture, rating assumed to be same as generator.
Note on G362: Author: Reference: DCYR01-ESMV-E0E001 SH. 3 Cheyenne-Ridge-Cap-Switcher-Approval-Drawings.pdf
Note on H362: Author: Reference: DCYR01-ESMV-E0E001 SH. 3
Note on I362: Author: Reference: DCYR01-ESMV-E0E001 SH. 3
Note on J362: Author: Reference: 5" AL TUBULAR BUS DCYR01-ESMV-E0E001 XEL-EVD-Facility-Rating-Supplement---Table---Tubular-and-Square-Conductor.xls
Note on K362: Author: (2) 2.5" Al. Bus = 2 * 1628 = 3256 Amps DCYR01-ESMV-E0E001 XEL-EVD-Facility-Rating-Supplement---Table---Tubular-and-Square-Conductor.xls
Note on C363: Author: Combined MVA of Capacitor Bank: 2252
Note on F363: Author: DCYR01-ESMV-E0E001 SH. 3 Ratings not provided by Cap Bank Manufacuture, rating assumed to be same as generator.
Note on G363: Author: Reference: DCYR01-ESMV-E0E001 SH. 3 Cheyenne-Ridge-Cap-Switcher-Approval-Drawings.pdf
Note on H363: Author: Reference: DCYR01-ESMV-E0E001 SH. 3
Note on I363: Author: Reference: DCYR01-ESMV-E0E001 SH. 3
Note on J363: Author: Reference: 5" AL TUBULAR BUS DCYR01-ESMV-E0E001 XEL-EVD-Facility-Rating-Supplement---Table---Tubular-and-Square-Conductor.xls
Note on K363: Author: (2) 2.5" Al. Bus = 2 * 1628 = 3256 Amps DCYR01-ESMV-E0E001 XEL-EVD-Facility-Rating-Supplement---Table---Tubular-and-Square-Conductor.xls
Note on C364: Author: Combined MVA of Capacitor Bank: 2253
Note on F364: Author: DCYR01-ESMV-E0E001 SH. 3 Ratings not provided by Cap Bank Manufacuture, rating assumed to be same as generator.
Note on G364: Author: Reference: DCYR01-ESMV-E0E001 SH. 3 Cheyenne-Ridge-Cap-Switcher-Approval-Drawings.pdf
Note on H364: Author: Reference: DCYR01-ESMV-E0E001 SH. 3
Note on I364: Author: Reference: DCYR01-ESMV-E0E001 SH. 3
Note on J364: Author: Reference: 5" AL TUBULAR BUS DCYR01-ESMV-E0E001 XEL-EVD-Facility-Rating-Supplement---Table---Tubular-and-Square-Conductor.xls
Note on K364: Author: (2) 2.5" Al. Bus = 2 * 1628 = 3256 Amps DCYR01-ESMV-E0E001 XEL-EVD-Facility-Rating-Supplement---Table---Tubular-and-Square-Conductor.xls
Note on C365: Author: Combined MVA of Capacitor Bank: 1152
Note on F365: Author: DCYR01-ESMV-E0W001 SH. 3 Ratings not provided by Cap Bank Manufacuture, rating assumed to be same as generator.
Note on G365: Author: Reference: DCYR01-ESMV-E0W001 SH. 3 Cheyenne-Ridge-Cap-Switcher-Approval-Drawings.pdf
Note on H365: Author: Reference: DCYR01-ESMV-E0W001 SH. 3
Note on I365: Author: Reference: DCYR01-ESMV-E0W001 SH. 3
Note on J365: Author: Reference: 5" AL TUBULAR BUS DCYR01-ESMV-E0W001 XEL-EVD-Facility-Rating-Supplement---Table---Tubular-and-Square-Conductor.xls
Note on K365: Author: (2) 2.5" Al. Bus = 2 * 1628 = 3256 Amps DCYR01-ESMV-E0W001 XEL-EVD-Facility-Rating-Supplement---Table---Tubular-and-Square-Conductor.xls
Note on C366: Author: Combined MVA of Capacitor Bank: 1153
Note on F366: Author: DCYR01-ESMV-E0W001 SH. 3 Ratings not provided by Cap Bank Manufacuture, rating assumed to be same as generator.
Note on G366: Author: Reference: DCYR01-ESMV-E0W001 SH. 3 Cheyenne-Ridge-Cap-Switcher-Approval-Drawings.pdf
Note on H366: Author: Reference: DCYR01-ESMV-E0W001 SH. 3
Note on I366: Author: Reference: DCYR01-ESMV-E0W001 SH. 3
Note on J366: Author: Reference: 5" AL TUBULAR BUS DCYR01-ESMV-E0W001 XEL-EVD-Facility-Rating-Supplement---Table---Tubular-and-Square-Conductor.xls
Note on K366: Author: (2) 2.5" Al. Bus = 2 * 1628 = 3256 Amps DCYR01-ESMV-E0W001 XEL-EVD-Facility-Rating-Supplement---Table---Tubular-and-Square-Conductor.xls
Note on C367: Author: Combined MVA of Capacitor Bank: 1252
Note on F367: Author: DCYR01-ESMV-E0W001 SH. 3 Ratings not provided by Cap Bank Manufacuture, rating assumed to be same as generator.
Note on G367: Author: Reference: DCYR01-ESMV-E0W001 SH. 3 Cheyenne-Ridge-Cap-Switcher-Approval-Drawings.pdf
Note on H367: Author: Reference: DCYR01-ESMV-E0W001 SH. 3
Note on I367: Author: Reference: DCYR01-ESMV-E0W001 SH. 3
Note on J367: Author: Reference: 5" AL TUBULAR BUS DCYR01-ESMV-E0W001 XEL-EVD-Facility-Rating-Supplement---Table---Tubular-and-Square-Conductor.xls
Note on K367: Author: (2) 2.5" Al. Bus = 2 * 1628 = 3256 Amps DCYR01-ESMV-E0W001 XEL-EVD-Facility-Rating-Supplement---Table---Tubular-and-Square-Conductor.xls
Note on C368: Author: Combined MVA of Capacitor Bank: 1253
Note on F368: Author: DCYR01-ESMV-E0W001 SH. 3 Ratings not provided by Cap Bank Manufacuture, rating assumed to be same as generator.
Note on G368: Author: Reference: DCYR01-ESMV-E0W001 SH. 3 Cheyenne-Ridge-Cap-Switcher-Approval-Drawings.pdf
Note on H368: Author: Reference: DCYR01-ESMV-E0W001 SH. 3
Note on I368: Author: Reference: DCYR01-ESMV-E0W001 SH. 3
Note on J368: Author: Reference: 5" AL TUBULAR BUS DCYR01-ESMV-E0W001 XEL-EVD-Facility-Rating-Supplement---Table---Tubular-and-Square-Conductor.xls
Note on K368: Author: (2) 2.5" Al. Bus = 2 * 1628 = 3256 Amps DCYR01-ESMV-E0W001 XEL-EVD-Facility-Rating-Supplement---Table---Tubular-and-Square-Conductor.xls
Note on F372: Author: 1272 MCM Narcissus Summer (normarl) @ 2 ft/sec XEL-EVD-Facility-Rating-Supplement---Table---Bare-Overhead-Conductor.xls ACYR00-SIMD-E01005.pdf
Note on H372: Author: 1272 MCM Narcissus Summer (normarl) @ 2 ft/sec XEL-EVD-Facility-Rating-Supplement---Table---Bare-Overhead-Conductor.xls ACYR00-SIMD-E01005.pdf
Note on J372: Author: 1272 MCM Narcissus Summer (normarl) @ 2 ft/sec XEL-EVD-Facility-Rating-Supplement---Table---Bare-Overhead-Conductor.xls ACYR00-SIMD-E01005.pdf
Note on C374: Author: Combined MVA of Reactor Bank: 2151
Note on F374: Author: Reference: DCYR01-ESMV-E0E001 SH. 3
Note on G374: Author: Reference: 2" AL TUBULAR BUS DCYR01-ESMV-E0E001 XEL-EVD-Facility-Rating-Supplement---Table---Tubular-and-Square-Conductor.xls
Note on H374: Author: Reference: DCYR01-ESMV-E0E001 SH. 3
Note on I374: Author: Reference: DCYR01-ESMV-E0E001 SH. 3 83210007.pdf
Note on J374: Author: Reference: DCYR01-ESMV-E0E001 SH. 3
Note on K374: Author: Reference: DCYR01-ESMV-E0E001 SH. 3
Note on L374: Author: Reference: 5" AL TUBULAR BUS DCYR01-ESMV-E0E001 XEL-EVD-Facility-Rating-Supplement---Table---Tubular-and-Square-Conductor.xls
Note on M374: Author: (2) 2.5" Al. Bus = 2 * 1628 = 3256 Amps DCYR01-ESMV-E0E001 XEL-EVD-Facility-Rating-Supplement---Table---Tubular-and-Square-Conductor.xls
Note on C375: Author: Combined MVA of Reactor Bank: 2251
Note on F375: Author: Reference: DCYR01-ESMV-E0E001 SH. 3
Note on G375: Author: Reference: 2" AL TUBULAR BUS DCYR01-ESMV-E0E001 XEL-EVD-Facility-Rating-Supplement---Table---Tubular-and-Square-Conductor.xls
Note on H375: Author: Reference: DCYR01-ESMV-E0E001 SH. 3
Note on I375: Author: Reference: DCYR01-ESMV-E0E001 SH. 3 83210007.pdf
Note on J375: Author: Reference: DCYR01-ESMV-E0E001 SH. 3
Note on K375: Author: Reference: DCYR01-ESMV-E0E001 SH. 3
Note on L375: Author: Reference: 5" AL TUBULAR BUS DCYR01-ESMV-E0E001 XEL-EVD-Facility-Rating-Supplement---Table---Tubular-and-Square-Conductor.xls
Note on M375: Author: (2) 2.5" Al. Bus = 2 * 1628 = 3256 Amps DCYR01-ESMV-E0E001 XEL-EVD-Facility-Rating-Supplement---Table---Tubular-and-Square-Conductor.xls
Note on C376: Author: Combined MVA of Reactor Bank: 1151
Note on F376: Author: Reference: DCYR01-ESMV-E0W001 SH. 3
Note on G376: Author: Reference: 2" AL TUBULAR BUS DCYR01-ESMV-E0W001 XEL-EVD-Facility-Rating-Supplement---Table---Tubular-and-Square-Conductor.xls
Note on H376: Author: Reference: DCYR01-ESMV-E0W001 SH. 3
Note on I376: Author: Reference: DCYR01-ESMV-E0W001 SH. 3 83210007.pdf
Note on J376: Author: Reference: DCYR01-ESMV-E0W001 SH. 3
Note on K376: Author: Reference: DCYR01-ESMV-E0W001 SH. 3
Note on L376: Author: Reference: 5" AL TUBULAR BUS DCYR01-ESMV-E0W001 XEL-EVD-Facility-Rating-Supplement---Table---Tubular-and-Square-Conductor.xls
Note on M376: Author: (2) 2.5" Al. Bus = 2 * 1628 = 3256 Amps DCYR01-ESMV-E0W001 XEL-EVD-Facility-Rating-Supplement---Table---Tubular-and-Square-Conductor.xls
Note on C377: Author: Combined MVA of Reactor Bank: 1251
Note on F377: Author: Reference: DCYR01-ESMV-E0W001 SH. 3
Note on G377: Author: Reference: 2" AL TUBULAR BUS DCYR01-ESMV-E0W001 XEL-EVD-Facility-Rating-Supplement---Table---Tubular-and-Square-Conductor.xls
Note on H377: Author: Reference: DCYR01-ESMV-E0W001 SH. 3
Note on I377: Author: Reference: DCYR01-ESMV-E0W001 SH. 3 83210007.pdf
Note on J377: Author: Reference: DCYR01-ESMV-E0W001 SH. 3
Note on K377: Author: Reference: DCYR01-ESMV-E0W001 SH. 3
Note on L377: Author: Reference: 5" AL TUBULAR BUS DCYR01-ESMV-E0W001 XEL-EVD-Facility-Rating-Supplement---Table---Tubular-and-Square-Conductor.xls
Note on M377: Author: (2) 2.5" Al. Bus = 2 * 1628 = 3256 Amps DCYR01-ESMV-E0W001 XEL-EVD-Facility-Rating-Supplement---Table---Tubular-and-Square-Conductor.xls
Note on G381: Author: 1272 MCM Narcissus Summer (normarl) @ 2 ft/sec XEL-EVD-Facility-Rating-Supplement---Table---Bare-Overhead-Conductor.xls ACYR00-SIMD-E01005.pdf
Note on C383: Author: Combined MVA of Capacitor Banks: 2152 and 2153
Note on F383: Author: Reference: 5" AL TUBULAR BUS DCYR01-ESMV-E0E001 XEL-EVD-Facility-Rating-Supplement---Table---Tubular-and-Square-Conductor.xls
Note on G383: Author: Reference: DCYR01-ESMV-E0E001 SH. 2
Note on C384: Author: MVA of Reactor Bank: 2151
Note on F384: Author: Reference: 5" AL TUBULAR BUS DCYR01-ESMV-E0E001 XEL-EVD-Facility-Rating-Supplement---Table---Tubular-and-Square-Conductor.xls
Note on G384: Author: Reference: DCYR01-ESMV-E0E001 SH. 2
Note on C385: Author: Combined MVA of Capacitor Banks: 2252 and 2253
Note on F385: Author: Reference: 5" AL TUBULAR BUS DCYR01-ESMV-E0E001 XEL-EVD-Facility-Rating-Supplement---Table---Tubular-and-Square-Conductor.xls
Note on G385: Author: Reference: DCYR01-ESMV-E0E001 SH. 2
Note on C386: Author: MVA of Reactor Bank: 2251
Note on F386: Author: Reference: 5" AL TUBULAR BUS DCYR01-ESMV-E0E001 XEL-EVD-Facility-Rating-Supplement---Table---Tubular-and-Square-Conductor.xls
Note on G386: Author: Reference: DCYR01-ESMV-E0E001 SH. 2
Note on C387: Author: Combined MVA of Capacitor Banks: 1152 and 1153
Note on F387: Author: Reference: 5" AL TUBULAR BUS DCYR01-ESMV-E0W001 XEL-EVD-Facility-Rating-Supplement---Table---Tubular-and-Square-Conductor.xls
Note on G387: Author: Reference: DCYR01-ESMV-E0W001 SH. 2
Note on C388: Author: MVA of Reactor Bank: 1151
Note on F388: Author: Reference: 5" AL TUBULAR BUS DCYR01-ESMV-E0W001 XEL-EVD-Facility-Rating-Supplement---Table---Tubular-and-Square-Conductor.xls
Note on G388: Author: Reference: DCYR01-ESMV-E0W001 SH. 2
Note on C389: Author: Combined MVA of Capacitor Banks: 1252 and 1253
Note on F389: Author: Reference: 5" AL TUBULAR BUS DCYR01-ESMV-E0W001 XEL-EVD-Facility-Rating-Supplement---Table---Tubular-and-Square-Conductor.xls
Note on G389: Author: Reference: DCYR01-ESMV-E0W001 SH. 2
Note on C390: Author: MVA of Reactor Bank: 1251
Note on F390: Author: Reference: 5" AL TUBULAR BUS DCYR01-ESMV-E0W001 XEL-EVD-Facility-Rating-Supplement---Table---Tubular-and-Square-Conductor.xls
Note on G390: Author: Reference: DCYR01-ESMV-E0W001 SH. 2
Note on G394: Author: 1272 MCM Narcissus Summer (normarl) @ 2 ft/sec XEL-EVD-Facility-Rating-Supplement---Table---Bare-Overhead-Conductor.xls ACYR00-SIMD-E01005.pdf
Note on K394: Author: 1272 MCM Narcissus Summer (normarl) @ 2 ft/sec XEL-EVD-Facility-Rating-Supplement---Table---Bare-Overhead-Conductor.xls ACYR00-SIMD-E01005.pdf
Note on M394: Author: 1272 MCM Narcissus Summer (normarl) @ 2 ft/sec XEL-EVD-Facility-Rating-Supplement---Table---Bare-Overhead-Conductor.xls ACYR00-SIMD-E01005.pdf
Note on C396: Author: Combined MVA of Capacitor Banks: 2152 and 2153
Note on F396: Author: Reference: 5" AL TUBULAR BUS DCYR01-ESMV-E0E001 SH. 2 XEL-EVD-Facility-Rating-Supplement---Table---Tubular-and-Square-Conductor.xls
Note on G396: Author: Reference: DCYR01-ESMV-E0E001 SH. 2
Note on H396: Author: Reference: DCYR01-ESPT-E8E001 SH. 2 3007854009-100 .pdf 2000:5A MR (2000:5A TAP) TRF: 2
Note on I396: Author: Reference: 3007854009-100 .pdf DCYR01-ESMV-E0E001 Sh. 2
Note on J396: Author: Reference: DCYR01-ESPT-E8E001 SH. 2 3007854009-100 .pdf 2000:5A MR (2000:5A TAP) TRF: 2
Note on K396: Author: Reference: DCYR01-ESMV-E0E001 SH. 2
Note on L396: Author: Reference: DCYR01-ESMV-E0E001 SH. 2
Note on M396: Author: Reference: DCYR01-ESMV-E0E001 SH. 2
Note on N396: Author: Reference Cheyenne Ridge PRC-025-2 Limiting Relay Element: 50WP1P = 1324 A 50WP2P = 636 A
Note on C397: Author: Combined MVA of Capacitor Banks: 2252 and 2253
Note on F397: Author: Reference: 5" AL TUBULAR BUS DCYR01-ESMV-E0E001 SH. 2 XEL-EVD-Facility-Rating-Supplement---Table---Tubular-and-Square-Conductor.xls
Note on G397: Author: Reference: DCYR01-ESMV-E0E001 SH. 2
Note on H397: Author: Reference: DCYR01-ESPT-E8E001 SH. 3 3007854009-100 .pdf 2000:5A MR (2000:5A TAP) TRF: 2
Note on I397: Author: Reference: 3007854009-100 .pdf DCYR01-ESMV-E0E001 Sh. 2
Note on J397: Author: Reference: DCYR01-ESPT-E8E001 SH. 3 3007854009-100 .pdf 2000:5A MR (2000:5A TAP) TRF: 2
Note on K397: Author: Reference: DCYR01-ESMV-E0E001 SH. 2
Note on L397: Author: Reference: DCYR01-ESMV-E0E001 SH. 2
Note on M397: Author: Reference: DCYR01-ESMV-E0E001 SH. 2
Note on N397: Author: Reference Cheyenne Ridge PRC-025-2 Limiting Relay Element: 50WP1P = 1324 A 50WP2P = 636 A
Note on C398: Author: Combined MVA of Capacitor Banks: 1152 and 1153
Note on F398: Author: Reference: 5" AL TUBULAR BUS DCYR01-ESMV-E0W001 SH. 2 XEL-EVD-Facility-Rating-Supplement---Table---Tubular-and-Square-Conductor.xls
Note on G398: Author: Reference: DCYR01-ESMV-E0W001 SH. 2
Note on H398: Author: Reference: DCYR01-ESPT-E8W001 SH.2 3007854009-100 .pdf 2000:5A MR (2000:5A TAP) TRF: 2
Note on I398: Author: Reference: 3007854009-100 .pdf DCYR01-ESMV-E0W001 Sh. 2
Note on J398: Author: Reference: DCYR01-ESPT-E8W001 SH.2 3007854009-100 .pdf 2000:5A MR (2000:5A TAP) TRF: 2
Note on K398: Author: Reference: DCYR01-ESMV-E0W001 SH. 2
Note on L398: Author: Reference: DCYR01-ESMV-E0W001 SH. 2
Note on M398: Author: Reference: DCYR01-ESMV-E0W001 SH. 2
Note on N398: Author: Reference Cheyenne Ridge PRC-025-2 Limiting Relay Element: 50WP1P = 1656 A 50WP2P = 796 A
Note on C399: Author: Combined MVA of Capacitor Banks: 1252 and 1253
Note on F399: Author: Reference: 5" AL TUBULAR BUS DCYR01-ESMV-E0W001 SH. 2 XEL-EVD-Facility-Rating-Supplement---Table---Tubular-and-Square-Conductor.xls
Note on G399: Author: Reference: DCYR01-ESMV-E0W001 SH. 2
Note on H399: Author: Reference: DCYR01-ESPT-E8W001 SH.3 3007854009-100 .pdf 2000:5A MR (2000:5A TAP) TRF: 2
Note on I399: Author: Reference: 3007854009-100 .pdf DCYR01-ESMV-E0W001 Sh. 2
Note on J399: Author: Reference: DCYR01-ESPT-E8W001 SH.3 3007854009-100 .pdf 2000:5A MR (2000:5A TAP) TRF: 2
Note on K399: Author: Reference: DCYR01-ESMV-E0W001 SH. 2
Note on L399: Author: Reference: DCYR01-ESMV-E0W001 SH. 2
Note on M399: Author: Reference: DCYR01-ESMV-E0W001 SH. 2
Note on N399: Author: Reference Cheyenne Ridge PRC-025-2 Limiting Relay Element: 50WP1P = 1656 A 50WP2P = 796 A
Note on C405: Author: Total Combined MVA of Turbines and Capacitor Banks Connected to Bus 1. Bus-Tie breaker is in the open position.
Note on F405: Author: Reference: 5" AL TUBULAR BUS DCYR01-ESMV-E0E001 SH. 1 XEL-EVD-Facility-Rating-Supplement---Table---Tubular-and-Square-Conductor.xls
Note on G405: Author: 3-1272 MCM Narcissus Summer (normarl) @ 2 ft/sec, 6" or Greater Spacing. XEL-EVD-Facility-Rating-Supplement---Table---Bare-Overhead-Conductor.xls DCYR01-ESEQ-E7E002
Note on H405: Author: Reference: 5" AL TUBULAR BUS DCYR01-ESMV-E0E001 SH. 1 XEL-EVD-Facility-Rating-Supplement---Table---Tubular-and-Square-Conductor.xls
Note on I405: Author: DCYR01-ESPT-E8E001 SH. 2 GIFD36-13.00.pdf 1500:5A SR TRF: 3
Note on J405: Author: Reference: 5" AL TUBULAR BUS DCYR01-ESMV-E0E001 SH. 1 XEL-EVD-Facility-Rating-Supplement---Table---Tubular-and-Square-Conductor.xls
Note on K405: Author: Reference: DCYR01-ESMV-E0E001 SH. 1
Note on L405: Author: 3-1272 MCM Narcissus Summer (normarl) @ 2 ft/sec, 6" or Greater Spacing. XEL-EVD-Facility-Rating-Supplement---Table---Bare-Overhead-Conductor.xls DCYR01-ESEQ-E7E002
Note on M405: Author: Reference: DCYR01-ESPT-E8E001 SH. 1 3007854009-100 .pdf 2000:5A MR (2000:5A TAP) TRF: 2
Note on N405: Author: Reference: DCYR01-ESMV-E0E001 SH. 1
Note on O405: Author: Reference: DCYR01-ESPT-E8E001 SH. 1 3007854009-100 .pdf 2000:5A MR (2000:5A TAP) TRF: 2
Note on P405: Author: 3-1272 MCM Narcissus Summer (normarl) @ 2 ft/sec, 6" or Greater Spacing. XEL-EVD-Facility-Rating-Supplement---Table---Bare-Overhead-Conductor.xls DCYR01-ESEQ-E7E002
Note on Q405: Author: Reference: DCYR01-ESMV-E0E001 SH. 1
Note on R405: Author: 3-1272 MCM Narcissus Summer (normarl) @ 2 ft/sec, 6" or Greater Spacing. XEL-EVD-Facility-Rating-Supplement---Table---Bare-Overhead-Conductor.xls DCYR01-ESEQ-E7E002
Note on S405: Author: Reference: DCYR01-ESPT-E8E001 SH. 1 D-18618_NAMEPLATE_1528.01-04_Rev 0.pdf 2620:5A SR TRF: 2
Note on T405: Author: Reference: DCYR01-ESPT-E8E001 SH. 1 D-18618_NAMEPLATE_1528.01-04_Rev 0.pdf 300:5A SR TRF: 2
Note on U405: Author: 2-954 MCM Magnolia Summer (normarl) @ 2 ft/sec, 6" or Greater Spacing. XEL-EVD-Facility-Rating-Supplement---Table---Bare-Overhead-Conductor.xls DCYR01-ESHV-E0E001 SH. 1
Note on V405: Author: Reference: 5" AL TUBULAR BUS DCYR01-ESMV-E0E001 SH. 1 XEL-EVD-Facility-Rating-Supplement---Table---Tubular-and-Square-Conductor.xls
Note on W405: Author: 2-954 MCM Magnolia Summer (normarl) @ 2 ft/sec, 6" or Greater Spacing. XEL-EVD-Facility-Rating-Supplement---Table---Bare-Overhead-Conductor.xls DCYR01-ESHV-E0E001 SH. 1
Note on X405: Author: Reference: DCYR01-ESPT-E8E001 SH. 1 280622-010_rev_00 .pdf 2000:5A MR (2000:5A TAP) TRF: 2
Note on Y405: Author: 280622-010_rev_00 .pdf DCYR01-ESHV-E0E001 SH.1
Note on Z405: Author: Reference: DCYR01-ESPT-E8E001 SH. 1 280622-010_rev_00 .pdf 2000:5A MR (2000:5A TAP) TRF: 2
Note on AA405: Author: 2-954 MCM Magnolia Summer (normarl) @ 2 ft/sec, 6" or Greater Spacing. XEL-EVD-Facility-Rating-Supplement---Table---Bare-Overhead-Conductor.xls DCYR01-ESHV-E0E001 SH. 1
Note on AB405: Author: DCYR01-ESHV-E0E001 SH. 1
Note on AC405: Author: Reference: 5" AL TUBULAR BUS DCYR01-ESMV-E0E001 SH. 1 XEL-EVD-Facility-Rating-Supplement---Table---Tubular-and-Square-Conductor.xls
Note on AD405: Author: (2) 2.5" Al. Bus = 2 * 1628 = 3256 Amps XEL-EVD-Facility-Rating-Supplement---Table---Tubular-and-Square-Conductor.xls
Note on C406: Author: Total Combined MVA of Turbines and Capacitor Banks Connected to Bus 2. Bus-Tie breaker is in the open position.
Note on F406: Author: Reference: 5" AL TUBULAR BUS DCYR01-ESMV-E0E001 SH. 1 XEL-EVD-Facility-Rating-Supplement---Table---Tubular-and-Square-Conductor.xls
Note on G406: Author: 3-1272 MCM Narcissus Summer (normarl) @ 2 ft/sec, 6" or Greater Spacing. XEL-EVD-Facility-Rating-Supplement---Table---Bare-Overhead-Conductor.xls DCYR01-ESEQ-E7E002
Note on H406: Author: Reference: 5" AL TUBULAR BUS DCYR01-ESMV-E0E001 SH. 1 XEL-EVD-Facility-Rating-Supplement---Table---Tubular-and-Square-Conductor.xls
Note on I406: Author: DCYR01-ESPT-E8E001 SH. 3 GIFD36-13.00.pdf 1500:5A SR TRF: 3
Note on J406: Author: Reference: 5" AL TUBULAR BUS DCYR01-ESMV-E0E001 SH. 1 XEL-EVD-Facility-Rating-Supplement---Table---Tubular-and-Square-Conductor.xls
Note on K406: Author: Reference: DCYR01-ESMV-E0E001 SH. 1
Note on L406: Author: 3-1272 MCM Narcissus Summer (normarl) @ 2 ft/sec, 6" or Greater Spacing. XEL-EVD-Facility-Rating-Supplement---Table---Bare-Overhead-Conductor.xls DCYR01-ESEQ-E7E002
Note on M406: Author: Reference: DCYR01-ESPT-E8E001 SH. 1 3007854009-100 .pdf 2000:5A MR (2000:5A TAP) TRF: 2
Note on N406: Author: Reference: DCYR01-ESMV-E0E001 SH. 1
Note on O406: Author: Reference: DCYR01-ESPT-E8E001 SH. 1 3007854009-100 .pdf 2000:5A MR (2000:5A TAP) TRF: 2
Note on P406: Author: 3-1272 MCM Narcissus Summer (normarl) @ 2 ft/sec, 6" or Greater Spacing. XEL-EVD-Facility-Rating-Supplement---Table---Bare-Overhead-Conductor.xls DCYR01-ESEQ-E7E002
Note on Q406: Author: Reference: DCYR01-ESMV-E0E001 SH. 1
Note on R406: Author: 3-1272 MCM Narcissus Summer (normarl) @ 2 ft/sec, 6" or Greater Spacing. XEL-EVD-Facility-Rating-Supplement---Table---Bare-Overhead-Conductor.xls DCYR01-ESEQ-E7E002
Note on S406: Author: Reference: DCYR01-ESPT-E8E001 SH. 1 D-18618_NAMEPLATE_1528.01-04_Rev 0.pdf 2620:5A SR TRF: 2
Note on T406: Author: Reference: DCYR01-ESPT-E8E001 SH. 1 D-18618_NAMEPLATE_1528.01-04_Rev 0.pdf 300:5A SR TRF: 2
Note on U406: Author: 2-954 MCM Magnolia Summer (normarl) @ 2 ft/sec, 6" or Greater Spacing. XEL-EVD-Facility-Rating-Supplement---Table---Bare-Overhead-Conductor.xls DCYR01-ESHV-E0E001 SH. 1
Note on V406: Author: Reference: 5" AL TUBULAR BUS DCYR01-ESMV-E0E001 SH. 1 XEL-EVD-Facility-Rating-Supplement---Table---Tubular-and-Square-Conductor.xls
Note on W406: Author: 2-954 MCM Magnolia Summer (normarl) @ 2 ft/sec, 6" or Greater Spacing. XEL-EVD-Facility-Rating-Supplement---Table---Bare-Overhead-Conductor.xls DCYR01-ESHV-E0E001 SH. 1
Note on X406: Author: Reference: DCYR01-ESPT-E8E001 SH. 1 280622-010_rev_00 .pdf 2000:5A MR (2000:5A TAP) TRF: 2
Note on Y406: Author: 280622-010_rev_00 .pdf DCYR01-ESHV-E0E001 SH.1
Note on Z406: Author: Reference: DCYR01-ESPT-E8E001 SH. 1 280622-010_rev_00 .pdf 2000:5A MR (2000:5A TAP) TRF: 2
Note on AA406: Author: 2-954 MCM Magnolia Summer (normarl) @ 2 ft/sec, 6" or Greater Spacing. XEL-EVD-Facility-Rating-Supplement---Table---Bare-Overhead-Conductor.xls DCYR01-ESHV-E0E001 SH. 1
Note on AB406: Author: DCYR01-ESHV-E0E001 SH. 1
Note on AC406: Author: Reference: 5" AL TUBULAR BUS DCYR01-ESMV-E0E001 SH. 1 XEL-EVD-Facility-Rating-Supplement---Table---Tubular-and-Square-Conductor.xls
Note on AD406: Author: (2) 2.5" Al. Bus = 2 * 1628 = 3256 Amps XEL-EVD-Facility-Rating-Supplement---Table---Tubular-and-Square-Conductor.xls
Note on C407: Author: Total Combined MVA of Turbines and Capacitor Banks Connected to Bus 1. Bus-Tie breaker is in the open position.
Note on F407: Author: Reference: 5" AL TUBULAR BUS DCYR01-ESMV-E0W001 SH. 1 XEL-EVD-Facility-Rating-Supplement---Table---Tubular-and-Square-Conductor.xls
Note on G407: Author: 3-1272 MCM Narcissus Summer (normarl) @ 2 ft/sec, 6" or Greater Spacing. XEL-EVD-Facility-Rating-Supplement---Table---Bare-Overhead-Conductor.xls DCYR01-ESEQ-E7W002
Note on H407: Author: Reference: 5" AL TUBULAR BUS DCYR01-ESMV-E0W001 SH. 1 XEL-EVD-Facility-Rating-Supplement---Table---Tubular-and-Square-Conductor.xls
Note on I407: Author: DCYR01-ESPT-E8W001 SH. 2 GIFD36-13.00.pdf 1500:5A SR TRF: 3
Note on J407: Author: Reference: 5" AL TUBULAR BUS DCYR01-ESMV-E0W001 SH. 1 XEL-EVD-Facility-Rating-Supplement---Table---Tubular-and-Square-Conductor.xls
Note on K407: Author: Reference: DCYR01-ESMV-E0W001 SH. 1
Note on L407: Author: 3-1272 MCM Narcissus Summer (normarl) @ 2 ft/sec, 6" or Greater Spacing. XEL-EVD-Facility-Rating-Supplement---Table---Bare-Overhead-Conductor.xls DCYR01-ESEQ-E7W002
Note on M407: Author: Reference: DCYR01-ESPT-E8W001 SH.1 3007854009-100 .pdf 2000:5A MR (2000:5A TAP) TRF: 2
Note on N407: Author: Reference: DCYR01-ESMV-E0W001 SH. 1
Note on O407: Author: Reference: DCYR01-ESPT-E8W001 SH.1 3007854009-100 .pdf 2000:5A MR (2000:5A TAP) TRF: 2
Note on P407: Author: 3-1272 MCM Narcissus Summer (normarl) @ 2 ft/sec, 6" or Greater Spacing. XEL-EVD-Facility-Rating-Supplement---Table---Bare-Overhead-Conductor.xls DCYR01-ESEQ-E7W002
Note on Q407: Author: Reference: DCYR01-ESMV-E0W001 SH. 1
Note on R407: Author: 3-1272 MCM Narcissus Summer (normarl) @ 2 ft/sec, 6" or Greater Spacing. XEL-EVD-Facility-Rating-Supplement---Table---Bare-Overhead-Conductor.xls DCYR01-ESEQ-E7W002
Note on S407: Author: Reference: DCYR01-ESPT-E8W001 SH. 1 D-18618_NAMEPLATE_1528.01-04_Rev 0.pdf 2620:5A SR TRF: 2
Note on T407: Author: Reference: DCYR01-ESPT-E8W001 SH. 1 D-18618_NAMEPLATE_1528.01-04_Rev 0.pdf 300:5A SR TRF: 2
Note on U407: Author: 2-954 MCM Magnolia Summer (normarl) @ 2 ft/sec, 6" or Greater Spacing. XEL-EVD-Facility-Rating-Supplement---Table---Bare-Overhead-Conductor.xls DCYR01-ESHV-E0W001 SH. 1
Note on V407: Author: Reference: 5" AL TUBULAR BUS DCYR01-ESMV-E0W001 SH. 1 XEL-EVD-Facility-Rating-Supplement---Table---Tubular-and-Square-Conductor.xls
Note on W407: Author: 2-954 MCM Magnolia Summer (normarl) @ 2 ft/sec, 6" or Greater Spacing. XEL-EVD-Facility-Rating-Supplement---Table---Bare-Overhead-Conductor.xls DCYR01-ESHV-E0W001 SH. 1
Note on X407: Author: Reference: DCYR01-ESPT-E8W001 SH. 1 280622-010_rev_00 .pdf 2000:5A MR (2000:5A TAP) TRF: 2
Note on Y407: Author: 280622-010_rev_00 .pdf DCYR01-ESHV-E0W001 SH.1
Note on Z407: Author: Reference: DCYR01-ESPT-E8W001 SH. 1 280622-010_rev_00 .pdf 2000:5A MR (2000:5A TAP) TRF: 2
Note on AA407: Author: 2-954 MCM Magnolia Summer (normarl) @ 2 ft/sec, 6" or Greater Spacing. XEL-EVD-Facility-Rating-Supplement---Table---Bare-Overhead-Conductor.xls DCYR01-ESHV-E0W001 SH. 1
Note on AB407: Author: DCYR01-ESHV-E0W001 SH. 1
Note on AC407: Author: Reference: 5" AL TUBULAR BUS DCYR01-ESMV-E0W001 SH. 1 XEL-EVD-Facility-Rating-Supplement---Table---Tubular-and-Square-Conductor.xls
Note on AD407: Author: (2) 2.5" Al. Bus = 2 * 1628 = 3256 Amps XEL-EVD-Facility-Rating-Supplement---Table---Tubular-and-Square-Conductor.xls
Note on C408: Author: Total Combined MVA of Turbines and Capacitor Banks Connected to Bus 2. Bus-Tie breaker is in the open position.
Note on F408: Author: Reference: 5" AL TUBULAR BUS DCYR01-ESMV-E0W001 SH. 1 XEL-EVD-Facility-Rating-Supplement---Table---Tubular-and-Square-Conductor.xls
Note on G408: Author: 3-1272 MCM Narcissus Summer (normarl) @ 2 ft/sec, 6" or Greater Spacing. XEL-EVD-Facility-Rating-Supplement---Table---Bare-Overhead-Conductor.xls DCYR01-ESEQ-E7W02
Note on H408: Author: Reference: 5" AL TUBULAR BUS DCYR01-ESMV-E0W001 SH. 1 XEL-EVD-Facility-Rating-Supplement---Table---Tubular-and-Square-Conductor.xls
Note on I408: Author: DCYR01-ESPT-E8W001 SH. 3 GIFD36-13.00.pdf 1500:5A SR TRF: 3
Note on J408: Author: Reference: 5" AL TUBULAR BUS DCYR01-ESMV-E0W001 SH. 1 XEL-EVD-Facility-Rating-Supplement---Table---Tubular-and-Square-Conductor.xls
Note on K408: Author: Reference: DCYR01-ESMV-E0W001 SH. 1
Note on L408: Author: 3-1272 MCM Narcissus Summer (normarl) @ 2 ft/sec, 6" or Greater Spacing. XEL-EVD-Facility-Rating-Supplement---Table---Bare-Overhead-Conductor.xls DCYR01-ESEQ-E7W02
Note on M408: Author: Reference: DCYR01-ESPT-E8W001 SH.1 3007854009-100 .pdf 2000:5A MR (2000:5A TAP) TRF: 2
Note on N408: Author: Reference: DCYR01-ESMV-E0W001 SH. 1
Note on O408: Author: Reference: DCYR01-ESPT-E8W001 SH.1 3007854009-100 .pdf 2000:5A MR (2000:5A TAP) TRF: 2
Note on P408: Author: 3-1272 MCM Narcissus Summer (normarl) @ 2 ft/sec, 6" or Greater Spacing. XEL-EVD-Facility-Rating-Supplement---Table---Bare-Overhead-Conductor.xls DCYR01-ESEQ-E7W02
Note on Q408: Author: Reference: DCYR01-ESMV-E0W001 SH. 1
Note on R408: Author: 3-1272 MCM Narcissus Summer (normarl) @ 2 ft/sec, 6" or Greater Spacing. XEL-EVD-Facility-Rating-Supplement---Table---Bare-Overhead-Conductor.xls DCYR01-ESEQ-E7W02
Note on S408: Author: Reference: DCYR01-ESPT-E8W001 SH. 1 D-18618_NAMEPLATE_1528.01-04_Rev 0.pdf 2620:5A SR TRF: 2
Note on T408: Author: Reference: DCYR01-ESPT-E8W001 SH. 1 D-18618_NAMEPLATE_1528.01-04_Rev 0.pdf 300:5A SR TRF: 2
Note on U408: Author: 2-954 MCM Magnolia Summer (normarl) @ 2 ft/sec, 6" or Greater Spacing. XEL-EVD-Facility-Rating-Supplement---Table---Bare-Overhead-Conductor.xls DCYR01-ESHV-E0W001 SH. 1
Note on V408: Author: Reference: 5" AL TUBULAR BUS DCYR01-ESMV-E0W001 SH. 1 XEL-EVD-Facility-Rating-Supplement---Table---Tubular-and-Square-Conductor.xls
Note on W408: Author: 2-954 MCM Magnolia Summer (normarl) @ 2 ft/sec, 6" or Greater Spacing. XEL-EVD-Facility-Rating-Supplement---Table---Bare-Overhead-Conductor.xls DCYR01-ESHV-E0W001 SH. 1
Note on X408: Author: Reference: DCYR01-ESPT-E8W001 SH. 1 280622-010_rev_00 .pdf 2000:5A MR (2000:5A TAP) TRF: 2
Note on Y408: Author: 280622-010_rev_00 .pdf DCYR01-ESHV-E0W001 SH.1
Note on Z408: Author: Reference: DCYR01-ESPT-E8W001 SH. 1 280622-010_rev_00 .pdf 2000:5A MR (2000:5A TAP) TRF: 2
Note on AA408: Author: 2-954 MCM Magnolia Summer (normarl) @ 2 ft/sec, 6" or Greater Spacing. XEL-EVD-Facility-Rating-Supplement---Table---Bare-Overhead-Conductor.xls DCYR01-ESHV-E0W001 SH. 1
Note on AB408: Author: DCYR01-ESHV-E0W001 SH. 1
Note on AC408: Author: Reference: 5" AL TUBULAR BUS DCYR01-ESMV-E0W001 SH. 1 XEL-EVD-Facility-Rating-Supplement---Table---Tubular-and-Square-Conductor.xls
Note on AD408: Author: (2) 2.5" Al. Bus = 2 * 1628 = 3256 Amps XEL-EVD-Facility-Rating-Supplement---Table---Tubular-and-Square-Conductor.xls
Note on C414: Author: Total Combined MVA of Turbines and Capacitor Banks Connected to Bus 1. Bus-Tie breaker is in the closed position.
Note on F414: Author: Reference: 5" AL TUBULAR BUS DCYR01-ESMV-E0E001 SH. 2 XEL-EVD-Facility-Rating-Supplement---Table---Tubular-and-Square-Conductor.xls
Note on G414: Author: Reference: DCYR01-ESMV-E0E001 SH. 2
Note on H414: Author: 3-1272 MCM Narcissus Summer (normarl) @ 2 ft/sec, 6" or Greater Spacing. XEL-EVD-Facility-Rating-Supplement---Table---Bare-Overhead-Conductor.xls DCYR01-ESEQ-E7E002
Note on I414: Author: Reference: DCYR01-ESPT-E8E001 SH. 2 3007854009-100 .pdf 2000:5A MR (2000:5A TAP) TRF: 2
Note on J414: Author: Reference: DCYR01-ESMV-E0E001 Sh.2
Note on K414: Author: Reference: DCYR01-ESPT-E8E001 SH. 2 3007854009-100 .pdf 2000:5A MR (2000:5A TAP) TRF: 2
Note on L414: Author: Reference: DCYR01-ESPT-E8E001 SH. 2 3007854009-100 .pdf 2000:5A MR (2000:5A TAP) TRF: 2
Note on M414: Author: 3-1272 MCM Narcissus Summer (normarl) @ 2 ft/sec, 6" or Greater Spacing. XEL-EVD-Facility-Rating-Supplement---Table---Bare-Overhead-Conductor.xls DCYR01-ESEQ-E7E002
Note on N414: Author: Reference: DCYR01-ESMV-E0E001 SH. 2
Note on O414: Author: Reference: 5" AL TUBULAR BUS DCYR01-ESMV-E0E001 SH. 2 XEL-EVD-Facility-Rating-Supplement---Table---Tubular-and-Square-Conductor.xls
Note on C415: Author: Total Combined MVA of Turbines and Capacitor Banks Connected to Bus 1. Bus-Tie breaker is in the closed position.
Note on F415: Author: Reference: 5" AL TUBULAR BUS DCYR01-ESMV-E0W001 SH. 2 XEL-EVD-Facility-Rating-Supplement---Table---Tubular-and-Square-Conductor.xls
Note on G415: Author: Reference: DCYR01-ESMV-E0W001 SH. 2
Note on H415: Author: 3-1272 MCM Narcissus Summer (normarl) @ 2 ft/sec, 6" or Greater Spacing. XEL-EVD-Facility-Rating-Supplement---Table---Bare-Overhead-Conductor.xls DCYR01-ESEQ-E7W02
Note on I415: Author: Reference: DCYR01-ESPT-E8W001 SH. 2 3007854009-100 .pdf 2000:5A MR (2000:5A TAP) TRF: 2
Note on J415: Author: Reference: DCYR01-ESMV-E0W001 Sh.2
Note on K415: Author: Reference: DCYR01-ESPT-E8W001 SH. 2 3007854009-100 .pdf 2000:5A MR (2000:5A TAP) TRF: 2
Note on L415: Author: Reference: DCYR01-ESPT-E8W001 SH. 2 3007854009-100 .pdf 2000:5A MR (2000:5A TAP) TRF: 2
Note on M415: Author: 3-1272 MCM Narcissus Summer (normarl) @ 2 ft/sec, 6" or Greater Spacing. XEL-EVD-Facility-Rating-Supplement---Table---Bare-Overhead-Conductor.xls DCYR01-ESEQ-E7W02
Note on N415: Author: Reference: DCYR01-ESMV-E0W001 SH. 2
Note on O415: Author: Reference: 5" AL TUBULAR BUS DCYR01-ESMV-E0W001 SH. 2 XEL-EVD-Facility-Rating-Supplement---Table---Tubular-and-Square-Conductor.xls
Note on C421: Author: Combined MVA of Cheyenne Ridge East
Note on C422: Author: Combined MVA of Cheyenne Ridge East
Note on C423: Author: Combined MVA of Cheyenne Ridge West
Note on C424: Author: Combined MVA of Cheyenne Ridge West
Note on C430: Author: Combined MVA of Cheyenne Ridge East.
Note on F430: Author: Reference: 5" AL TUBULAR BUS DCYR01-ESHV-E0E001 SH. 1 XEL-EVD-Facility-Rating-Supplement---Table---Tubular-and-Square-Conductor.xls
Note on G430: Author: DCYR01-ESHV-E0E001 SH. 2
Note on H430: Author: 2-954 MCM Magnolia Summer (normarl) @ 2 ft/sec, 6" or Greater Spacing. XEL-EVD-Facility-Rating-Supplement---Table---Bare-Overhead-Conductor.xls DCYR01-ESHV-E0E001 SH. 2
Note on I430: Author: DCYR01-ESHV-E0E001 SH. 2 2868280010-001.pdf
Note on J430: Author: 2-954 MCM Magnolia Summer (normarl) @ 2 ft/sec, 6" or Greater Spacing. XEL-EVD-Facility-Rating-Supplement---Table---Bare-Overhead-Conductor.xls DCYR01-ESHV-E0E001 SH. 2
Note on K430: Author: 2-954 MCM Cardinal Summer (normarl) @ 2 ft/sec, 6" or Greater Spacing. XEL-EVD-Facility-Rating-Supplement---Table---Bare-Overhead-Conductor.xls DCYR01-ESHV-E0E001 SH. 2
Note on L430: Author: Combined MVA of XFMR TR1 and TR2
Note on M430: Author: Combined MVA of MPT TR1 and TR2
Note on C433: Author: Combined MVA of Cheyenne Ridge East and West MPT MVA.
Note on F433: Author: 2-954 MCM Cardinal Summer (normarl) @ 2 ft/sec, 6" or Greater Spacing. XEL-EVD-Facility-Rating-Supplement---Table---Bare-Overhead-Conductor.xls DCYR01-ESHV-E0E001 SH. 2
Note on G433: Author: 2-954 MCM Magnolia Summer (normarl) @ 2 ft/sec, 6" or Greater Spacing. XEL-EVD-Facility-Rating-Supplement---Table---Bare-Overhead-Conductor.xls DCYR01-ESHV-E0W001 SH. 2
Note on H433: Author: DCYR01-ESHV-E0E001 SH. 2 2868280010-001.pdf
Note on I433: Author: 2-954 MCM Magnolia Summer (normarl) @ 2 ft/sec, 6" or Greater Spacing. XEL-EVD-Facility-Rating-Supplement---Table---Bare-Overhead-Conductor.xls DCYR01-ESHV-E0W001 SH. 2
Note on J433: Author: DCYR01-ESHV-E0W001 SH. 2
Note on K433: Author: 2-954 MCM Magnolia Summer (normarl) @ 2 ft/sec, 6" or Greater Spacing. XEL-EVD-Facility-Rating-Supplement---Table---Bare-Overhead-Conductor.xls DCYR01-ESHV-E0W001 SH. 2
Note on L433: Author: Reference: DCYR01-ESPT-E8W001 SH. 2 3007854009-100 .pdf 2000:5A MR (2000:5A TAP) TRF: 2
Note on N433: Author: Reference: DCYR01-ESPT-E8W001 SH. 2 3007854009-100 .pdf 2000:5A MR (2000:5A TAP) TRF: 2
Note on O433: Author: 2-954 MCM Magnolia Summer (normarl) @ 2 ft/sec, 6" or Greater Spacing. XEL-EVD-Facility-Rating-Supplement---Table---Bare-Overhead-Conductor.xls DCYR01-ESHV-E0W001 SH. 2
Note on P433: Author: DCYR01-ESHV-E0W001 SH. 2
Note on Q433: Author: Reference: 5" AL TUBULAR BUS DCYR01-ESMV-E0W001 SH. 1 XEL-EVD-Facility-Rating-Supplement---Table---Tubular-and-Square-Conductor.xls
Note on R433: Author: DCYR01-ESHV-E0W001 SH. 2
Note on S433: Author: 2-954 MCM Magnolia Summer (normarl) @ 2 ft/sec, 6" or Greater Spacing. XEL-EVD-Facility-Rating-Supplement---Table---Bare-Overhead-Conductor.xls DCYR01-ESHV-E0W001 SH. 2
Note on T433: Author: DCYR01-ESHV-E0E001 SH. 2 2868280010-001.pdf
Note on U433: Author: 2-954 MCM Magnolia Summer (normarl) @ 2 ft/sec, 6" or Greater Spacing. XEL-EVD-Facility-Rating-Supplement---Table---Bare-Overhead-Conductor.xls DCYR01-ESHV-E0W001 SH. 2
Note on C436: Author: Combined MVA of MPT TR1 and TR2. Breaker 7215 is in the open position.
Note on F436: Author: Reference: 5" AL TUBULAR BUS DCYR01-ESMV-E0W001 SH. 1 XEL-EVD-Facility-Rating-Supplement---Table---Tubular-and-Square-Conductor.xls
Note on G436: Author: DCYR01-ESHV-E0W001 SH. 2
Note on H436: Author: 2-954 MCM Magnolia Summer (normarl) @ 2 ft/sec, 6" or Greater Spacing. XEL-EVD-Facility-Rating-Supplement---Table---Bare-Overhead-Conductor.xls DCYR01-ESHV-E0E001 SH. 2
Note on I436: Author: DCYR01-ESHV-E0W001 SH. 2 2868280010-001.pdf
Note on J436: Author: 2-954 MCM Magnolia Summer (normarl) @ 2 ft/sec, 6" or Greater Spacing. XEL-EVD-Facility-Rating-Supplement---Table---Bare-Overhead-Conductor.xls DCYR01-ESHV-E0W001 SH. 2
Note on K436: Author: 2-954 MCM Cardinal Summer (normarl) @ 2 ft/sec, 6" or Greater Spacing. XEL-EVD-Facility-Rating-Supplement---Table---Bare-Overhead-Conductor.xls DCYR01-ESHV-E0W001 SH. 2
Note on L436: Author: Combined MVA of XFMR TR1 and TR2